## Server Version
Server Version | 2760
2760
2760
Note on B1: Edgar F. Hilton: This queries the server to obtain the version of the server. This is generally a good thing to check for before contacting support.

## Feature Discovery
Index | Supported Variable | SI | British | Supported Units | Supported Calculation Type
1 | ENTROPY_SUCTION | kJ/kg_K | Btu/(lb) (R) | SI | FROM_CAPACITY
2 | SPEED_SOUND | m/s | ft/sec | British | FROM_EVAP_MASS_FLOW
3 | DENSITY_SUCTION | kg/m3 | lb/ft3 |  | FROM_POWER
4 | ENTHALPY_LIQUID_CONDENSER_EXIT | kJ/kg | Btu/lb
5 | ENTHALPY_DISCHARGE_ISENTROPIC | kJ/kg | Btu/lb
6 | ENTHALPY_SUCTION | kJ/kg | Btu/lb
7 | SPEED_COMPRESSOR | RPM | RPM
8 | MASS_FLOW_RATE_EVAPORATOR | kg/s | lbs/sec
9 | MASS_FLOW_RATE_MOTOR_COOLING | kg/s | lbs/sec
10 | COEFFICIENT_OF_PERFORMANCE | kW/kW | kW/ton
11 | POWER_INPUT_ELECTRICAL | kW | kW
12 | CAPACITY_EVAPORATOR | kW | Ton
13 | TEMPERATURE_SUCT_SAT | C | F
14 | TEMPERATURE_DISCH_SAT | C | F
15 | TEMPERATURE_SUCT_SUPER_HEAT | C | F
16 | TEMPERATURE_CONDENSER_LIQUID_LEAVING | C | F
17 | PRESSURE_SUCT_ABSOLUTE | kPa | PSI
18 | PRESSURE_DISCH_ABSOLUTE | kPa | PSI
19 | TEMPERATURE_DISCH | C | F
20 | PRESSURE_RATIO
21 | POWER_FACTOR
22 | IGV_ANGLE | % | %
23 | INPUT_CURRENT | A | A
24 | ECON_SAT_TEMP | C | F
25 | ECON_INTERSTAGE_P | kPa | PSI
26 | ECON_CAPACITY | kW | Ton
27 | ECON_MASS_FLOW | kg/s | lbs/sec
28 | TEMPERATURE_ECO_LIQUID_LEAVING | C | F
29 | ENTHALPY_LIQUID_ECO_EXIT | kJ/kg | Btu/lb
Note on A1: Edgar F. Hilton: Just a counter. We'll be using these counters to help us with the columns to the right.
Note on B1: Edgar F. Hilton: This is a list of variables which the server knows about. You may want to call NumberOfVariables() first to obtain the total number of variables available to you.
Note on C1: Edgar F. Hilton: SI units for the variables in the previous column.
Note on D1: Edgar F. Hilton: British Units for the variables column.
Note on F1: Edgar F. Hilton: The list of supported units.
Note on H1: Edgar F. Hilton: The list of calculation types supported by the server. We'll be using these when we start querying the server to do a calculation for us.

## TGH285-noEcon_A
PN | 2718315
Calculation Type | FROM_POWER
Units | SI
Use Economizer? | FALSE
Compressor | TGH285-E-3-MT-SL
| 3 | 2.5 |  |  | 6 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 11 | 11
| INPUT BLOCK | [5 empty] | 1: OUTPUT
CID | SST Verd. Temp | SDT Kond. Temperatur | Value Power | SSH Superheat | LLT Leaving Liquid Temp | tapp T approach Economizer | ENTROPY_SUCTION | SPEED_SOUND | DENSITY_SUCTION | ENTHALPY_LIQUID_CONDENSER_EXIT | ENTHALPY_DISCHARGE_ISENTROPIC | ENTHALPY_SUCTION | SPEED_COMPRESSOR | MASS_FLOW_RATE_EVAPORATOR | MASS_FLOW_RATE_MOTOR_COOLING | COEFFICIENT_OF_PERFORMANCE | POWER_INPUT_ELECTRICAL | CAPACITY_EVAPORATOR | TEMPERATURE_SUCT_SAT | TEMPERATURE_DISCH_SAT | TEMPERATURE_SUCT_SUPER_HEAT | TEMPERATURE_CONDENSER_LIQUID_LEAVING | PRESSURE_SUCT_ABSOLUTE | PRESSURE_DISCH_ABSOLUTE | TEMPERATURE_DISCH | PRESSURE_RATIO | POWER_FACTOR | IGV_ANGLE | INPUT_CURRENT | ECON_SAT_TEMP | ECON_INTERSTAGE_P | ECON_CAPACITY | ECON_MASS_FLOW | TEMPERATURE_ECO_LIQUID_LEAVING | ENTHALPY_LIQUID_ECO_EXIT | TOLERANCE | POWER_INPUT_ELECTRICAL | POWER_INPUT_ELECTRICAL
CID=2042708102 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042708005 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707908 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707819 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707978 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707881 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707784 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707695 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2042707854 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267114 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718266955 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267052 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267149 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267238 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267079 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267176 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267273 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267362 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1718267203 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636537935 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636537776 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636537873 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636537970 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636538059 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636537900 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636537997 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636538094 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636538183 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-636538024 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=992928184 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=992928343 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=992928246 | -15 | -5 | 0 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18392.1631 | 0.25599 | 0.0066823 | 11.2411 | 4.3303 | 48.6773 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 4.3564 | 1.4946 | 0.63776 | 87.9036 | 10.316 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=992928149 | -15 | -2.5 | 0 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 19056.3892 | 0.2821 | 0.0066258 | 10.1428 | 5.2351 | 53.0986 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 7.2978 | 1.6437 | 0.64853 | 110 | 12.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3.8092 | 8.6947
CID=992928060 | -15 | 0 | 0 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 20149.9949 | 0.29654 | 0.0067855 | 9.1365 | 6.0042 | 54.857 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 9.8784 | 1.804 | 0.65736 | 110 | 13.8772 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.4307 | 11.0329
CID=992928219 | -15 | 2.5 | 0 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 21689.2314 | 0.33983 | 0.0071557 | 8.2109 | 7.5222 | 61.7641 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 12.9419 | 1.9762 | 0.67396 | 110 | 16.9577 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.2867 | 13.7049
CID=992928122 | -15 | 5 | 0 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 23002.3501 | 0.37841 | 0.0076386 | 7.4652 | 9.0474 | 67.5409 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 15.6716 | 2.1607 | 0.68958 | 110 | 19.9341 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1823 | 16.1956
CID=992928025 | -15 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 23903.3886 | 0.39178 | 0.0080529 | 6.8077 | 10.0834 | 68.6447 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 18.1992 | 2.3583 | 0.69962 | 110 | 21.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2299 | 19.3754
CID=992927936 | -15 | 10 | 0 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 25127.9974 | 0.43244 | 0.0087503 | 6.1996 | 11.9921 | 74.3463 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 21.0538 | 2.5693 | 0.71698 | 110 | 25.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5747 | 23.0861
CID=992928095 | -15 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 26384.7866 | 0.48667 | 0.0096702 | 5.6813 | 14.4438 | 82.0597 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 23.871 | 2.7945 | 0.7373 | 110 | 29.7643 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0921 | 27.0734
CID=2074657363 | -15 | 15 | 0 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 27270.15 | 0.51349 | 0.01043 | 5.2353 | 16.2119 | 84.8739 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 26.4724 | 3.0345 | 0.75067 | 110 | 32.8125 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.5676 | 30.0979
CID=2074657522 | -15 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 28099.5967 | 0.54022 | 0.01127 | 4.8338 | 18.099 | 87.4872 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 29.1007 | 3.2899 | 0.76387 | 110 | 35.999 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.3575 | 34.2767
CID=2074657425 | -15 | 20 | 0 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 29145.1984 | 0.5941 | 0.01254 | 4.4628 | 21.1117 | 94.2162 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 31.9016 | 3.5612 | 0.78284 | 110 | 40.9737 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3391 | 38.2422
CID=2074657328 | -15 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 29832.3435 | 0.60699 | 0.013437 | 4.1175 | 22.8801 | 94.2092 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 34.6869 | 3.8493 | 0.79288 | 110 | 43.8434 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6718 | 39.9189
CID=2074657239 | -15 | 25 | 0 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 30604.7003 | 0.63485 | 0.014597 | 3.8166 | 25.2515 | 96.3756 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 37.4365 | 4.1546 | 0.80521 | 110 | 47.647 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9411 | 40.1319
CID=2074657398 | -15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 31401.8054 | 0.67337 | 0.015994 | 3.5558 | 28.1011 | 99.9208 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 40.091 | 4.4779 | 0.81845 | 110 | 52.1663 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9327 | 40.079
CID=2074657301 | -15 | 30 | 0 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 32161.5934 | 0.69956 | 0.017381 | 3.2991 | 30.7354 | 101.4004 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 42.9388 | 4.8198 | 0.82932 | 109.4 | 56.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.5427 | 40.0954
CID=2074657204 | -15 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 33266.3376 | 0.7934 | 0.020054 | 3.0796 | 36.4512 | 112.2561 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 45.7248 | 5.1811 | 0.84908 | 110 | 65.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1228 | 40.4314
CID=2074657115 | -15 | 35 | 0 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33967.0954 | 0.84664 | 0.021959 | 2.9274 | 39.9119 | 116.8401 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 47.7086 | 5.5624 | 0.85889 | 110 | 70.6029 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7162 | 35.7098 | 39.9119
CID=2074657274 | -15 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.78091 | 139.7222 | 6.5785 | 67.0967 | 235.4912 | 201.5939 | 34087.7014 | 0.79147 | 0.021982 | 2.7587 | 38.5874 | 106.4508 | -15 | 37.5 | 4 | 31.5 | 120.0066 | 715.7661 | 49.9149 | 5.9644 | 0.8553 | 109.605 | 68.5458 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.2301 | 38.5874
CID=-1686317694 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317535 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317632 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317729 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317818 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317659 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317756 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317853 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317942 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1686317783 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604588515 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604588356 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604588453 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604588550 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604588639 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604588480 | -12 | 0 | 0 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 18455.1018 | 0.29307 | 0.0066675 | 10.6873 | 5.1305 | 54.8312 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 9.2034 | 1.5931 | 0.64731 | 104.53 | 12.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5016 | 4.1993 | 8.8682
CID=-604588577 | -12 | 2.5 | 0 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 19668.387 | 0.3193 | 0.0068455 | 9.5316 | 6.1587 | 58.7023 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 12.046 | 1.7452 | 0.6591 | 110 | 14.1968 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.6238 | 11.4069
CID=-604588674 | -12 | 5 | 0 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 21176.2136 | 0.3655 | 0.0072368 | 8.5825 | 7.6906 | 66.0046 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 14.9253 | 1.9081 | 0.67574 | 110 | 17.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4802 | 14.2089
CID=-604588763 | -12 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 22374.1014 | 0.3961 | 0.0076979 | 7.7332 | 9.082 | 70.2332 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 17.6767 | 2.0826 | 0.68992 | 110 | 20.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.3445 | 17.3877
CID=-604588604 | -12 | 10 | 0 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 23633.5603 | 0.44205 | 0.0083395 | 7.0436 | 10.9213 | 76.926 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 20.3568 | 2.269 | 0.70742 | 110 | 23.4561 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5663 | 20.1421
CID=897079924 | -12 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 24683.8943 | 0.47247 | 0.0089841 | 6.4157 | 12.5716 | 80.6563 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 23.0262 | 2.4678 | 0.72198 | 110 | 26.4558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9351 | 24.0547
CID=897080083 | -12 | 15 | 0 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 25827.6565 | 0.51819 | 0.0098481 | 5.8665 | 14.7856 | 86.7398 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 25.7575 | 2.6798 | 0.73996 | 110 | 30.3588 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.4239 | 28.2107
CID=897079986 | -12 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 26730.2819 | 0.54844 | 0.010663 | 5.3918 | 16.6863 | 89.9696 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 28.3731 | 2.9053 | 0.75409 | 110 | 33.6196 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.959 | 32.2434
CID=897079889 | -12 | 20 | 0 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 27695.5999 | 0.59398 | 0.01172 | 4.9779 | 19.1733 | 95.4434 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 30.9894 | 3.1449 | 0.77092 | 110 | 37.7872 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.8048 | 36.0111
CID=897079800 | -12 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 28636.4613 | 0.63937 | 0.012923 | 4.5887 | 21.9183 | 100.5762 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 33.7282 | 3.3993 | 0.78752 | 110 | 42.2867 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8745 | 40.4827
CID=897079959 | -12 | 25 | 0 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 29413.3077 | 0.66976 | 0.01405 | 4.2454 | 24.2805 | 103.0812 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 36.3919 | 3.6689 | 0.80031 | 110 | 46.0949 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0705 | 44.884
CID=897079862 | -12 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 30282.3934 | 0.71442 | 0.015519 | 3.9214 | 27.4168 | 107.5123 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 39.2224 | 3.9544 | 0.81541 | 110 | 51.0852 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8318 | 45.1309
CID=897079765 | -12 | 30 | 0 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 30899.4064 | 0.72884 | 0.016634 | 3.6438 | 29.413 | 107.1747 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 41.8574 | 4.2564 | 0.82402 | 110 | 54.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.4146 | 44.9448
CID=897079676 | -12 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 31637.9412 | 0.75845 | 0.018087 | 3.3892 | 32.1329 | 108.9035 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 44.5505 | 4.5754 | 0.83461 | 109.8578 | 58.4955 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5551 | 27.064 | 44.9312
CID=897079835 | -12 | 35 | 0 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 32470.65 | 0.80916 | 0.020064 | 3.151 | 35.9783 | 113.3671 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 47.3531 | 4.9121 | 0.84762 | 109.5597 | 64.4901 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.8778 | 45.1391
CID=1978809103 | -12 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 33597.1861 | 0.92399 | 0.023379 | 2.9467 | 42.8323 | 126.2148 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 50.0493 | 5.2671 | 0.8661 | 110 | 75.138 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0704 | 45.4468
CID=1978809262 | -12 | 40 | 0 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 34087.8464 | 0.95343 | 0.025006 | 2.805 | 45.2292 | 126.8692 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 51.935 | 5.6411 | 0.87138 | 110 | 78.8622 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7063 | 41.392 | 45.2292
CID=1978809165 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978809068 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978808979 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978809138 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978809041 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978808944 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978808855 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1978809014 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-181789221 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-282545770 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1304182683 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1404497696 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1102669585 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1203426134 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2069904249 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=483617332 | -9 | 2.5 | 0 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 18439.9347 | 0.32239 | 0.0067073 | 11.2912 | 5.309 | 59.9452 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 11.3922 | 1.5462 | 0.6494 | 92.5605 | 12.4211 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.3612 | 8.9771
CID=1659971507 | -9 | 5 | 0 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 19150.788 | 0.34188 | 0.0068994 | 10.0087 | 6.24 | 62.4548 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 14.0931 | 1.6906 | 0.66001 | 109.8832 | 14.3644 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2921 | 4.5803 | 11.7505
CID=1559214958 | -9 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 20539.075 | 0.38209 | 0.0072863 | 8.9034 | 7.6993 | 68.5493 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 17.0209 | 1.8452 | 0.67583 | 110 | 17.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6398 | 14.6838
CID=-181783972 | -9 | 10 | 0 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 22001.1592 | 0.4364 | 0.0078809 | 8.0144 | 9.5898 | 76.8567 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 19.8474 | 2.0103 | 0.69489 | 110 | 20.9676 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.707 | 18.0132
CID=-282540521 | -9 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 23030.3956 | 0.46243 | 0.0084168 | 7.2729 | 10.9875 | 79.9118 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 22.3989 | 2.1865 | 0.70802 | 110 | 23.5781 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7039 | 20.8962
CID=-1304177434 | -9 | 15 | 0 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 24068.4868 | 0.49664 | 0.0090842 | 6.6342 | 12.6877 | 84.1723 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 24.9713 | 2.3743 | 0.72297 | 110 | 26.6637 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2107 | 24.9456
CID=1404502945 | -9 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 25109.7049 | 0.53074 | 0.009863 | 6.0402 | 14.5985 | 88.1776 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 27.6914 | 2.5741 | 0.73851 | 110 | 30.0338 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7125 | 29.4124
CID=-1102664336 | -9 | 20 | 0 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 26335.0399 | 0.5993 | 0.011056 | 5.5347 | 17.6259 | 97.5546 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 30.446 | 2.7864 | 0.76066 | 110 | 35.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5811 | 34.2136
CID=-1203420885 | -9 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 27322.1576 | 0.65047 | 0.012205 | 5.1029 | 20.3189 | 103.6854 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 33.0426 | 3.0118 | 0.77808 | 110 | 39.6761 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.2865 | 37.7584
CID=2069909498 | -9 | 25 | 0 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 27993.824 | 0.66704 | 0.013075 | 4.7202 | 22.0455 | 104.0593 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 35.5394 | 3.2507 | 0.78824 | 110 | 42.4931 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.365 | 42.7201
CID=483622581 | -9 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 28814.7337 | 0.70071 | 0.014278 | 4.3508 | 24.5739 | 106.917 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 38.269 | 3.5036 | 0.80181 | 110 | 46.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.8057 | 47.4545
CID=1659976756 | -9 | 30 | 0 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 29679.023 | 0.75149 | 0.015816 | 4.0261 | 27.8384 | 112.08 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 40.9841 | 3.7712 | 0.81729 | 110 | 51.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4049 | 50.6676
CID=1559220207 | -9 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 30428.3692 | 0.78493 | 0.017257 | 3.7323 | 30.6379 | 114.3501 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 43.6779 | 4.0538 | 0.82894 | 110 | 56.1554 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.4891 | 51.064
CID=-181787175 | -9 | 35 | 0 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 31183.9692 | 0.83544 | 0.019062 | 3.4761 | 34.176 | 118.7982 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 46.2954 | 4.3522 | 0.84179 | 110 | 61.6839 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.363 | 50.7666
CID=-282543724 | -9 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 31990.2423 | 0.88283 | 0.02104 | 3.2308 | 37.8985 | 122.4409 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 49.0365 | 4.6667 | 0.85336 | 109.9781 | 67.4754 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5469 | 31.5427 | 50.2122
CID=-1304180637 | -9 | 40 | 0 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 32765.1969 | 0.93584 | 0.023298 | 3.0091 | 42.0353 | 126.4889 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 51.7549 | 4.9981 | 0.86422 | 109.4067 | 73.9003 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9445 | 35.6622 | 51.0088
CID=1404499742 | -9 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 33721.4206 | 1.0371 | 0.026654 | 2.817 | 48.4527 | 136.4901 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 54.3586 | 5.3467 | 0.87767 | 110 | 83.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6387 | 50.9152
CID=-1102667539 | -9 | 45 | 0 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 34117.2202 | 1.053 | 0.028193 | 2.6819 | 50.2672 | 134.8111 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.2252 | 5.7134 | 0.88085 | 110 | 86.7041 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=-1203424088 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2069906295 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=483619378 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1659973553 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1559217004 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-181790374 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-282546923 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1304183836 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1404496543 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1102670738 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1203427287 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2069903096 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=483616179 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1659970354 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1559213805 | -6 | 5 | 0 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18461.0374 | 0.34464 | 0.0067502 | 11.9308 | 5.3374 | 63.6796 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 13.4868 | 1.5026 | 0.64973 | 79.7001 | 12.4812 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=-181793321 | -6 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 18633.2962 | 0.36396 | 0.0069528 | 10.4822 | 6.3018 | 66.0571 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 16.2118 | 1.64 | 0.6607 | 105.3157 | 14.4915 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.779 | 12.0604
CID=-282549870 | -6 | 10 | 0 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 20193.7847 | 0.42206 | 0.0074165 | 9.3243 | 8.0664 | 75.2131 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 19.1238 | 1.7868 | 0.67965 | 110 | 18.0322 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7257 | 15.1552
CID=-1304186783 | -6 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 21322.0328 | 0.45056 | 0.0079052 | 8.3186 | 9.4729 | 78.8015 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 21.8498 | 1.9434 | 0.69376 | 110 | 20.7459 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8046 | 18.649
CID=1404493596 | -6 | 15 | 0 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 22579.1103 | 0.49897 | 0.0085937 | 7.5145 | 11.3926 | 85.6093 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 24.5304 | 2.1103 | 0.71168 | 110 | 24.3216 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.1409 | 22.5502
CID=-1102673685 | -6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 23791.5091 | 0.55668 | 0.0094579 | 6.842 | 13.6874 | 93.6486 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 27.1461 | 2.2879 | 0.73126 | 110 | 28.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4617 | 25.8429
CID=-1203430234 | -6 | 20 | 0 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 24805.5116 | 0.59488 | 0.010301 | 6.2357 | 15.7281 | 98.0759 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 29.7606 | 2.4766 | 0.74711 | 110 | 31.985 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.2332 | 30.5791
CID=2069900149 | -6 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 25776.5782 | 0.63298 | 0.011244 | 5.7024 | 17.9255 | 102.2184 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 32.3914 | 2.6769 | 0.7627 | 110 | 35.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9502 | 35.5459
CID=483613232 | -6 | 25 | 0 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 26776.0091 | 0.69031 | 0.012471 | 5.2476 | 20.7967 | 109.1316 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 34.9874 | 2.8892 | 0.78097 | 110 | 40.459 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7519 | 40.5021
CID=1659967407 | -6 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 27714.9812 | 0.74752 | 0.013831 | 4.8459 | 23.8594 | 115.6194 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 37.5558 | 3.1141 | 0.79813 | 110 | 45.4198 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9384 | 44.721
CID=1559210858 | -6 | 30 | 0 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 28500.5272 | 0.78527 | 0.015124 | 4.4743 | 26.5423 | 118.7573 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 40.1699 | 3.3519 | 0.8114 | 110 | 49.7001 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.4722 | 50.1265
CID=-181788072 | -6 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 29362.5721 | 0.84218 | 0.016785 | 4.1439 | 30.0316 | 124.448 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 42.7914 | 3.6031 | 0.82653 | 110 | 55.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.148 | 55.2599
CID=-282544621 | -6 | 35 | 0 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 30008.6991 | 0.86036 | 0.018122 | 3.8252 | 32.4526 | 124.138 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 45.5418 | 3.8682 | 0.83578 | 110 | 58.9951 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0822 | 56.636
CID=-1304181534 | -6 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 30634.9789 | 0.8785 | 0.019508 | 3.5522 | 34.8162 | 123.6743 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 48.1644 | 4.1478 | 0.84392 | 109.5592 | 62.6813 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4083 | 28.0639 | 56.9451
CID=1404498845 | -6 | 40 | 0 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 31455.3155 | 0.95412 | 0.021919 | 3.3137 | 39.5184 | 130.9524 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 50.7501 | 4.4423 | 0.85784 | 109.9997 | 69.9917 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0027 | 31.7052 | 56.788
CID=-1102668436 | -6 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 32173.5392 | 0.99116 | 0.023978 | 3.0779 | 43.0519 | 132.511 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 53.496 | 4.7522 | 0.86661 | 109.7106 | 75.4791 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4113 | 36.4168 | 56.5732
CID=-1203424985 | -6 | 45 | 0 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 33078.2937 | 1.0854 | 0.027295 | 2.8687 | 49.2313 | 141.2298 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 56.212 | 5.0781 | 0.87906 | 110 | 85.0895 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.914 | 56.8886
CID=2069905398 | -6 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 34006.5957 | 1.1986 | 0.031228 | 2.6906 | 56.3571 | 151.6327 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 58.7214 | 5.4204 | 0.88987 | 110 | 96.223 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8283 | 57.2808
CID=483618481 | -6 | 50 | 0 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34208.218 | 1.1781 | 0.032228 | 2.561 | 56.521 | 144.7519 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 60.572 | 5.7798 | 0.89008 | 110 | 96.4798 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=1659972656 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1559216107 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-181791275 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-282547824 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1304184737 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1404495642 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1102671639 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1203428188 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2069902195 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=483615278 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1659969453 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1559212904 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-181794474 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-282551023 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1304187936 | -3 | 10 | 0 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 18487.9861 | 0.40695 | 0.0070562 | 10.9866 | 6.6778 | 73.3665 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 18.5098 | 1.5929 | 0.66486 | 102.5819 | 15.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.3391 | 12.2784
CID=1404492443 | -3 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 19665.7892 | 0.44588 | 0.0074869 | 9.6833 | 8.1491 | 78.9104 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 21.2984 | 1.7325 | 0.6805 | 109.6442 | 18.1943 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9678 | 5.9798 | 15.6157
CID=-1102674838 | -3 | 15 | 0 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 20945.1341 | 0.49308 | 0.0080837 | 8.6231 | 9.9297 | 85.6244 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 24.0545 | 1.8813 | 0.69816 | 110 | 21.6092 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.1813 | 19.2479
CID=-1203431387 | -3 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 22114.1062 | 0.53599 | 0.0087602 | 7.7724 | 11.7445 | 91.283 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 26.6565 | 2.0396 | 0.71481 | 110 | 24.9631 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3228 | 23.3226
CID=2069898996 | -3 | 20 | 0 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 23193.6249 | 0.57879 | 0.0095374 | 7.048 | 13.7099 | 96.6276 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 29.2336 | 2.2079 | 0.73144 | 110 | 28.4782 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6291 | 26.7511
CID=483612079 | -3 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 24192.3338 | 0.6215 | 0.010407 | 6.4326 | 15.8034 | 101.6577 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 31.7615 | 2.3864 | 0.74767 | 110 | 32.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.6237 | 31.6404
CID=1659966254 | -3 | 25 | 0 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 25194.5942 | 0.66408 | 0.01141 | 5.8623 | 18.144 | 106.3648 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 34.4248 | 2.5757 | 0.76417 | 110 | 36.0742 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2655 | 36.9411
CID=1559209705 | -3 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 26381.6624 | 0.74969 | 0.012952 | 5.3729 | 21.8718 | 117.515 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 37.12 | 2.7762 | 0.78725 | 110 | 42.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.5311 | 42.6405
CID=-181797421 | -3 | 30 | 0 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 27210.8428 | 0.79204 | 0.014181 | 4.9578 | 24.4924 | 121.4291 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 39.6288 | 2.9882 | 0.8014 | 110 | 46.4343 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4826 | 46.7387
CID=-282553970 | -3 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 27972.2799 | 0.83429 | 0.015515 | 4.5919 | 27.2259 | 125.0181 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 42.1061 | 3.2122 | 0.81455 | 110 | 50.7832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0462 | 52.5507
CID=-1304190883 | -3 | 35 | 0 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 28760.0834 | 0.87635 | 0.017037 | 4.2371 | 30.2727 | 128.2676 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 44.7679 | 3.4485 | 0.8275 | 110 | 55.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9114 | 58.111
CID=1404489496 | -3 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 29586.8334 | 0.93978 | 0.018977 | 3.9276 | 34.1828 | 134.2562 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 47.3839 | 3.6978 | 0.84181 | 110 | 61.6946 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.5999 | 63.3351
CID=-1102677785 | -3 | 40 | 0 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 30306.5421 | 0.9815 | 0.020829 | 3.6358 | 37.6128 | 136.7521 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 50.0839 | 3.9603 | 0.85254 | 110 | 67.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1961 | 63.4544
CID=-1203434334 | -3 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 30967.2197 | 1.0231 | 0.022791 | 3.3832 | 41.0595 | 138.9128 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 52.6694 | 4.2366 | 0.86183 | 110 | 72.3849 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0001 | 32.3922 | 63.0494
CID=2069896049 | -3 | 45 | 0 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 31642.9894 | 1.0646 | 0.024919 | 3.153 | 44.6327 | 140.7281 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 55.2498 | 4.5271 | 0.87011 | 109.9815 | 77.9351 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4626 | 36.8219 | 63.027
CID=483609132 | -3 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 32317.3789 | 1.1058 | 0.027311 | 2.9302 | 48.5231 | 142.1825 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 57.9761 | 4.8323 | 0.8778 | 109.4 | 83.9864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.7507 | 63.4939
CID=1659963307 | -3 | 50 | 0 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 33190.296 | 1.2108 | 0.031176 | 2.7322 | 55.3723 | 151.2909 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 60.6632 | 5.1527 | 0.88856 | 109.8231 | 94.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4741 | 46.6377 | 63.7961
CID=1559206758 | -3 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 34116.1013 | 1.3586 | 0.035928 | 2.5903 | 63.6127 | 164.7735 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 62.7591 | 5.4887 | 0.89794 | 110 | 107.6342 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7462 | 53.5574 | 63.6127
CID=-181792172 | -3 | 55 | 0 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34136.3697 | 1.2932 | 0.035989 | 2.4776 | 61.3723 | 152.0561 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 64.4061 | 5.841 | 0.89571 | 110 | 104.102 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=-282548721 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1304185634 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1404494745 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1102672536 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1203429085 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2069901298 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=483614381 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1659968556 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1559212007 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1626730432 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=322768517 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-60313034 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1364274949 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=705850068 | 0 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 18486.4512 | 0.42946 | 0.0071034 | 11.5305 | 6.6687 | 76.893 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 20.6352 | 1.5491 | 0.66476 | 84.9036 | 15.2415 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.6702 | 13.1874
CID=-598111847 | 0 | 15 | 0 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 19193.9398 | 0.47749 | 0.0075723 | 10.1268 | 8.2856 | 83.9065 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 23.4144 | 1.6821 | 0.68191 | 109.9341 | 18.4609 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1647 | 5.883 | 16.0314
CID=-981193398 | 0 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 20448.1095 | 0.52538 | 0.0081935 | 8.9549 | 10.1134 | 90.5651 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 26.1914 | 1.8236 | 0.6999 | 110 | 21.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2692 | 19.8154
CID=2009811983 | 0 | 20 | 0 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 21443.0489 | 0.54905 | 0.0087783 | 8.0141 | 11.5795 | 92.7999 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 28.7891 | 1.9741 | 0.71335 | 108.3727 | 24.6629 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0682 | 8.7353 | 24.0702
CID=-826476136 | 0 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 22743.5452 | 0.62083 | 0.0097547 | 7.2615 | 14.1616 | 102.8347 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 31.4025 | 2.1337 | 0.73507 | 110 | 29.2714 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1199 | 28.0987
CID=-2130438051 | 0 | 25 | 0 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 23908.4982 | 0.69247 | 0.010877 | 6.6182 | 16.9754 | 112.3471 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 33.958 | 2.303 | 0.75614 | 110 | 34.1092 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7385 | 32.6801
CID=1626735681 | 0 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 24887.6858 | 0.7399 | 0.011957 | 6.0375 | 19.4637 | 117.5121 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 36.5308 | 2.4822 | 0.77277 | 110 | 38.2677 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9765 | 38.3214
CID=322773766 | 0 | 30 | 0 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 25822.8909 | 0.7872 | 0.01316 | 5.5253 | 22.1376 | 122.3172 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 39.1228 | 2.6717 | 0.78876 | 110 | 42.6424 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9309 | 44.1758
CID=-60307785 | 0 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 26786.3996 | 0.8584 | 0.01472 | 5.0897 | 25.6222 | 130.4093 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 41.6648 | 2.872 | 0.80702 | 110 | 48.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0018 | 50.2286
CID=-1364269700 | 0 | 35 | 0 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 27580.4406 | 0.90545 | 0.016175 | 4.6993 | 28.6006 | 134.4033 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 44.1859 | 3.0833 | 0.8206 | 110 | 52.9538 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6907 | 54.8307
CID=705855317 | 0 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 28447.4721 | 0.97631 | 0.018078 | 4.3474 | 32.5478 | 141.4975 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 46.7478 | 3.3062 | 0.83612 | 110 | 59.1438 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6252 | 61.2623
CID=-598106598 | 0 | 40 | 0 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 29193.8056 | 1.023 | 0.019888 | 4.0183 | 35.999 | 144.6536 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 49.3793 | 3.5409 | 0.84769 | 110 | 64.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4682 | 67.1838
CID=-981188149 | 0 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 29797.0362 | 1.0456 | 0.021507 | 3.7213 | 38.7333 | 144.1363 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 51.9988 | 3.7879 | 0.85571 | 110 | 68.7723 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9202 | 70.4572
CID=2009817232 | 0 | 45 | 0 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 30492.3622 | 1.092 | 0.023622 | 3.4548 | 42.4394 | 146.62 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 54.6195 | 4.0477 | 0.86518 | 110 | 74.5278 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7902 | 71.0175
CID=-826470887 | 0 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 31127.5064 | 1.1383 | 0.025891 | 3.2178 | 46.218 | 148.7205 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 57.1831 | 4.3205 | 0.8734 | 110 | 80.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3283 | 70.5862
CID=-2130432802 | 0 | 50 | 0 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 31792.9486 | 1.1843 | 0.028395 | 2.9954 | 50.2188 | 150.4237 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 59.8084 | 4.607 | 0.88077 | 109.8242 | 86.6286 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3957 | 42.4342 | 70.2774
CID=1626732478 | 0 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 32518.9846 | 1.2538 | 0.031635 | 2.7869 | 55.4949 | 154.6569 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 62.5048 | 4.9075 | 0.88873 | 109.6473 | 94.8722 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4085 | 47.5636 | 70.9719
CID=322770563 | 0 | 55 | 0 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 33451.2683 | 1.3943 | 0.036675 | 2.6 | 64.1651 | 166.8296 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 65.1661 | 5.2224 | 0.89846 | 110 | 108.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.837 | 71.2608
CID=-60310988 | 0 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 34179.6268 | 1.511 | 0.04119 | 2.4652 | 71.0549 | 175.1622 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 67.2261 | 5.5522 | 0.90398 | 110 | 119.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 4.741 | 60.8149 | 71.0549
CID=-1364272903 | 0 | 60 | 0 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34188.5699 | 1.4382 | 0.04127 | 2.3565 | 68.4511 | 161.3036 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 68.908 | 5.8975 | 0.90209 | 110 | 115.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=705852114 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-598109801 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-981191352 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2009814029 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-826474090 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2130436005 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1626729279 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=322767364 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-60314187 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1364276102 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=705848915 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-598113000 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-981194551 | 3 | 15 | 0 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 18490.092 | 0.4774 | 0.0072152 | 12.0959 | 7.0167 | 84.8736 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 22.9424 | 1.5081 | 0.66855 | 80.8526 | 15.9461 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=2009810830 | 3 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 18678.8836 | 0.5039 | 0.0076363 | 10.5637 | 8.3211 | 87.901 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 25.5785 | 1.635 | 0.68227 | 105.471 | 18.5302 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.1159 | 16.4081
CID=-826477289 | 3 | 20 | 0 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 19952.768 | 0.55709 | 0.0082905 | 9.3082 | 10.2391 | 95.3077 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 28.3358 | 1.7699 | 0.70109 | 107.0508 | 22.1894 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9492 | 7.4444 | 20.3842
CID=-2130439204 | 3 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 21150.1658 | 0.61016 | 0.0090666 | 8.3113 | 12.3116 | 102.325 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 30.9827 | 1.9131 | 0.71975 | 110 | 25.9887 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.8813 | 24.8225
CID=1626726332 | 3 | 25 | 0 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 22103.7668 | 0.63638 | 0.0097711 | 7.4881 | 13.9634 | 104.5589 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 33.5102 | 2.0648 | 0.73348 | 108.0934 | 28.9238 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.3039 | 29.7346
CID=322764417 | 3 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 23315.1688 | 0.71596 | 0.010956 | 6.8016 | 16.9353 | 115.1869 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 36.099 | 2.2255 | 0.75586 | 110 | 34.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.151 | 33.7526
CID=-60317134 | 3 | 30 | 0 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 24282.8445 | 0.76869 | 0.012069 | 6.2111 | 19.4855 | 121.0266 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 38.6034 | 2.3954 | 0.77291 | 110 | 38.3036 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.3139 | 39.5659
CID=-1364279049 | 3 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 25241.032 | 0.82127 | 0.013338 | 5.6706 | 22.3014 | 126.462 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 41.2076 | 2.575 | 0.78968 | 110 | 42.9078 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.265 | 45.7721
CID=705845968 | 3 | 35 | 0 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 26265.5824 | 0.90036 | 0.015021 | 5.1991 | 26.0631 | 135.5033 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 43.8309 | 2.7645 | 0.80914 | 110 | 48.9391 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.9753 | 52.4501
CID=-598115947 | 3 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 27068.7431 | 0.95268 | 0.016548 | 4.801 | 29.1683 | 140.0366 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 46.3125 | 2.9643 | 0.823 | 110 | 53.8477 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.2782 | 57.13
CID=-981197498 | 3 | 40 | 0 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 27798.0267 | 1.0049 | 0.018189 | 4.4555 | 32.3558 | 144.1626 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 48.7248 | 3.1747 | 0.83542 | 110 | 58.8437 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.2945 | 63.85
CID=2009807883 | 3 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 28671.3449 | 1.0834 | 0.020441 | 4.1128 | 36.8545 | 151.5746 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 51.3755 | 3.3962 | 0.8503 | 110 | 65.8527 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2941 | 70.4485
CID=-826480236 | 3 | 45 | 0 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 29473.1825 | 1.1617 | 0.022881 | 3.8158 | 41.5045 | 158.3725 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 53.9356 | 3.6291 | 0.86293 | 110 | 73.076 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.628 | 77.0074
CID=-2130442151 | 3 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 30070.1635 | 1.1867 | 0.02482 | 3.5288 | 44.6321 | 157.4961 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 56.6176 | 3.8738 | 0.87011 | 110 | 77.9341 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4646 | 78.0241
CID=1626731581 | 3 | 50 | 0 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 30646.678 | 1.2116 | 0.026839 | 3.2803 | 47.6767 | 156.3948 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 59.1921 | 4.1306 | 0.87623 | 109.6802 | 82.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1985 | 38.3198 | 78.3946
CID=322769666 | 3 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 31336.9713 | 1.2893 | 0.029935 | 3.0593 | 52.8531 | 161.6934 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 61.7341 | 4.4 | 0.88497 | 110 | 90.7399 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.5765 | 78.2557
CID=-60311885 | 3 | 55 | 0 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 31996.898 | 1.3401 | 0.032921 | 2.8434 | 57.3659 | 163.1162 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 64.4106 | 4.6823 | 0.89115 | 109.884 | 97.8049 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8999 | 48.3691 | 77.4469
CID=-1364273800 | 3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 32612.9014 | 1.3907 | 0.036174 | 2.6457 | 62.0203 | 164.086 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 67.0819 | 4.9781 | 0.89638 | 109.3261 | 105.1228 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.8459 | 78.4246
CID=705851217 | 3 | 60 | 0 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 33518.9714 | 1.5464 | 0.042052 | 2.4683 | 71.5602 | 176.629 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 69.7241 | 5.2877 | 0.90433 | 110 | 120.2268 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59.7005 | 78.6223
CID=-598110698 | 3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 34132.9211 | 1.6495 | 0.046678 | 2.3406 | 77.8125 | 182.1309 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 71.762 | 5.6115 | 0.90802 | 110 | 130.1993 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7218 | 68.5754 | 77.8125
CID=-981192249 | 3 | 65 | 0 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34220.7783 | 1.5949 | 0.047436 | 2.2349 | 76.0577 | 169.9779 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 73.5019 | 5.95 | 0.90708 | 110 | 127.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=2009813132 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-826474987 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2130436902 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1626728378 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=322766463 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-60315088 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1364277003 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=705848014 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-598113901 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-981195452 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2009809929 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-826478190 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2130440105 | 6 | 20 | 0 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 18504.8142 | 0.55857 | 0.0078112 | 10.993 | 8.797 | 96.7057 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 27.9126 | 1.5911 | 0.68709 | 102.9443 | 19.4528 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.8403 | 16.6703
CID=1626725179 | 6 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 19464.9412 | 0.58781 | 0.0083789 | 9.6662 | 10.3228 | 99.782 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 30.5219 | 1.7198 | 0.70188 | 108.1166 | 22.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.7456 | 20.9315
CID=322763264 | 6 | 25 | 0 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 20655.9554 | 0.6466 | 0.0092092 | 8.5791 | 12.538 | 107.5639 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 33.2119 | 1.8563 | 0.72169 | 109.9998 | 26.3955 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0005 | 9.3478 | 25.5163
CID=-60318287 | 6 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 21680.5703 | 0.68544 | 0.010022 | 7.7074 | 14.4903 | 111.683 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 35.7612 | 2.0007 | 0.73766 | 107.7879 | 29.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 8.3474 | 10.8391 | 30.6162
CID=-1364280202 | 6 | 30 | 0 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 22865.1055 | 0.76383 | 0.011214 | 6.9935 | 17.4201 | 121.827 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 38.2998 | 2.1535 | 0.75925 | 110 | 34.8598 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4236 | 34.7884
CID=705844815 | 6 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 23985.0328 | 0.85183 | 0.012645 | 6.3827 | 20.824 | 132.9137 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 40.8095 | 2.3149 | 0.78113 | 110 | 40.5038 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.4257 | 40.7528
CID=-598117100 | 6 | 35 | 0 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 24932.599 | 0.91007 | 0.014014 | 5.8253 | 23.8327 | 138.8323 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 43.3667 | 2.4852 | 0.79799 | 110 | 45.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.097 | 47.374
CID=-981198651 | 6 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 25831.7235 | 0.96818 | 0.015527 | 5.3381 | 27.0322 | 144.3013 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 45.9195 | 2.6649 | 0.81367 | 110 | 50.4765 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.3967 | 54.193
CID=2009806730 | 6 | 40 | 0 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 26763.1209 | 1.0556 | 0.017498 | 4.9204 | 31.2186 | 153.6092 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 48.432 | 2.8541 | 0.83119 | 110 | 57.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.7901 | 61.371
CID=-826481389 | 6 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 27531.3007 | 1.1134 | 0.01933 | 4.545 | 34.7765 | 158.0592 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 50.9338 | 3.0532 | 0.84379 | 110 | 62.6195 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0078 | 66.415
CID=-2130443304 | 6 | 45 | 0 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 28142.2886 | 1.1416 | 0.020943 | 4.2083 | 37.5384 | 157.9731 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 53.4168 | 3.2625 | 0.85232 | 110 | 66.9159 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0513 | 73.8077
CID=1626722232 | 6 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 28870.1446 | 1.199 | 0.023155 | 3.8912 | 41.5265 | 161.59 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 56.0224 | 3.4825 | 0.86299 | 110 | 73.1102 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5834 | 80.6463
CID=322760317 | 6 | 50 | 0 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 29646.7419 | 1.2856 | 0.026005 | 3.6095 | 46.705 | 168.5822 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 58.6096 | 3.7134 | 0.87437 | 110 | 81.1568 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.1297 | 86.4588
CID=-60321234 | 6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 30313.4381 | 1.3425 | 0.028705 | 3.3455 | 51.151 | 171.1234 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 61.2556 | 3.9556 | 0.88231 | 110 | 88.0825 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.549 | 86.5615
CID=-1364283149 | 6 | 55 | 0 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 30854.1955 | 1.37 | 0.031074 | 3.1117 | 54.4897 | 169.5554 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 63.8232 | 4.2094 | 0.88735 | 109.4941 | 93.2987 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5297 | 43.4253 | 85.8853
CID=705841868 | 6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 31459.5123 | 1.4265 | 0.034147 | 2.902 | 59.0044 | 171.232 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 66.3544 | 4.4753 | 0.89311 | 109.7696 | 100.3773 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9202 | 48.4863 | 86.5751
CID=-598120047 | 6 | 60 | 0 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 32091.772 | 1.4826 | 0.037646 | 2.695 | 63.9655 | 172.3862 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 69.0535 | 4.7536 | 0.89828 | 109.6799 | 108.1912 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.7344 | 86.0097
CID=-981201598 | 6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 32845.9418 | 1.5968 | 0.042724 | 2.5084 | 71.5958 | 179.5894 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 71.721 | 5.0447 | 0.90435 | 109.4271 | 120.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7745 | 60.5946 | 87.0244
CID=2009803783 | 6 | 65 | 0 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 33736.5743 | 1.7687 | 0.049672 | 2.3397 | 82.1174 | 192.1326 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 74.3395 | 5.349 | 0.91005 | 110 | 137.0968 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.1624 | 87.1744
CID=-826484336 | 6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 34154.7164 | 1.8243 | 0.053717 | 2.216 | 86.2309 | 191.091 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 76.3923 | 5.667 | 0.91166 | 110 | 143.7095 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7178 | 76.7476 | 86.2309
CID=-2130446251 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1626727481 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=322765566 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-60315985 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1364277900 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=705847117 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-598114798 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-981196349 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2009809032 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-826479087 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2130441002 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545001253 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=444244704 | 9 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 18478.5895 | 0.58476 | 0.0078638 | 11.4626 | 8.7639 | 100.4574 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 30.1286 | 1.5501 | 0.68675 | 86.2472 | 19.3889 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.3644 | 17.597
CID=-1142042213 | 9 | 25 | 0 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 19184.4652 | 0.64987 | 0.0086064 | 10.0576 | 10.8806 | 109.433 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 32.7827 | 1.6731 | 0.70705 | 109.9465 | 23.3809 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1339 | 7.5779 | 21.4167
CID=1566638166 | 9 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 20383.7508 | 0.71481 | 0.0095126 | 8.8886 | 13.267 | 117.9248 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 35.4596 | 1.8033 | 0.72781 | 110 | 27.6954 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3386 | 26.1844
CID=-375879111 | 9 | 30 | 0 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 21322.4891 | 0.74692 | 0.010328 | 7.9566 | 15.1639 | 120.6525 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 37.9922 | 1.941 | 0.74287 | 109.4534 | 31.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3666 | 11.0478 | 31.5026
CID=-476635660 | 9 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 22408.4163 | 0.81164 | 0.011456 | 7.1936 | 17.835 | 128.2976 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 40.5135 | 2.0864 | 0.76209 | 110 | 35.5569 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9917 | 37.3388
CID=-2062922577 | 9 | 35 | 0 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 23397.0968 | 0.87622 | 0.01272 | 6.5434 | 20.7009 | 135.4542 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 43.0118 | 2.24 | 0.7804 | 110 | 40.3023 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.0271 | 41.988
CID=645757802 | 9 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 24333.3124 | 0.94066 | 0.014124 | 5.9808 | 23.7624 | 142.1178 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 45.4982 | 2.4019 | 0.79762 | 110 | 45.2639 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4302 | 48.8161
CID=-1908205315 | 9 | 40 | 0 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 25249.2861 | 1.0049 | 0.015713 | 5.4697 | 27.1089 | 148.2782 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 48.0591 | 2.5724 | 0.81402 | 110 | 50.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.739 | 55.9939
CID=-2008961864 | 9 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 26238.8726 | 1.1016 | 0.017832 | 5.0185 | 31.6077 | 158.6227 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 50.6531 | 2.7519 | 0.83266 | 110 | 57.6742 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9419 | 63.7251
CID=545006502 | 9 | 45 | 0 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 27007.9814 | 1.1655 | 0.019742 | 4.6388 | 35.2795 | 163.6552 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 53.1078 | 2.9406 | 0.84542 | 110 | 63.4027 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6277 | 69.0029
CID=444249953 | 9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 27717.9974 | 1.2293 | 0.021811 | 4.3033 | 39.08 | 168.1746 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 55.5305 | 3.1388 | 0.85666 | 110 | 69.3108 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.871 | 76.6845
CID=-1142036964 | 9 | 50 | 0 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 28551.209 | 1.3252 | 0.024624 | 3.978 | 44.3644 | 176.4825 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 58.124 | 3.3469 | 0.86954 | 110 | 77.5181 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.4252 | 84.4459
CID=1566643415 | 9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 29339.753 | 1.4209 | 0.02772 | 3.6864 | 49.9167 | 184.0135 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 60.7024 | 3.5652 | 0.88025 | 110 | 86.1577 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2376 | 90.1325
CID=-375873862 | 9 | 55 | 0 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 29799.4457 | 1.419 | 0.0296 | 3.4127 | 52.3112 | 178.5227 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 63.3199 | 3.794 | 0.88414 | 110 | 89.8935 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.4435 | 90.1325
CID=-476630411 | 9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 30443.9263 | 1.4818 | 0.032697 | 3.1686 | 57.0887 | 180.889 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 65.9259 | 4.0336 | 0.8908 | 110 | 97.37 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.1717 | 90.1326
CID=-2062917328 | 9 | 60 | 0 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 31030.6759 | 1.5443 | 0.036039 | 2.9495 | 61.9451 | 182.705 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 68.4889 | 4.2845 | 0.8963 | 110 | 105.0044 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2777 | 90.1326
CID=645763051 | 9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 31638.5424 | 1.6065 | 0.0397 | 2.7466 | 66.9768 | 183.9553 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 71.0669 | 4.5468 | 0.90091 | 109.9905 | 112.9528 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2371 | 55.0994 | 90.1325
CID=-1908200066 | 9 | 65 | 0 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 32161.9214 | 1.636 | 0.04313 | 2.5491 | 71.0245 | 181.051 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 73.7609 | 4.8211 | 0.90396 | 109.3531 | 119.375 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.5516 | 90.1325
CID=-2008956615 | 9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 32894.1647 | 1.7617 | 0.049091 | 2.3699 | 79.383 | 188.1301 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 76.4427 | 5.1077 | 0.9088 | 109.3237 | 132.7127 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.8089 | 90.1325
CID=545003299 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=444246750 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1142040167 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1566640212 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-375877065 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-476633614 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2062920531 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=645759848 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1908203269 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2008959818 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545000100 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=444243551 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1142043366 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1566637013 | 12 | 25 | 0 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 18462.9745 | 0.64496 | 0.008032 | 11.988 | 9.1686 | 109.9127 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 32.4226 | 1.5117 | 0.69078 | 81.9557 | 20.166 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.9035 | 14.4449
CID=-375880264 | 12 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 18670.2209 | 0.68059 | 0.0086733 | 10.4624 | 10.8636 | 113.6588 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 34.9904 | 1.6293 | 0.70689 | 105.6502 | 23.3495 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.806 | 21.8594
CID=-476636813 | 12 | 30 | 0 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 19892.128 | 0.75219 | 0.0096277 | 9.2011 | 13.371 | 123.0286 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 37.6806 | 1.7537 | 0.72867 | 107.8864 | 27.8797 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1136 | 9.6007 | 26.8405
CID=-2062923730 | 12 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 21033.023 | 0.82366 | 0.010717 | 8.2126 | 16.0566 | 131.8666 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 40.2615 | 1.8852 | 0.74954 | 110 | 32.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4509 | 32.3474
CID=645756649 | 12 | 35 | 0 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 21930.7867 | 0.85897 | 0.011683 | 7.3987 | 18.1826 | 134.5276 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 42.7506 | 2.0239 | 0.76443 | 109.1632 | 36.1387 | 0 | 0 | 0 | 0 | 0 | 0 | 7.092 | 13.2216 | 38.3861
CID=-1908206468 | 12 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 22943.9067 | 0.93019 | 0.013019 | 6.7189 | 21.1968 | 142.4194 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 45.2399 | 2.1702 | 0.78334 | 110 | 41.1126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1077 | 43.1811
CID=-2008963017 | 12 | 40 | 0 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 23873.7258 | 1.0013 | 0.0145 | 6.1383 | 24.3987 | 149.7664 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 47.6972 | 2.3243 | 0.80092 | 110 | 46.2843 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6528 | 50.1588
CID=544997153 | 12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 24798.6168 | 1.0721 | 0.016188 | 5.6057 | 27.9279 | 156.5545 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 50.25 | 2.4864 | 0.81769 | 110 | 51.8929 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6832 | 57.8258
CID=444240604 | 12 | 45 | 0 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 25803.0365 | 1.1787 | 0.018432 | 5.1431 | 32.6449 | 167.897 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 52.8045 | 2.6569 | 0.83647 | 110 | 59.2955 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3728 | 65.6764
CID=-1142046313 | 12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 26705.3483 | 1.2851 | 0.020909 | 4.7416 | 37.6262 | 178.4089 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 55.3115 | 2.836 | 0.85257 | 110 | 67.0524 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.1625 | 73.9419
CID=1566634066 | 12 | 50 | 0 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 27447.439 | 1.3553 | 0.023204 | 4.3812 | 41.8227 | 183.2339 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 57.8077 | 3.0241 | 0.86371 | 110 | 73.5701 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.7952 | 79.5389
CID=-375883211 | 12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 28015.2954 | 1.3896 | 0.025191 | 4.0637 | 44.9772 | 182.7745 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 60.2489 | 3.2213 | 0.87085 | 110 | 78.4705 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.0954 | 87.9361
CID=-476639760 | 12 | 55 | 0 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 28720.5613 | 1.4594 | 0.027975 | 3.7558 | 49.6713 | 186.5548 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 62.8573 | 3.428 | 0.87983 | 110 | 85.7752 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3247 | 90.1325
CID=-2062926677 | 12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 29467.5142 | 1.5647 | 0.031534 | 3.4864 | 55.6951 | 194.1748 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 65.4091 | 3.6445 | 0.889 | 110 | 95.1857 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.1087 | 90.1325
CID=645753702 | 12 | 60 | 0 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 30018.0849 | 1.5981 | 0.034352 | 3.2252 | 59.6273 | 192.31 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 68.077 | 3.8712 | 0.89382 | 110 | 101.3562 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.939 | 90.1325
CID=-1908209415 | 12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 30548.9354 | 1.6314 | 0.03731 | 2.9966 | 63.4452 | 190.1178 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 70.6581 | 4.1083 | 0.89778 | 109.8554 | 107.3699 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4463 | 50.8496 | 90.1325
CID=-2008965964 | 12 | 65 | 0 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 31182.36 | 1.7357 | 0.041912 | 2.7889 | 70.1358 | 195.5996 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 73.2375 | 4.3561 | 0.90334 | 110 | 117.9628 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.6734 | 90.1325
CID=545002402 | 12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 31711.4893 | 1.7683 | 0.045525 | 2.5917 | 74.2431 | 192.4192 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 75.8593 | 4.615 | 0.90604 | 109.8728 | 124.4993 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1806 | 62.1983 | 90.1326
CID=444245853 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1142041064 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1566639315 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-375877962 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-476634511 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2062921428 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=645758951 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1908204166 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2008960715 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=544999199 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=444242650 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1142044267 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1566636112 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-375881165 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-476637714 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18440.3342 | 0.66993 | 0.0080535 | 12.5859 | 8.9962 | 113.225 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 34.5993 | 1.4757 | 0.68907 | 69.2139 | 19.8358 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=-2062924631 | 15 | 30 | 0 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 18463.992 | 0.74882 | 0.0089199 | 10.8357 | 11.4421 | 123.9835 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 37.3587 | 1.5883 | 0.71213 | 103.3181 | 24.4121 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.6958 | 22.1642
CID=645755748 | 15 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 19400.0337 | 0.7879 | 0.0097218 | 9.5347 | 13.3961 | 127.7268 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 39.9083 | 1.7074 | 0.72888 | 108.089 | 27.924 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.9438 | 27.4707
CID=-1908207369 | 15 | 35 | 0 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 20542.229 | 0.86651 | 0.010883 | 8.4561 | 16.2546 | 137.4504 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 42.5428 | 1.833 | 0.75098 | 110 | 32.8853 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8586 | 33.1342
CID=-2008963918 | 15 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 21448.8628 | 0.90537 | 0.011901 | 7.5971 | 18.486 | 140.4403 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 45.039 | 1.9655 | 0.76645 | 107.8012 | 36.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.9017 | 39.38
CID=544996000 | 15 | 40 | 0 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 22489.0863 | 0.98372 | 0.013307 | 6.8929 | 21.6341 | 149.1215 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 47.5076 | 2.1051 | 0.78589 | 109.5564 | 41.8248 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2179 | 15.8898 | 45.3962
CID=444239451 | 15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 23546.3778 | 1.09 | 0.015134 | 6.2795 | 25.6946 | 161.3489 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 50.0097 | 2.2519 | 0.80737 | 110 | 48.353 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2373 | 51.5431
CID=-1142047466 | 15 | 45 | 0 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 24343.5219 | 1.1399 | 0.016645 | 5.7448 | 28.6626 | 164.6623 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 52.468 | 2.4063 | 0.82087 | 110 | 53.0516 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.0094 | 59.4744
CID=1566632913 | 15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 25220.6579 | 1.2177 | 0.018624 | 5.2604 | 32.6029 | 171.504 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 55.0097 | 2.5686 | 0.83632 | 110 | 59.2298 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.7775 | 67.6857
CID=-375884364 | 15 | 50 | 0 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 26175.2423 | 1.3347 | 0.021274 | 4.8299 | 37.9154 | 183.1276 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 57.5873 | 2.7389 | 0.85341 | 110 | 67.5018 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.453 | 76.5318
CID=-476640913 | 15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 26911.7916 | 1.4121 | 0.023654 | 4.4674 | 42.2094 | 188.5676 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 60.0355 | 2.9175 | 0.86464 | 110 | 74.1707 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.551 | 82.4122
CID=-2062927830 | 15 | 55 | 0 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 27603.017 | 1.4892 | 0.026256 | 4.1415 | 46.6899 | 193.3646 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 62.4851 | 3.1047 | 0.87434 | 110 | 81.1334 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.9713 | 90.1325
CID=645752549 | 15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 28398.247 | 1.6054 | 0.029758 | 3.8323 | 52.8287 | 202.4557 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 65.0469 | 3.3008 | 0.88493 | 110 | 90.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3346 | 90.1325
CID=-1908210568 | 15 | 60 | 0 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 28860.4167 | 1.6033 | 0.031825 | 3.5444 | 55.3426 | 196.1585 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 67.6335 | 3.5061 | 0.88852 | 110 | 94.6337 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.1963 | 90.1325
CID=-2008967117 | 15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 29589.1759 | 1.7188 | 0.035995 | 3.2862 | 62.0021 | 203.7525 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 70.236 | 3.7208 | 0.89636 | 110 | 105.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.6943 | 90.1325
CID=544993053 | 15 | 65 | 0 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 30191.726 | 1.7877 | 0.039822 | 3.0439 | 67.3659 | 205.0581 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 72.886 | 3.9453 | 0.90123 | 110 | 113.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.93 | 90.1325
CID=444236504 | 15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 30624.209 | 1.7919 | 0.042674 | 2.8271 | 70.2438 | 198.5833 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 75.4723 | 4.1798 | 0.90342 | 109.4505 | 118.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.5173 | 90.1325
CID=-1142050413 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1566629966 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-375887311 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-476643860 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2062930777 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=645749602 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1908213515 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2008970064 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=544998302 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=444241753 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1142045164 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1566635215 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-375882062 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-476638611 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2062925528 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=645754851 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1908208266 | 18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 18411.311 | 0.77848 | 0.0089793 | 11.2311 | 11.3748 | 127.7519 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 39.6611 | 1.5499 | 0.71152 | 87.5903 | 24.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.4876 | 22.9766
CID=-2008964815 | 18 | 35 | 0 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 19120.6563 | 0.86492 | 0.010027 | 9.8787 | 14.063 | 138.9252 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 42.219 | 1.664 | 0.73428 | 109.8888 | 29.0986 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2779 | 9.6985 | 28.0193
CID=-909871350 | 18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 20268.1164 | 0.95117 | 0.011275 | 8.7397 | 17.0994 | 149.443 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 44.8268 | 1.7842 | 0.75701 | 110 | 34.3188 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8592 | 33.8929
CID=2081134031 | 18 | 40 | 0 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 21154.9458 | 0.99382 | 0.012376 | 7.829 | 19.496 | 152.6346 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 47.3233 | 1.9109 | 0.77297 | 110 | 38.321 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.906 | 40.396
CID=-2032264812 | 18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 22017.1723 | 1.0364 | 0.013565 | 7.0797 | 21.9622 | 155.486 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 49.7742 | 2.0442 | 0.78777 | 108.1287 | 42.3579 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.0656 | 47.4637
CID=958740569 | 18 | 45 | 0 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 22984.7006 | 1.1222 | 0.015236 | 6.4372 | 25.5302 | 164.3429 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 52.2584 | 2.1844 | 0.80657 | 109.6435 | 48.0912 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7823 | 18.496 | 52.9123
CID=11009014 | 18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 23875.5902 | 1.2079 | 0.017076 | 5.8905 | 29.2893 | 172.5282 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 54.7021 | 2.3317 | 0.8235 | 110 | 54.0379 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.5596 | 60.9897
CID=-1292952901 | 18 | 50 | 0 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 24766.4095 | 1.2932 | 0.019182 | 5.3821 | 33.4482 | 180.0217 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 57.2577 | 2.4862 | 0.83931 | 110 | 60.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7665 | 69.7483
CID=-1111384448 | 18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 25736.4994 | 1.4217 | 0.021983 | 4.9407 | 39.0005 | 192.688 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 59.8087 | 2.6484 | 0.85644 | 110 | 69.1874 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8781 | 78.6886
CID=1879620933 | 18 | 55 | 0 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 26610.4597 | 1.5498 | 0.025084 | 4.5545 | 44.862 | 204.3248 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 62.3278 | 2.8184 | 0.8706 | 110 | 78.2915 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.0948 | 88.1043
CID=931889378 | 18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 27327.6999 | 1.6345 | 0.027955 | 4.2076 | 49.7637 | 209.3839 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 64.8401 | 2.9964 | 0.87999 | 110 | 85.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0067 | 90.1325
CID=-372072537 | 18 | 60 | 0 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 27751.387 | 1.6326 | 0.029797 | 3.9058 | 51.9746 | 203.0011 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 67.2626 | 3.1827 | 0.88362 | 110 | 89.3679 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.0194 | 90.1325
CID=-909866101 | 18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 28535.3854 | 1.7598 | 0.033899 | 3.6088 | 58.7783 | 212.1203 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 69.8874 | 3.3776 | 0.89285 | 110 | 100.022 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.2784 | 90.1325
CID=2081139280 | 18 | 65 | 0 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 29266.7443 | 1.8865 | 0.038383 | 3.3465 | 65.7876 | 220.1563 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 72.4592 | 3.5814 | 0.89991 | 110 | 111.0707 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0659 | 90.1326
CID=-2032259563 | 18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 29686.8008 | 1.8837 | 0.041155 | 3.0931 | 68.7082 | 212.5235 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 75.1208 | 3.7943 | 0.90228 | 110 | 115.6967 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.0188 | 90.1325
CID=958745818 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=11014263 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1292947652 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1111379199 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1879626182 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=931894627 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-372067288 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-909869304 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2081136077 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2032262766 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=958742615 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=11011060 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1292950855 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1111382402 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1879622979 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=931891424 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-372070491 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-909872503 | 21 | 35 | 0 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 18374.7383 | 0.85278 | 0.0091993 | 11.7297 | 11.8214 | 138.6619 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 41.95 | 1.5138 | 0.71549 | 83.0814 | 25.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.9152 | 20.974
CID=2081132878 | 21 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 18605.6544 | 0.89978 | 0.01009 | 10.2549 | 13.9591 | 143.1485 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 44.469 | 1.6232 | 0.73345 | 105.8872 | 28.9163 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.8342 | 28.5245
CID=-2032265965 | 21 | 40 | 0 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 19777.4233 | 0.99424 | 0.011406 | 9.017 | 17.1528 | 154.666 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 47.1162 | 1.7385 | 0.75739 | 108.4118 | 34.409 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5882 | 12.2151 | 34.6277
CID=958739416 | 21 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 20658.5389 | 1.041 | 0.012567 | 8.0436 | 19.6721 | 158.2337 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 49.6402 | 1.8598 | 0.77408 | 108.7475 | 38.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1313 | 14.5417 | 41.3248
CID=11007861 | 21 | 45 | 0 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 21531.4464 | 1.0876 | 0.013817 | 7.2562 | 22.2469 | 161.4277 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 52.1006 | 1.9873 | 0.78938 | 106.2601 | 42.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.752 | 48.6019
CID=-1292954054 | 21 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 22527.1682 | 1.1816 | 0.015572 | 6.591 | 25.9625 | 171.1186 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 54.5738 | 2.1213 | 0.80866 | 109 | 48.7791 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.0805 | 54.2307
CID=-1111385601 | 21 | 50 | 0 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 23585.2388 | 1.3229 | 0.01797 | 6.0142 | 31.0538 | 186.7648 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 57.0709 | 2.2619 | 0.83055 | 110 | 56.8071 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9077 | 62.5046
CID=1879619780 | 21 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 24449.6166 | 1.4164 | 0.020201 | 5.5046 | 35.3848 | 194.7779 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 59.5612 | 2.4094 | 0.84575 | 110 | 63.5665 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.2501 | 71.6014
CID=931888225 | 21 | 55 | 0 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 25153.8601 | 1.4623 | 0.022182 | 5.0434 | 38.7997 | 195.6834 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 62.0885 | 2.564 | 0.85589 | 110 | 68.8755 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.3799 | 80.9026
CID=-372073690 | 21 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 26073.9413 | 1.6027 | 0.025482 | 4.6327 | 45.0032 | 208.487 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 64.6676 | 2.726 | 0.8709 | 110 | 78.5108 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.5224 | 90.1325
CID=-909875450 | 21 | 60 | 0 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 26661.2719 | 1.6483 | 0.027826 | 4.2858 | 48.5802 | 208.2059 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 67.1167 | 2.8955 | 0.8779 | 110 | 84.0754 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.0509 | 90.1326
CID=2081129931 | 21 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 27451.7104 | 1.788 | 0.031714 | 3.9687 | 55.1987 | 219.0653 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 69.6219 | 3.0728 | 0.88833 | 110 | 94.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.8051 | 90.1326
CID=-2032268912 | 21 | 65 | 0 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 27999.8827 | 1.833 | 0.034653 | 3.6715 | 59.2489 | 217.5343 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 72.1704 | 3.2582 | 0.89339 | 110 | 100.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3855 | 90.1326
CID=958736469 | 21 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 28647.8306 | 1.9247 | 0.038685 | 3.3938 | 65.1045 | 220.954 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 74.7916 | 3.4519 | 0.89931 | 110 | 109.9905 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2427 | 90.1326
CID=11004914 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1292957001 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1111388548 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1879616833 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=931885278 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-372076637 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-909870201 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2081135180 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2032263663 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=958741718 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=11010163 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1292951752 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1111383299 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1879622082 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=931890527 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-372071388 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-909873404 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2081131977 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2032266866 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18330.5158 | 0.88013 | 0.0092176 | 12.2242 | 11.5956 | 141.7459 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 44.2283 | 1.4799 | 0.71349 | 70.3891 | 24.6921 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=958738515 | 24 | 40 | 0 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 18360.943 | 0.98356 | 0.010416 | 10.5836 | 14.6387 | 154.9309 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 46.8717 | 1.5849 | 0.73882 | 103.7413 | 30.1036 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.888 | 28.8692
CID=11006960 | 24 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 19282.0352 | 1.0348 | 0.011501 | 9.3247 | 17.0859 | 159.3215 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 49.3928 | 1.6955 | 0.75692 | 108.0847 | 34.2961 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.5977 | 35.3309
CID=-1292954955 | 24 | 45 | 0 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 20376.0354 | 1.1378 | 0.013069 | 8.2733 | 20.6827 | 171.114 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 51.9942 | 1.8118 | 0.78029 | 110 | 40.2724 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8492 | 42.1901
CID=-1111386502 | 24 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 21231.9778 | 1.1888 | 0.014419 | 7.4432 | 23.4425 | 174.4882 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 54.4643 | 1.9339 | 0.79592 | 108.6712 | 44.7497 | 0 | 0 | 0 | 0 | 0 | 0 | 8.322 | 17.2586 | 49.7239
CID=1879618879 | 24 | 50 | 0 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 22064.9918 | 1.2397 | 0.015877 | 6.7525 | 26.2784 | 177.4442 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 56.8998 | 2.0621 | 0.81017 | 108.7979 | 49.2811 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.8019 | 57.9119
CID=931887324 | 24 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 22985.2881 | 1.3422 | 0.017943 | 6.1515 | 30.4321 | 187.2034 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 59.3789 | 2.1966 | 0.82813 | 109.1326 | 55.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3369 | 22.5727 | 64.0509
CID=-372074591 | 24 | 55 | 0 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 23836.8313 | 1.4446 | 0.020216 | 5.6376 | 34.7909 | 196.1373 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 61.8238 | 2.3376 | 0.84383 | 110 | 62.642 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0461 | 73.2965
CID=-909876603 | 24 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 24694.7485 | 1.5466 | 0.022836 | 5.1516 | 39.642 | 204.2178 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 64.4005 | 2.4852 | 0.85817 | 110 | 70.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.3599 | 83.1958
CID=2081128778 | 24 | 60 | 0 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 25631.5211 | 1.7 | 0.026324 | 4.7295 | 46.1105 | 218.0796 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 66.9674 | 2.6398 | 0.87319 | 110 | 80.2322 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.9235 | 90.1325
CID=-2032270065 | 24 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 26354.1583 | 1.8015 | 0.029531 | 4.3579 | 51.4561 | 224.2419 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 69.5012 | 2.8015 | 0.8828 | 110 | 88.5586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5949 | 90.1326
CID=958735316 | 24 | 65 | 0 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 27049.6798 | 1.9026 | 0.033058 | 4.0248 | 57.0268 | 229.5213 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 72.0372 | 2.9705 | 0.89072 | 110 | 97.2729 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7589 | 90.1326
CID=11003761 | 24 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 27553.0727 | 1.9519 | 0.036058 | 3.7368 | 60.9869 | 227.8968 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 74.4869 | 3.147 | 0.89531 | 110 | 103.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.532 | 90.1326
CID=-1292958154 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1111389701 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1879615680 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=931884125 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-372077790 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-909879550 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2081125831 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2032273012 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=958732369 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=11000814 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1292961101 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1111392648 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1879612733 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=931881178 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-372080737 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-909874301 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2081131080 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2032267763 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=958737618 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=11006063 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1292955852 | 27 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 18279.5024 | 1.073 | 0.010755 | 10.9182 | 15.3215 | 167.2834 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 49.2907 | 1.5489 | 0.74406 | 100.8387 | 31.2858 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.0582 | 29.3459
CID=-1111387399 | 27 | 45 | 0 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 18999.9929 | 1.1289 | 0.011896 | 9.6299 | 17.8564 | 171.955 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 51.7523 | 1.6551 | 0.76223 | 109.7304 | 35.5929 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6739 | 12.2922 | 35.9335
CID=1879617982 | 27 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 20097.7705 | 1.2413 | 0.013566 | 8.5317 | 21.6367 | 184.5981 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 54.3259 | 1.7667 | 0.7859 | 110 | 41.829 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8597 | 43.0269
CID=931886427 | 27 | 50 | 0 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 20936.3039 | 1.2969 | 0.015027 | 7.6476 | 24.6021 | 188.1466 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 56.8184 | 1.8839 | 0.80196 | 110 | 46.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4382 | 50.8249
CID=-372075488 | 27 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 21749.6993 | 1.3523 | 0.016608 | 6.9154 | 27.6535 | 191.2339 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 59.2806 | 2.0067 | 0.81647 | 108.7995 | 51.4594 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0012 | 19.9821 | 59.2263
CID=-1991600529 | 27 | 55 | 0 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 22523.6758 | 1.4076 | 0.018332 | 6.2879 | 30.8293 | 193.8509 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 61.7452 | 2.1355 | 0.82969 | 109 | 56.4554 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.6823 | 65.5153
CID=-2092357078 | 27 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 23536.7317 | 1.5758 | 0.021299 | 5.7457 | 36.7454 | 211.1286 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 64.2461 | 2.2704 | 0.84997 | 110 | 65.6832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0535 | 74.9452
CID=1180973305 | 27 | 60 | 0 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 24375.433 | 1.6871 | 0.024078 | 5.2567 | 41.7919 | 219.6888 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 66.7762 | 2.4116 | 0.86363 | 110 | 73.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1043 | 85.2525
CID=-405313612 | 27 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 25047.9962 | 1.7417 | 0.026531 | 4.8175 | 45.7033 | 220.176 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 69.3285 | 2.5593 | 0.87236 | 110 | 79.5992 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.5524 | 90.1325
CID=-1070720165 | 27 | 65 | 0 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 25934.0095 | 1.9087 | 0.030636 | 4.425 | 52.8722 | 233.9602 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 71.9256 | 2.7136 | 0.885 | 110 | 90.7698 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.1555 | 90.1326
CID=-1171476714 | 27 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 26493.0588 | 1.9628 | 0.033559 | 4.0914 | 56.9434 | 232.9776 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 74.4116 | 2.875 | 0.89062 | 110 | 97.1421 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9411 | 90.1326
CID=2101853669 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=515566752 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-149839801 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-250596350 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1991595280 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2092351829 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1180978554 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405308363 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1070714916 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1171471465 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2101858918 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=515572001 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-149834552 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-250591101 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1991598483 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2092355032 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1180975351 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405311566 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1070718119 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1171474668 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2101855715 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=515568798 | 30 | 45 | 0 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 18219.6456 | 1.1066 | 0.010757 | 11.3881 | 14.9875 | 170.6793 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 51.5487 | 1.515 | 0.74152 | 84.2604 | 30.7088 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.2153 | 30.0035
CID=-149837755 | 30 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 18486.0713 | 1.1675 | 0.011958 | 9.9615 | 17.6536 | 175.8556 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 54.0715 | 1.6171 | 0.76085 | 106.2834 | 35.2525 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.6305 | 36.4854
CID=-250594304 | 30 | 50 | 0 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 19604.9982 | 1.2899 | 0.01371 | 8.7785 | 21.5983 | 189.6012 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 56.6809 | 1.7244 | 0.78568 | 108.5598 | 41.7667 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4402 | 15.2979 | 43.826
CID=-1991601682 | 30 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 20438.6931 | 1.3504 | 0.015244 | 7.8401 | 24.6872 | 193.549 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 59.1996 | 1.8368 | 0.80239 | 109.1939 | 46.7459 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0152 | 18.16 | 51.8244
CID=-2092358231 | 30 | 55 | 0 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 21264.4284 | 1.4108 | 0.016899 | 7.0726 | 27.8528 | 196.9918 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 61.6778 | 1.9547 | 0.81736 | 107.0925 | 51.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.8596 | 60.4554
CID=1180972152 | 30 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 22063.4413 | 1.4711 | 0.018693 | 6.4255 | 31.1139 | 199.9207 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 64.1382 | 2.0782 | 0.83078 | 108.5595 | 56.9012 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.677 | 68.5376
CID=-405314765 | 30 | 60 | 0 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 22943.4466 | 1.5927 | 0.021248 | 5.8594 | 35.9164 | 210.4487 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 66.6401 | 2.2074 | 0.84743 | 109 | 64.3939 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.9058 | 76.6398
CID=-1070721318 | 30 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 23764.6784 | 1.714 | 0.024065 | 5.3717 | 40.9492 | 219.9651 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 69.1186 | 2.3426 | 0.86155 | 109.8881 | 72.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1194 | 30.8512 | 87.1331
CID=-1171477867 | 30 | 65 | 0 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 24583.4079 | 1.8349 | 0.027304 | 4.9115 | 46.5102 | 228.4364 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 71.7119 | 2.4839 | 0.87398 | 110 | 80.8539 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4695 | 90.1325
CID=2101852516 | 30 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 25487.3246 | 2.0168 | 0.031645 | 4.5071 | 53.9713 | 243.2539 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 74.309 | 2.6315 | 0.88661 | 110 | 92.4879 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.5113 | 90.1325
CID=515565599 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0

## TGH285-noEcon_APower 0
PN | 2718315
Calculation Type | FROM_POWER
Units | SI
Use Economizer? | FALSE
Compressor | TGH285-E-3-MT-SL
| Step SST | Step SDT | Percent Power |  | Subcooling
| 3 | 2.5 | 0 |  | 6 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 11 | 11
| INPUT BLOCK | [5 empty] | 1: OUTPUT
CID | SST Verd. Temp | SDT Kond. Temperatur | Value Power | SSH Superheat | LLT Leaving Liquid Temp | tapp T approach Economizer | ENTROPY_SUCTION | SPEED_SOUND | DENSITY_SUCTION | ENTHALPY_LIQUID_CONDENSER_EXIT | ENTHALPY_DISCHARGE_ISENTROPIC | ENTHALPY_SUCTION | SPEED_COMPRESSOR | MASS_FLOW_RATE_EVAPORATOR | MASS_FLOW_RATE_MOTOR_COOLING | COEFFICIENT_OF_PERFORMANCE | POWER_INPUT_ELECTRICAL | CAPACITY_EVAPORATOR | TEMPERATURE_SUCT_SAT | TEMPERATURE_DISCH_SAT | TEMPERATURE_SUCT_SUPER_HEAT | TEMPERATURE_CONDENSER_LIQUID_LEAVING | PRESSURE_SUCT_ABSOLUTE | PRESSURE_DISCH_ABSOLUTE | TEMPERATURE_DISCH | PRESSURE_RATIO | POWER_FACTOR | IGV_ANGLE | INPUT_CURRENT | ECON_SAT_TEMP | ECON_INTERSTAGE_P | ECON_CAPACITY | ECON_MASS_FLOW | TEMPERATURE_ECO_LIQUID_LEAVING | ENTHALPY_LIQUID_ECO_EXIT | TOLERANCE | POWER_INPUT_ELECTRICAL | POWER_INPUT_ELECTRICAL
CID=131910985 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-251170566 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1555132481 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=514992536 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-788969379 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1172050930 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1818954451 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405887828 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1709849743 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1435871747 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=131909832 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-251171719 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1555133634 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=514991383 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-788970532 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1172052083 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1818953298 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405888981 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1709850896 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1435866498 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=131904583 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-251176968 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1555138883 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=514986134 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-788975781 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1172057332 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1818948049 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405894230 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1709856145 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1435873801 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=131911886 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-251169665 | -15 | -5 | 3.8194 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18379.9421 | 0.21348 | 0.0069779 | 10.6284 | 3.8194 | 40.594 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 3.9657 | 1.4946 | 0.6315 | 60.0336 | 9.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=-1555131580 | -15 | -2.5 | 3.8092 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 18258.0774 | 0.16427 | 0.0070592 | 8.1171 | 3.8092 | 30.9202 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 8.051 | 1.6437 | 0.63137 | 42.6137 | 9.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1631 | 3.8092 | 8.6947
CID=514993437 | -15 | 0 | 4.4307 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 19735.2322 | 0.1724 | 0.0068375 | 7.198 | 4.4307 | 31.8924 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 12.1262 | 1.804 | 0.63898 | 28.5396 | 10.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.4307 | 11.0329
CID=-788968478 | -15 | 2.5 | 5.2867 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 20805.0487 | 0.19271 | 0.0068619 | 6.6252 | 5.2867 | 35.0254 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 15.5052 | 1.9762 | 0.64914 | 54.3169 | 12.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.2867 | 13.7049
CID=-1172050029 | -15 | 5 | 6.1823 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 22223.2326 | 0.21354 | 0.007054 | 6.1652 | 6.1823 | 38.1149 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 18.3245 | 2.1607 | 0.65937 | 46.0636 | 14.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.1823 | 16.1956
CID=1818955352 | -15 | 7.5 | 7.2299 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 23424.1101 | 0.22817 | 0.0073625 | 5.5296 | 7.2299 | 39.9786 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 22.0414 | 2.3583 | 0.67085 | 51.2498 | 16.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.2299 | 19.3754
CID=-405886927 | -15 | 10 | 8.5747 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 24387.515 | 0.25415 | 0.0078105 | 5.0956 | 8.5747 | 43.6936 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 25.1914 | 2.5693 | 0.68485 | 65.3109 | 19.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5747 | 23.0861
CID=-1709848842 | -15 | 12.5 | 10.0921 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 25518.2818 | 0.28116 | 0.0083705 | 4.6975 | 10.0921 | 47.408 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 28.3226 | 2.7945 | 0.6997 | 91.1196 | 21.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.0921 | 27.0734
CID=1435877000 | -15 | 15 | 11.5676 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 26685.2565 | 0.30061 | 0.0089729 | 4.2955 | 11.5676 | 49.6882 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 31.6805 | 3.0345 | 0.71324 | 66.6222 | 24.6411 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.5676 | 30.0979
CID=131915085 | -15 | 17.5 | 13.3575 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 27710.9998 | 0.32719 | 0.0097193 | 3.9669 | 13.3575 | 52.9875 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 34.8318 | 3.2899 | 0.72856 | 62.5656 | 27.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.3575 | 34.2767
CID=-251166466 | -15 | 20 | 15.3391 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 29040.967 | 0.35269 | 0.010579 | 3.6463 | 15.3391 | 55.9317 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 38.2193 | 3.5612 | 0.7442 | 54.2825 | 31.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.3391 | 38.2422
CID=-1555128381 | -15 | 22.5 | 17.6718 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 29698.7413 | 0.38822 | 0.011611 | 3.4096 | 17.6718 | 60.2545 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 41.0371 | 3.8493 | 0.76098 | 60.9766 | 35.283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.6718 | 39.9189
CID=514996636 | -15 | 25 | 19.9411 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 30609.0676 | 0.41473 | 0.01268 | 3.1572 | 19.9411 | 62.9588 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 44.2438 | 4.1546 | 0.77576 | 62.7732 | 39.055 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.9411 | 40.1319
CID=-788965279 | -15 | 27.5 | 22.9327 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 31266.0418 | 0.45013 | 0.014074 | 2.9126 | 22.9327 | 66.7946 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 47.7398 | 4.4779 | 0.79317 | 73.0309 | 43.9283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9327 | 40.079
CID=-1172046830 | -15 | 30 | 26.5427 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 31930.2043 | 0.49858 | 0.015779 | 2.7227 | 26.5427 | 72.2681 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 50.7324 | 4.8198 | 0.81141 | 97.8722 | 49.7007 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.5427 | 40.0954
CID=1818958551 | -15 | 32.5 | 30.1228 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 32831.9828 | 0.54601 | 0.017566 | 2.5646 | 30.1229 | 77.2539 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 53.36 | 5.1811 | 0.8269 | 86.677 | 55.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.1228 | 40.4314
CID=-405883728 | -15 | 35 | 35.7098 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33545.2398 | 0.627 | 0.020261 | 2.4231 | 35.7098 | 86.5285 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 55.9282 | 5.5624 | 0.84678 | 99.2484 | 64.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.7098 | 39.9119
CID=-1709845643 | -15 | 37.5 | 40.2301 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1435875847 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=131913932 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-251167619 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1555129534 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=514995483 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-788966432 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1172047983 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1818957398 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405884881 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1709846796 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1435870598 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=131908683 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-251172868 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1555134783 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=514990234 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-788971681 | -12 | 0 | 4.1993 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 18384.81 | 0.20856 | 0.0068425 | 9.2921 | 4.1993 | 39.02 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 9.8733 | 1.5931 | 0.63617 | 49.3087 | 10.029 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0431 | 4.1993 | 8.8682
CID=-1172053232 | -12 | 2.5 | 4.6238 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 19195.696 | 0.19506 | 0.0068352 | 7.756 | 4.6238 | 35.862 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 13.8825 | 1.7452 | 0.6413 | 30.941 | 10.9545 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.6238 | 11.4069
CID=1818952149 | -12 | 5 | 5.4802 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 20366.421 | 0.21052 | 0.0069106 | 6.9372 | 5.4802 | 38.0171 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 17.4978 | 1.9081 | 0.65138 | 52.1393 | 12.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.4802 | 14.2089
CID=-405890130 | -12 | 7.5 | 6.3445 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 21855.3975 | 0.2273 | 0.0071228 | 6.3525 | 6.3445 | 40.3034 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 20.473 | 2.0826 | 0.66118 | 33.781 | 14.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.3445 | 17.3877
CID=-1709852045 | -12 | 10 | 7.5663 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 22789.9153 | 0.25654 | 0.0074828 | 5.9003 | 7.5663 | 44.6431 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 23.2717 | 2.269 | 0.67443 | 63.2355 | 17.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.5663 | 20.1421
CID=1435861501 | -12 | 12.5 | 8.9351 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 24122.4936 | 0.27743 | 0.0079573 | 5.3005 | 8.9351 | 47.3607 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 26.9004 | 2.4678 | 0.68846 | 47.5994 | 19.7185 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.9351 | 24.0547
CID=131899586 | -12 | 15 | 10.4239 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 25015.7983 | 0.30209 | 0.0085261 | 4.8509 | 10.424 | 50.566 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 30.0852 | 2.6798 | 0.70282 | 77.5049 | 22.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.4239 | 28.2107
CID=-251181965 | -12 | 17.5 | 11.959 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 26043.1365 | 0.32278 | 0.0091602 | 4.4277 | 11.959 | 52.9514 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 33.3924 | 2.9053 | 0.7167 | 82.8254 | 25.3523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.959 | 32.2434
CID=-1555143880 | -12 | 20 | 13.8048 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 27348.2827 | 0.35142 | 0.0099398 | 4.0905 | 13.8048 | 56.4681 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 36.4311 | 3.1449 | 0.73221 | 54.6982 | 28.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.8048 | 36.0111
CID=514981137 | -12 | 22.5 | 15.8745 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 28317.9953 | 0.37886 | 0.010845 | 3.7542 | 15.8745 | 59.5964 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 39.7702 | 3.3993 | 0.7482 | 70.3102 | 32.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.8745 | 40.4827
CID=-788980778 | -12 | 25 | 18.0705 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 29290.6412 | 0.40748 | 0.011849 | 3.4705 | 18.0705 | 62.7141 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 42.9138 | 3.6689 | 0.76368 | 56.989 | 35.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.0705 | 44.884
CID=-1172062329 | -12 | 27.5 | 20.8318 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 30111.8936 | 0.44561 | 0.013114 | 3.2191 | 20.8318 | 67.0596 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 46.0335 | 3.9544 | 0.78118 | 59.0954 | 40.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.8318 | 45.1309
CID=1818943052 | -12 | 30 | 23.4146 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 30914.6718 | 0.48505 | 0.014382 | 3.0462 | 23.4146 | 71.3253 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 48.3273 | 4.2564 | 0.79577 | 64.6028 | 44.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.4146 | 44.9448
CID=-405899227 | -12 | 32.5 | 27.064 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 31427.4173 | 0.52296 | 0.016129 | 2.7745 | 27.064 | 75.09 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 52.3393 | 4.5754 | 0.81381 | 85.2528 | 50.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.064 | 44.9312
CID=-1709861142 | -12 | 35 | 30.8778 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 32229.4892 | 0.5752 | 0.018039 | 2.6099 | 30.8778 | 80.5883 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 54.986 | 4.9121 | 0.82987 | 93.2704 | 56.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.8778 | 45.1391
CID=1435864700 | -12 | 37.5 | 35.0704 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 33053.8921 | 0.62616 | 0.020208 | 2.4389 | 35.0704 | 85.5323 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 57.9496 | 5.2671 | 0.84474 | 87.0429 | 63.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.0704 | 45.4468
CID=131902785 | -12 | 40 | 41.392 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 33789.9486 | 0.6761 | 0.023395 | 2.1735 | 41.392 | 89.9669 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 63.3584 | 5.6411 | 0.86265 | 95.4343 | 72.9013 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.392 | 45.2292
CID=-251178766 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1555140681 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=514984336 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-788977579 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1172059130 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1818946251 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-405896028 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1709857943 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319758 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319727 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319696 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319665 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319634 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319603 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319572 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568319541 | -9 | 2.5 | 4.3612 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 18288.7935 | 0.24162 | 0.0068235 | 10.3018 | 4.3612 | 44.9281 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 11.5084 | 1.5462 | 0.63814 | 52.1738 | 10.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 10.295 | 4.3612 | 8.9771
CID=-568320006 | -9 | 5 | 4.5803 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 18533.518 | 0.2034 | 0.0068874 | 8.1123 | 4.5803 | 37.1571 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 15.7687 | 1.6906 | 0.64078 | 39.5045 | 10.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.5803 | 11.7505
CID=-568319975 | -9 | 7.5 | 5.6398 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 20204.1782 | 0.22482 | 0.0069646 | 7.1517 | 5.6398 | 40.3341 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 19.7753 | 1.8452 | 0.65322 | 23.1821 | 13.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.6398 | 14.6838
CID=513409421 | -9 | 10 | 6.707 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 21263.7005 | 0.25435 | 0.0072281 | 6.6789 | 6.707 | 44.7958 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 22.3465 | 2.0103 | 0.66518 | 48.2233 | 15.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.707 | 18.0132
CID=513409452 | -9 | 12.5 | 7.7039 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 22372.3734 | 0.27146 | 0.0075655 | 6.0891 | 7.7039 | 46.9097 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 25.2658 | 2.1865 | 0.67588 | 55.3675 | 17.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.7039 | 20.8962
CID=513409483 | -9 | 15 | 9.2107 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 23686.4797 | 0.29816 | 0.0080875 | 5.4864 | 9.2107 | 50.5332 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 28.7414 | 2.3743 | 0.69119 | 51.2497 | 20.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.2107 | 24.9456
CID=513409514 | -9 | 17.5 | 10.7125 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 24527.6335 | 0.32266 | 0.0086739 | 5.0042 | 10.7125 | 53.6077 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 31.9 | 2.5741 | 0.7055 | 65.6954 | 23.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7125 | 29.4124
CID=513409545 | -9 | 20 | 12.5811 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 25597.2882 | 0.35679 | 0.0094249 | 4.6163 | 12.5811 | 58.0785 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 34.85 | 2.7864 | 0.72206 | 91.0651 | 26.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.5811 | 34.2136
CID=513409576 | -9 | 22.5 | 14.2865 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 26681.8468 | 0.37698 | 0.010177 | 4.2061 | 14.2866 | 60.0902 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 38.1751 | 3.0118 | 0.73606 | 66.6223 | 29.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.2865 | 37.7584
CID=513409607 | -9 | 25 | 16.365 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 27746.536 | 0.40743 | 0.011103 | 3.8839 | 16.365 | 63.5597 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 41.1947 | 3.2507 | 0.75178 | 62.1583 | 33.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.365 | 42.7201
CID=513409638 | -9 | 27.5 | 18.8057 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 28962.8225 | 0.4412 | 0.012212 | 3.5797 | 18.8057 | 67.3193 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 44.3702 | 3.5036 | 0.76854 | 56.0906 | 37.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.8057 | 47.4545
CID=513409173 | -9 | 30 | 21.4049 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 29571.5695 | 0.47876 | 0.013442 | 3.3358 | 21.4049 | 71.4034 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 47.1897 | 3.7712 | 0.78456 | 59.3723 | 41.4518 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.4049 | 50.6676
CID=513409204 | -9 | 32.5 | 24.4891 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 30428.8418 | 0.52158 | 0.014922 | 3.1028 | 24.4891 | 75.984 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 50.1442 | 4.0538 | 0.80138 | 61.826 | 46.429 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.4891 | 51.064
CID=-406179288 | -9 | 35 | 27.363 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 31177.537 | 0.55908 | 0.016403 | 2.9054 | 27.363 | 79.5001 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 52.8305 | 4.3522 | 0.81517 | 68.2381 | 51.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.363 | 50.7666
CID=-406179257 | -9 | 37.5 | 31.5427 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 31640.9352 | 0.60314 | 0.018489 | 2.652 | 31.5427 | 83.6509 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 56.7121 | 4.6667 | 0.83241 | 97.4739 | 57.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.5427 | 50.2122
CID=-406179226 | -9 | 40 | 35.6622 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 32492.5803 | 0.65925 | 0.020667 | 2.4986 | 35.6622 | 89.1056 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 59.239 | 4.9981 | 0.84663 | 93.2626 | 63.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.6622 | 51.0088
CID=-406179195 | -9 | 42.5 | 40.6387 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 33245.1639 | 0.71375 | 0.023335 | 2.3114 | 40.6387 | 93.9328 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 62.6375 | 5.3467 | 0.86077 | 88.7438 | 71.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.6387 | 50.9152
CID=-406179164 | -9 | 45 | 47.1582 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 33837.7491 | 0.96844 | 0.026834 | 2.6291 | 47.1582 | 123.9833 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.9529 | 5.7134 | 0.87525 | 108.6144 | 81.862 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=-406179133 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406179102 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406179071 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406179536 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406179505 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675549891 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675549922 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675549953 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675549984 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675550015 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675550046 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675550077 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675550108 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675549643 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675549674 | -6 | 5 | 4.7732 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18419.3194 | 0.29704 | 0.0067778 | 11.4983 | 4.7732 | 54.8839 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 13.4304 | 1.5026 | 0.64309 | 58.8967 | 11.277 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=-536370338 | -6 | 7.5 | 4.779 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 18319.5431 | 0.23404 | 0.0068993 | 8.8884 | 4.779 | 42.4774 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 17.3585 | 1.64 | 0.64316 | 42.592 | 11.2895 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1863 | 4.779 | 12.0604
CID=-536370307 | -6 | 10 | 5.7257 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 19734.3238 | 0.24677 | 0.0070177 | 7.6802 | 5.7257 | 43.9746 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 21.21 | 1.7868 | 0.6542 | 28.0112 | 13.2976 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.7257 | 15.1552
CID=-536370276 | -6 | 12.5 | 6.8046 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 20667.1794 | 0.26601 | 0.0072955 | 6.8372 | 6.8046 | 46.524 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 24.6151 | 1.9434 | 0.66625 | 54.3497 | 15.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.8046 | 18.649
CID=-536370245 | -6 | 15 | 8.1409 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 22194.077 | 0.30253 | 0.0077208 | 6.376 | 8.1409 | 51.9061 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 27.1073 | 2.1103 | 0.68042 | 33.7812 | 18.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.1409 | 22.5502
CID=-536370214 | -6 | 17.5 | 9.4617 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 23058.2835 | 0.32366 | 0.0082154 | 5.7546 | 9.4617 | 54.4482 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 30.2758 | 2.2879 | 0.69365 | 59.3555 | 20.7246 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.4617 | 25.8429
CID=-536370183 | -6 | 20 | 11.2332 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 24216.8689 | 0.35614 | 0.0088953 | 5.2271 | 11.2332 | 58.7164 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 33.4764 | 2.4766 | 0.71025 | 47.5997 | 24.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.2332 | 30.5791
CID=-536370152 | -6 | 22.5 | 12.9502 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 25104.8106 | 0.38082 | 0.0096171 | 4.7488 | 12.9502 | 61.4981 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 36.7012 | 2.6769 | 0.72518 | 77.9042 | 27.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.9502 | 35.5459
CID=-536370121 | -6 | 25 | 14.7519 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 26071.2637 | 0.40403 | 0.010416 | 4.3298 | 14.7519 | 63.8733 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 39.9176 | 2.8892 | 0.7397 | 82.8254 | 30.3004 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.7519 | 40.5021
CID=-536370586 | -6 | 27.5 | 16.9384 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 27312.0469 | 0.43761 | 0.011397 | 3.9959 | 16.9384 | 67.6848 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 42.8767 | 3.1141 | 0.75588 | 55.5799 | 34.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.9384 | 44.721
CID=-536370555 | -6 | 30 | 19.4722 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 28114.5805 | 0.47549 | 0.01256 | 3.6929 | 19.4722 | 71.9082 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 45.8696 | 3.3519 | 0.77282 | 77.1551 | 38.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.4722 | 50.1265
CID=545358841 | -6 | 32.5 | 22.148 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 29281.6373 | 0.51325 | 0.013842 | 3.4243 | 22.148 | 75.8425 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 48.7912 | 3.6031 | 0.78882 | 57.3728 | 42.6593 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.148 | 55.2599
CID=545358872 | -6 | 35 | 25.0822 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 29912.8608 | 0.55084 | 0.015293 | 3.1687 | 25.0822 | 79.4786 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 51.8504 | 3.8682 | 0.80437 | 60.295 | 47.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.0822 | 56.636
CID=545358903 | -6 | 37.5 | 28.0639 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 30723.6554 | 0.58833 | 0.016844 | 2.9513 | 28.0639 | 82.8253 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 54.6995 | 4.1478 | 0.81828 | 62.9412 | 52.1076 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.0639 | 56.9451
CID=545358934 | -6 | 40 | 31.7052 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 31356.5267 | 0.62966 | 0.018749 | 2.7257 | 31.7053 | 86.4198 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 57.9657 | 4.4423 | 0.83303 | 73.0304 | 57.8268 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.7052 | 56.788
CID=545358965 | -6 | 42.5 | 36.4168 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 31865.6524 | 0.69099 | 0.021208 | 2.5368 | 36.4168 | 92.3811 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 60.9932 | 4.7522 | 0.84898 | 98.6211 | 65.1722 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.4168 | 56.5732
CID=545358996 | -6 | 45 | 40.914 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 32702.6499 | 0.75102 | 0.023721 | 2.3883 | 40.914 | 97.7165 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 63.5103 | 5.0781 | 0.86146 | 88.6684 | 72.159 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.914 | 56.8886
CID=545359027 | -6 | 47.5 | 46.8283 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 33208.5014 | 0.98782 | 0.027314 | 2.6299 | 47.5154 | 124.9625 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 59.4541 | 5.4204 | 0.87593 | 108.0349 | 82.4177 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.8283 | 57.2808
CID=545359058 | -6 | 50 | 53.3934 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34051.8858 | 0.88288 | 0.030801 | 2.0316 | 53.3934 | 108.4757 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 70.5464 | 5.7798 | 0.88577 | 95.3511 | 91.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=545358593 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545358624 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229868 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229837 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229806 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229775 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229744 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229713 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229682 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229651 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374230116 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374230085 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707499311 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707499342 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707499373 | -3 | 10 | 5.3391 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 18408.5647 | 0.29119 | 0.0069182 | 9.8323 | 5.3391 | 52.4962 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 19.2343 | 1.5929 | 0.64975 | 49.1469 | 12.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1041 | 5.3391 | 12.2784
CID=707499404 | -3 | 12.5 | 5.9798 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 19199.1786 | 0.27618 | 0.0070902 | 8.1737 | 5.9798 | 48.8768 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 23.0434 | 1.7325 | 0.65709 | 32.8298 | 13.8266 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.9798 | 15.6157
CID=707499435 | -3 | 15 | 7.1813 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 20396.6364 | 0.29764 | 0.007419 | 7.1972 | 7.1813 | 51.6854 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 26.5009 | 1.8813 | 0.67033 | 44.8285 | 16.2768 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.1813 | 19.2479
CID=707499466 | -3 | 17.5 | 8.3228 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 21637.2882 | 0.31903 | 0.007822 | 6.5282 | 8.3228 | 54.3329 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 29.3545 | 2.0396 | 0.68229 | 40.1449 | 18.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.3228 | 23.3226
CID=707499497 | -3 | 20 | 9.6291 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 22519.8736 | 0.3442 | 0.0083245 | 5.9677 | 9.6291 | 57.4641 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 32.122 | 2.2079 | 0.69527 | 61.261 | 21.042 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6291 | 26.7511
CID=707499528 | -3 | 22.5 | 11.6237 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 23894.3203 | 0.38249 | 0.0090843 | 5.3824 | 11.6237 | 62.563 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 35.4448 | 2.3864 | 0.71374 | 51.2495 | 24.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.6237 | 31.6404
CID=707499063 | -3 | 25 | 13.2655 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 24625.7296 | 0.40421 | 0.0097975 | 4.8805 | 13.2655 | 64.7423 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 38.6032 | 2.5757 | 0.7278 | 66.0002 | 27.6927 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.2655 | 36.9411
CID=707499094 | -3 | 27.5 | 15.5311 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 25638.1487 | 0.44682 | 0.010768 | 4.5096 | 15.5311 | 70.0394 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 41.3976 | 2.7762 | 0.74564 | 90.8866 | 31.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.5311 | 42.6405
CID=-504420918 | -3 | 30 | 17.4826 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 26643.0071 | 0.46769 | 0.011689 | 4.1013 | 17.4826 | 71.7019 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 44.6755 | 2.9882 | 0.75968 | 67.1257 | 34.965 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.4826 | 46.7387
CID=-504420887 | -3 | 32.5 | 20.0462 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 27717.1432 | 0.51007 | 0.012884 | 3.8129 | 20.0462 | 76.4344 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 47.3878 | 3.2122 | 0.77641 | 58.7304 | 39.228 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.0462 | 52.5507
CID=-504420856 | -3 | 35 | 22.9114 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 28801.2551 | 0.5505 | 0.01426 | 3.5168 | 22.9114 | 80.574 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 50.4262 | 3.4485 | 0.79306 | 70.3081 | 43.894 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9114 | 58.111
CID=-504420825 | -3 | 37.5 | 25.5999 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 29461.7927 | 0.57942 | 0.015646 | 3.2334 | 25.5999 | 82.7752 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 53.6227 | 3.6978 | 0.80691 | 56.9188 | 48.2022 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.5999 | 63.3351
CID=-504420794 | -3 | 40 | 29.1961 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 30240.1837 | 0.62827 | 0.017469 | 2.9982 | 29.1961 | 87.5361 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 56.6171 | 3.9603 | 0.82312 | 59.0954 | 53.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.1961 | 63.4544
CID=-504420763 | -3 | 42.5 | 32.3922 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 30966.3489 | 0.67577 | 0.019234 | 2.8325 | 32.3923 | 91.7519 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 58.8819 | 4.2366 | 0.83556 | 62.6995 | 58.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.3922 | 63.0494
CID=-504420732 | -3 | 45 | 36.8219 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 31473.0843 | 0.72125 | 0.02162 | 2.5893 | 36.822 | 95.3437 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 62.545 | 4.5271 | 0.8502 | 85.2522 | 65.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.8219 | 63.027
CID=-504420701 | -3 | 47.5 | 41.7507 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 32075.1537 | 0.78677 | 0.024366 | 2.4231 | 41.7507 | 101.1657 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 65.2888 | 4.8323 | 0.86353 | 97.8722 | 73.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.7507 | 63.4939
CID=-504421166 | -3 | 50 | 46.6377 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 32873.8902 | 0.85076 | 0.027262 | 2.2793 | 46.6378 | 106.2992 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 67.8048 | 5.1527 | 0.87423 | 86.6769 | 81.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.6377 | 63.7961
CID=-504421135 | -3 | 52.5 | 53.5574 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 33345.9168 | 1.1017 | 0.031388 | 2.484 | 53.7902 | 133.6122 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 64.2218 | 5.4887 | 0.88635 | 107.8926 | 92.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.5574 | 63.6127
CID=577308261 | -3 | 55 | 60.1316 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34145.4602 | 0.99407 | 0.035397 | 1.9438 | 60.1316 | 116.8842 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 74.5756 | 5.841 | 0.89438 | 97.0874 | 102.1493 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=577308292 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308323 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308354 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308385 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308416 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308447 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308478 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308013 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577308044 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568318737 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568318640 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568318543 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568318702 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568318613 | 0 | 12.5 | 5.6702 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 18485.4826 | 0.33257 | 0.0069806 | 10.5015 | 5.6702 | 59.5451 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 21.3389 | 1.5491 | 0.65357 | 47.2924 | 13.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.6702 | 13.1874
CID=-568318516 | 0 | 15 | 5.883 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 18568.3581 | 0.28471 | 0.0071307 | 8.5041 | 5.883 | 50.0297 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 25.0358 | 1.6821 | 0.65599 | 39.5045 | 13.6257 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.883 | 16.0314
CID=-568318419 | 0 | 17.5 | 7.2692 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 20190.9523 | 0.3078 | 0.0074914 | 7.2992 | 7.2692 | 53.059 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 28.9795 | 1.8236 | 0.67127 | 23.4226 | 16.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.2692 | 19.8154
CID=-568318578 | 0 | 20 | 8.7353 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 21066.5888 | 0.3513 | 0.0079854 | 6.7972 | 8.7353 | 59.3758 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 31.3481 | 1.9741 | 0.68647 | 54.3168 | 19.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.7353 | 24.0702
CID=-568318985 | 0 | 22.5 | 10.1199 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 22327.8968 | 0.37953 | 0.0085287 | 6.212 | 10.1199 | 62.8646 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 34.023 | 2.1337 | 0.69996 | 43.3478 | 21.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.1199 | 28.0987
CID=-568318888 | 0 | 25 | 11.7385 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 23272.6667 | 0.40311 | 0.009194 | 5.5715 | 11.7385 | 65.4016 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 37.2499 | 2.303 | 0.71476 | 55.9625 | 24.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.7385 | 32.6801
CID=513410442 | 0 | 27.5 | 13.9765 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 24276.4614 | 0.45002 | 0.010113 | 5.1137 | 13.9765 | 71.4725 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 40.0887 | 2.4822 | 0.73359 | 47.6059 | 28.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.9765 | 38.3214
CID=513410539 | 0 | 30 | 15.9309 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 25154.5739 | 0.47407 | 0.010999 | 4.6238 | 15.9309 | 73.662 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 43.3358 | 2.6717 | 0.74861 | 78.1639 | 32.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.9309 | 44.1758
CID=513410636 | 0 | 32.5 | 18.0018 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 26063.5396 | 0.49915 | 0.011979 | 4.2124 | 18.0018 | 75.8315 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 46.4874 | 2.872 | 0.76322 | 82.8254 | 35.8364 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.0018 | 50.2286
CID=513410477 | 0 | 35 | 20.6907 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 27219.0248 | 0.54458 | 0.013243 | 3.9069 | 20.6907 | 80.8369 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 49.2176 | 3.0833 | 0.78034 | 58.623 | 40.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.6907 | 54.8307
CID=513410566 | 0 | 37.5 | 23.6252 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 27918.5787 | 0.58956 | 0.014672 | 3.6167 | 23.6252 | 85.4458 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 52.0589 | 3.3062 | 0.79689 | 62.5691 | 45.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.6252 | 61.2623
CID=513410663 | 0 | 40 | 26.4682 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 29189.0143 | 0.62014 | 0.016146 | 3.313 | 26.4682 | 87.6881 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 55.309 | 3.5409 | 0.81106 | 54.2825 | 49.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.4682 | 67.1838
CID=513410760 | 0 | 42.5 | 29.9202 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 29704.7489 | 0.67308 | 0.017949 | 3.1009 | 29.9202 | 92.78 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 57.8748 | 3.7879 | 0.82609 | 59.3724 | 55.0294 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.9202 | 70.4572
CID=513410601 | 0 | 45 | 33.7902 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 30489.1136 | 0.72418 | 0.020029 | 2.8775 | 33.7902 | 97.2304 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 60.7993 | 4.0477 | 0.84048 | 61.826 | 61.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.7902 | 71.0175
CID=513410194 | 0 | 47.5 | 37.3283 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 31178.7424 | 0.77375 | 0.022091 | 2.7082 | 37.3283 | 101.0941 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 63.1879 | 4.3205 | 0.85171 | 64.6031 | 66.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 37.3283 | 70.5862
CID=513410291 | 0 | 50 | 42.4342 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 31570.3412 | 0.82097 | 0.024967 | 2.4574 | 42.4343 | 104.2779 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 67.1131 | 4.607 | 0.86517 | 85.2542 | 74.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.4342 | 70.2774
CID=-406178267 | 0 | 52.5 | 47.5636 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 32271.7587 | 0.89072 | 0.028034 | 2.31 | 47.5636 | 109.872 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 69.6224 | 4.9075 | 0.87602 | 97.8716 | 82.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.5636 | 70.9719
CID=-406178170 | 0 | 55 | 52.837 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 33008.9618 | 0.95869 | 0.031368 | 2.171 | 52.837 | 114.7112 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 72.1322 | 5.2224 | 0.88494 | 86.6769 | 90.7148 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52.837 | 71.2608
CID=-406178073 | 0 | 57.5 | 60.8149 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 33491.1567 | 1.191 | 0.036234 | 2.2703 | 60.8149 | 138.0697 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 70.2336 | 5.5522 | 0.89512 | 105.8926 | 103.2244 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.8149 | 71.0549
CID=-406178232 | 0 | 60 | 67.3745 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34214.8195 | 1.1117 | 0.040731 | 1.8506 | 67.3745 | 124.6827 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 78.7717 | 5.8975 | 0.90124 | 97.0874 | 113.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=-406178143 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406178046 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406177949 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406178108 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406178515 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406178418 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675550912 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675551009 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675551106 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675550947 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675551036 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675551133 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675551230 | 3 | 15 | 6.0686 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 18384.9627 | 0.40183 | 0.007068 | 11.772 | 6.0686 | 71.4398 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 22.8745 | 1.5081 | 0.65809 | 59.0782 | 14.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=675551071 | 3 | 17.5 | 6.1159 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 18331.1857 | 0.32299 | 0.0072092 | 9.2124 | 6.1159 | 56.3424 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 26.6839 | 1.635 | 0.65862 | 42.5768 | 14.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2074 | 6.1159 | 16.4081
CID=675550664 | 3 | 20 | 7.4444 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 19693.1882 | 0.34241 | 0.0075851 | 7.869 | 7.4444 | 58.5804 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 30.3776 | 1.7699 | 0.67314 | 27.023 | 16.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.4444 | 20.3842
CID=675550761 | 3 | 22.5 | 8.8813 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 20564.9261 | 0.36883 | 0.0080861 | 6.9645 | 8.8813 | 61.8543 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 33.5994 | 1.9131 | 0.68793 | 54.495 | 19.6151 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.8813 | 24.8225
CID=-536369317 | 3 | 25 | 10.3039 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 21946.8319 | 0.39771 | 0.0086513 | 6.3417 | 10.304 | 65.3443 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 36.2994 | 2.0648 | 0.7017 | 33.781 | 22.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.3039 | 29.7346
CID=-536369220 | 3 | 27.5 | 12.151 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 22707.0676 | 0.44139 | 0.0094004 | 5.8442 | 12.151 | 71.0122 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 38.8537 | 2.2255 | 0.71837 | 61.2612 | 25.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.151 | 33.7526
CID=-536369123 | 3 | 30 | 14.3139 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 24009.6867 | 0.4743 | 0.010313 | 5.217 | 14.3139 | 74.6758 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 42.2649 | 2.3954 | 0.73627 | 49.6423 | 29.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.3139 | 39.5659
CID=-536369282 | 3 | 32.5 | 16.265 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 24683.4774 | 0.50032 | 0.011214 | 4.7366 | 16.265 | 77.041 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 45.323 | 2.575 | 0.75106 | 66.2486 | 32.903 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.265 | 45.7721
CID=-536369193 | 3 | 35 | 18.9753 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 25642.0824 | 0.55294 | 0.012442 | 4.3856 | 18.9753 | 83.2171 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 47.9875 | 2.7645 | 0.76964 | 90.637 | 37.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.9753 | 52.4501
CID=-536369096 | 3 | 37.5 | 21.2782 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 26570.0719 | 0.57871 | 0.013591 | 3.9978 | 21.2782 | 85.0667 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 51.1215 | 2.9643 | 0.78382 | 69.2762 | 41.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.2782 | 57.13
CID=-536368999 | 3 | 40 | 24.2945 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 27655.6085 | 0.63107 | 0.015079 | 3.7266 | 24.2945 | 90.535 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 53.6809 | 3.1747 | 0.80038 | 55.4416 | 46.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.2945 | 63.85
CID=-536369158 | 3 | 42.5 | 27.2941 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 28513.2347 | 0.66332 | 0.016645 | 3.4001 | 27.2941 | 92.803 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 56.982 | 3.3962 | 0.81486 | 70.3101 | 50.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.2941 | 70.4485
CID=-536369565 | 3 | 45 | 30.628 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 29372.0316 | 0.70848 | 0.018437 | 3.1535 | 30.628 | 96.584 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 59.8106 | 3.6291 | 0.8289 | 57.1748 | 56.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.628 | 77.0074
CID=-536369468 | 3 | 47.5 | 34.4646 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 29986.1631 | 0.76022 | 0.020545 | 2.9275 | 34.4646 | 100.8938 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 62.6622 | 3.8738 | 0.84276 | 60.0823 | 62.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.4646 | 78.0241
CID=545359862 | 3 | 50 | 38.3198 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 30714.2625 | 0.81182 | 0.022789 | 2.7346 | 38.3198 | 104.7897 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 65.3102 | 4.1306 | 0.85456 | 63.436 | 68.13 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.3198 | 78.3946
CID=545359959 | 3 | 52.5 | 42.5765 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 31326.8028 | 0.86311 | 0.02535 | 2.5424 | 42.5765 | 108.2449 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 68.17 | 4.4 | 0.8655 | 70.7725 | 74.7407 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.5765 | 78.2557
CID=545360056 | 3 | 55 | 48.3691 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 31713.2052 | 0.92914 | 0.028781 | 2.3381 | 48.3692 | 113.09 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 71.5247 | 4.6823 | 0.87752 | 97.4739 | 83.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.3691 | 77.4469
CID=545359897 | 3 | 57.5 | 53.8459 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 32435.6001 | 1.0031 | 0.032291 | 2.1979 | 53.8459 | 118.3472 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 73.9908 | 4.9781 | 0.88643 | 93.2703 | 92.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.8459 | 78.4246
CID=545359986 | 3 | 60 | 59.7005 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 33115.5477 | 1.0749 | 0.036228 | 2.0565 | 59.7005 | 122.7764 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 76.6431 | 5.2877 | 0.8939 | 87.0428 | 101.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 59.7005 | 78.6223
CID=545360083 | 3 | 62.5 | 68.5754 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 33625.8435 | 1.2619 | 0.041983 | 2.0319 | 68.5754 | 139.3374 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 77.0407 | 5.6115 | 0.90218 | 102.0569 | 115.4862 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.5754 | 77.8125
CID=545360180 | 3 | 65 | 75.117 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34259.8974 | 1.2377 | 0.04694 | 1.7561 | 75.117 | 131.9152 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 83.036 | 5.95 | 0.90655 | 97.0875 | 125.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=545360021 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545359614 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545359711 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228847 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228750 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228653 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228812 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228723 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228626 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228529 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228688 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374229095 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374228998 | 6 | 20 | 6.8403 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 18381.545 | 0.39526 | 0.0073763 | 10.0042 | 6.8403 | 68.4315 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 28.6135 | 1.5911 | 0.66664 | 49.0253 | 15.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1591 | 6.8403 | 16.6703
CID=707500332 | 6 | 22.5 | 7.7456 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 19160.1475 | 0.37981 | 0.0077111 | 8.3239 | 7.7456 | 64.4739 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 32.2549 | 1.7198 | 0.67631 | 34.3339 | 17.4006 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.7456 | 20.9315
CID=707500429 | 6 | 25 | 9.3478 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 20374.258 | 0.40905 | 0.0082768 | 7.2795 | 9.3478 | 68.0478 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 35.5769 | 1.8563 | 0.69254 | 38.6252 | 20.508 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.3478 | 25.5163
CID=707500526 | 6 | 27.5 | 10.8391 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 21395.2776 | 0.43826 | 0.0088823 | 6.588 | 10.8391 | 71.4076 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 38.3035 | 2.0007 | 0.70667 | 46.359 | 23.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.8391 | 30.6162
CID=707500367 | 6 | 30 | 12.4236 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 22397.9505 | 0.46738 | 0.0095688 | 6.0003 | 12.4236 | 74.5451 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 40.9782 | 2.1535 | 0.72072 | 51.4417 | 26.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.4236 | 34.7884
CID=707500456 | 6 | 32.5 | 14.4257 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 23436.6059 | 0.49632 | 0.010444 | 5.3683 | 14.4257 | 77.4421 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 44.2161 | 2.3149 | 0.73716 | 52.944 | 29.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.4257 | 40.7528
CID=707500553 | 6 | 35 | 17.097 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 24316.996 | 0.55477 | 0.011611 | 4.95 | 17.097 | 84.6299 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 46.8714 | 2.4852 | 0.757 | 62.5752 | 34.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.097 | 47.374
CID=707500650 | 6 | 37.5 | 19.3967 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 25166.2916 | 0.58347 | 0.012717 | 4.4834 | 19.3967 | 86.9627 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 50.0117 | 2.6649 | 0.77234 | 78.3376 | 38.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.3967 | 54.193
CID=707500491 | 6 | 40 | 21.7901 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 26025.9846 | 0.61208 | 0.013922 | 4.0874 | 21.7901 | 89.065 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 53.0791 | 2.8541 | 0.78678 | 83.7371 | 42.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.7901 | 61.371
CID=707500084 | 6 | 42.5 | 25.0078 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 27095.2485 | 0.6701 | 0.015515 | 3.8038 | 25.0078 | 95.1259 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 55.6517 | 3.0532 | 0.804 | 61.546 | 47.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.0078 | 66.415
CID=707500181 | 6 | 45 | 28.0513 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 27865.474 | 0.70924 | 0.017131 | 3.4987 | 28.0513 | 98.1425 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 58.618 | 3.2625 | 0.81823 | 62.5656 | 52.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.0513 | 73.8077
CID=-504419897 | 6 | 47.5 | 31.5834 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 29002.4683 | 0.756 | 0.019044 | 3.2259 | 31.5834 | 101.8843 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 61.5859 | 3.4825 | 0.83257 | 56.6601 | 57.6362 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.5834 | 80.6463
CID=-504419800 | 6 | 50 | 35.1297 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 29523.2587 | 0.80055 | 0.021076 | 2.9883 | 35.1297 | 104.9764 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 64.443 | 3.7134 | 0.84493 | 56.9188 | 63.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.1297 | 86.4588
CID=-504419703 | 6 | 52.5 | 39.549 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 30241.1278 | 0.85772 | 0.023616 | 2.7644 | 39.5491 | 109.3279 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 67.4141 | 3.9556 | 0.85793 | 59.0954 | 70.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.549 | 86.5615
CID=-504419862 | 6 | 55 | 43.4253 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 30902.4611 | 0.9131 | 0.02607 | 2.6024 | 43.4253 | 113.0111 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 69.7482 | 4.2094 | 0.86746 | 62.6993 | 76.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.4253 | 85.8853
CID=-504419773 | 6 | 57.5 | 48.4863 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 31418.9028 | 0.96592 | 0.029239 | 2.3913 | 48.4864 | 115.9446 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 73.0353 | 4.4753 | 0.87773 | 73.0305 | 83.9293 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.4863 | 86.5751
CID=-504419676 | 6 | 60 | 54.7344 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 31845.4985 | 1.0459 | 0.033195 | 2.2218 | 54.7344 | 121.6087 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 75.9374 | 4.7536 | 0.88769 | 98.6211 | 93.6816 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.7344 | 86.0097
CID=-504419579 | 6 | 62.5 | 60.5946 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 32567.5523 | 1.124 | 0.037237 | 2.0862 | 60.5947 | 126.4134 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 78.4041 | 5.0447 | 0.89489 | 93.2685 | 102.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.5946 | 87.0244
CID=-504419738 | 6 | 65 | 67.1624 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 33194.5677 | 1.1996 | 0.041945 | 1.9402 | 67.1624 | 130.3083 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 81.2524 | 5.349 | 0.90107 | 87.0429 | 113.2467 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.1624 | 87.1744
CID=-504420145 | 6 | 67.5 | 76.7476 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 33708.1622 | 1.3621 | 0.048634 | 1.8591 | 76.7476 | 142.6829 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 82.8722 | 5.667 | 0.90746 | 99.979 | 128.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.7476 | 86.2309
CID=-504420048 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309282 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309379 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309476 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309317 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309406 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309503 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309600 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309441 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309034 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577309131 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568321936 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568321905 | 9 | 22.5 | 7.3644 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 18477.6118 | 0.4534 | 0.0075368 | 10.5765 | 7.3644 | 77.8896 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 30.8087 | 1.5501 | 0.67229 | 47.882 | 16.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.3644 | 17.597
CID=-568321742 | 9 | 25 | 7.5779 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 18557.5134 | 0.38823 | 0.0077355 | 8.6271 | 7.5779 | 65.3753 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 34.3393 | 1.6731 | 0.67455 | 39.5045 | 17.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.5779 | 21.4167
CID=-568321711 | 9 | 27.5 | 9.3386 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 20077.7768 | 0.41966 | 0.0083435 | 7.4137 | 9.3386 | 69.2338 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 37.9373 | 1.8033 | 0.69245 | 24.988 | 20.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.3386 | 26.1844
CID=-568321812 | 9 | 30 | 11.0478 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 20831.5168 | 0.46091 | 0.0090225 | 6.7391 | 11.0478 | 74.4525 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 40.577 | 1.941 | 0.70857 | 54.3169 | 23.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.0478 | 31.5026
CID=-568321781 | 9 | 32.5 | 12.9917 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 22181.171 | 0.51024 | 0.0098384 | 6.2082 | 12.9917 | 80.6554 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 43.0071 | 2.0864 | 0.72553 | 33.7811 | 27.2063 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.9917 | 37.3388
CID=-568321618 | 9 | 35 | 15.0271 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 22864.9591 | 0.54896 | 0.010746 | 5.6473 | 15.0271 | 84.863 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 45.7556 | 2.24 | 0.74182 | 63.3535 | 30.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.0271 | 41.988
CID=-568321587 | 9 | 37.5 | 17.4302 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 24078.734 | 0.58078 | 0.011842 | 5.0342 | 17.4302 | 87.7465 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 49.1169 | 2.4019 | 0.75932 | 48.6763 | 34.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.4302 | 48.8161
CID=-568322184 | 9 | 40 | 19.739 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 24702.0825 | 0.61258 | 0.012971 | 4.5791 | 19.739 | 90.3874 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 52.0836 | 2.5724 | 0.7745 | 66.4607 | 38.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.739 | 55.9939
CID=-568322153 | 9 | 42.5 | 22.9419 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 25609.8866 | 0.67689 | 0.014507 | 4.2486 | 22.9419 | 97.4701 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 54.644 | 2.7519 | 0.79322 | 90.3615 | 43.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9419 | 63.7251
CID=513407243 | 9 | 45 | 25.6277 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 26464.8565 | 0.70839 | 0.015929 | 3.8813 | 25.6277 | 99.4691 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 57.6596 | 2.9406 | 0.80705 | 71.3427 | 48.2464 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.6277 | 69.0029
CID=513407274 | 9 | 47.5 | 28.871 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 27523.9272 | 0.75817 | 0.01766 | 3.5926 | 28.8711 | 103.7224 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 60.3796 | 3.1388 | 0.82175 | 54.6982 | 53.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.871 | 76.6845
CID=513407437 | 9 | 50 | 32.4252 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 28207.7606 | 0.80347 | 0.019623 | 3.2998 | 32.4252 | 106.9977 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 63.4034 | 3.3469 | 0.83568 | 75.216 | 58.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.4252 | 84.4459
CID=513407468 | 9 | 52.5 | 36.2376 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 29246.1052 | 0.85533 | 0.021818 | 3.0567 | 36.2376 | 110.7677 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 66.2115 | 3.5652 | 0.84843 | 54.2826 | 64.8935 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.2376 | 90.1325
CID=513407367 | 9 | 55 | 40.4435 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 29712.645 | 0.91684 | 0.024324 | 2.852 | 40.4435 | 115.3436 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 68.8158 | 3.794 | 0.86027 | 59.3724 | 71.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.4435 | 90.1325
CID=513407398 | 9 | 57.5 | 45.1717 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 30430.608 | 0.9759 | 0.027231 | 2.6373 | 45.1717 | 119.1331 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 71.7642 | 4.0336 | 0.87126 | 61.8259 | 78.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.1717 | 90.1326
CID=513407561 | 9 | 60 | 49.2777 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 31053.1804 | 1.033 | 0.03004 | 2.4802 | 49.2777 | 122.2168 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 74.1134 | 4.2845 | 0.87915 | 64.6028 | 85.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.2777 | 90.1326
CID=513407592 | 9 | 62.5 | 55.0994 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 31471.6371 | 1.0871 | 0.033884 | 2.2592 | 55.0994 | 124.4798 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 77.6789 | 4.5468 | 0.88819 | 85.2522 | 94.253 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.0994 | 90.1325
CID=513406995 | 9 | 65 | 61.5516 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 31957.1429 | 1.1714 | 0.038328 | 2.1062 | 61.5517 | 129.6423 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 80.3921 | 4.8211 | 0.8959 | 98.6211 | 104.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.5516 | 90.1325
CID=513407026 | 9 | 67.5 | 67.8089 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 32658.3848 | 1.2536 | 0.043007 | 1.9742 | 67.8089 | 133.8671 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 82.8761 | 5.1077 | 0.90159 | 88.6685 | 114.271 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.8089 | 90.1325
CID=-406181466 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181435 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181272 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181241 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181342 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181311 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181148 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181117 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181714 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406181683 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675547713 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675547744 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675547907 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675547938 | 12 | 25 | 7.9035 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 18438.9763 | 0.53063 | 0.0077172 | 11.4415 | 7.9035 | 90.4283 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 32.7223 | 1.5117 | 0.67796 | 53.0966 | 17.7122 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0818 | 7.9035 | 14.4449
CID=675547837 | 12 | 27.5 | 7.806 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 18284.3624 | 0.43382 | 0.0078523 | 9.281 | 7.806 | 72.4476 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 36.046 | 1.6293 | 0.67695 | 42.5649 | 17.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2314 | 7.806 | 21.8594
CID=675547868 | 12 | 30 | 9.6007 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 19608.8265 | 0.46312 | 0.0084889 | 7.8897 | 9.6007 | 75.747 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 39.6085 | 1.7537 | 0.695 | 26.2624 | 20.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6007 | 26.8405
CID=675548031 | 12 | 32.5 | 11.4509 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 20431.4528 | 0.49865 | 0.0092275 | 6.9718 | 11.4509 | 79.8337 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 42.6839 | 1.8852 | 0.7122 | 53.8615 | 24.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.4509 | 32.3474
CID=675548062 | 12 | 35 | 13.2216 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 21659.5756 | 0.53415 | 0.010005 | 6.3272 | 13.2216 | 83.6563 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 45.3279 | 2.0239 | 0.72744 | 39.208 | 27.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.2216 | 38.3861
CID=675547465 | 12 | 37.5 | 15.1077 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 22429.8735 | 0.56956 | 0.010877 | 5.7721 | 15.1078 | 87.2041 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 47.9471 | 2.1702 | 0.74244 | 58.9118 | 30.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.1077 | 43.1811
CID=675547496 | 12 | 40 | 17.6528 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 23555.819 | 0.61016 | 0.012041 | 5.1701 | 17.6528 | 91.2663 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 51.1327 | 2.3243 | 0.76085 | 51.2498 | 35.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.6528 | 50.1588
CID=-536372516 | 12 | 42.5 | 20.6832 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 24321.719 | 0.67581 | 0.013459 | 4.7712 | 20.6832 | 98.683 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 53.7166 | 2.4864 | 0.78029 | 63.1845 | 40.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.6832 | 57.8258
CID=-536372485 | 12 | 45 | 23.3728 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 25140.7489 | 0.71071 | 0.014831 | 4.3313 | 23.3728 | 101.2346 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 56.7549 | 2.6569 | 0.79555 | 78.4721 | 44.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.3728 | 65.6764
CID=-536372322 | 12 | 47.5 | 26.1625 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 25958.2587 | 0.7455 | 0.016323 | 3.956 | 26.1625 | 103.4992 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 59.7255 | 2.836 | 0.80962 | 85.3977 | 49.097 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.1625 | 73.9419
CID=-536372291 | 12 | 50 | 29.7952 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 26941.9598 | 0.81043 | 0.018249 | 3.6773 | 29.7952 | 109.5661 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 62.2903 | 3.0241 | 0.82558 | 66.622 | 54.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.7952 | 79.5389
CID=-536372392 | 12 | 52.5 | 33.0954 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 27766.3824 | 0.8505 | 0.020152 | 3.3801 | 33.0954 | 111.8653 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 65.2183 | 3.2213 | 0.83807 | 61.5464 | 59.9988 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.0954 | 87.9361
CID=-536372361 | 12 | 55 | 37.3247 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 28728.6575 | 0.91368 | 0.022577 | 3.1292 | 37.3247 | 116.7959 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 68.0024 | 3.428 | 0.8517 | 70.3095 | 66.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 37.3247 | 90.1325
CID=-536372198 | 12 | 57.5 | 41.1087 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 29354.7935 | 0.95453 | 0.024957 | 2.8816 | 41.1087 | 118.457 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 70.9858 | 3.6445 | 0.86195 | 57.0591 | 72.4613 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.1087 | 90.1325
CID=-536372167 | 12 | 60 | 45.939 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 29927.5122 | 1.0241 | 0.027982 | 2.6825 | 45.939 | 123.2301 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 73.662 | 3.8712 | 0.87284 | 60.2012 | 79.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.939 | 90.1325
CID=-536372764 | 12 | 62.5 | 50.8496 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 30585.7181 | 1.0933 | 0.031253 | 2.5056 | 50.8496 | 127.4111 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 76.2317 | 4.1083 | 0.88182 | 64.1525 | 87.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50.8496 | 90.1325
CID=-536372733 | 12 | 65 | 55.6734 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 31177.5767 | 1.1622 | 0.034715 | 2.3525 | 55.6734 | 130.9713 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 78.6196 | 4.3561 | 0.88897 | 64.6088 | 95.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.6734 | 90.1325
CID=545356663 | 12 | 67.5 | 62.1983 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 31505.398 | 1.2172 | 0.039315 | 2.1294 | 62.1984 | 132.4468 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 82.3488 | 4.615 | 0.89656 | 85.2525 | 105.4035 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 62.1983 | 90.1326
CID=545356694 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356857 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356888 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356787 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356818 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356981 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545357012 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356415 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545356446 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374232046 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374232015 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374231852 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374231821 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374231922 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374231891 | 15 | 27.5 | 8.5925 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18438.7117 | 0.6276 | 0.0079495 | 12.3447 | 8.5925 | 106.0713 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 34.7451 | 1.4757 | 0.68503 | 59.7235 | 19.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=-374231728 | 15 | 30 | 8.6958 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 18295.1538 | 0.52337 | 0.0081414 | 9.9652 | 8.6958 | 86.6555 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 38.0313 | 1.5883 | 0.68607 | 48.9268 | 19.2574 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2146 | 8.6958 | 22.1642
CID=-374231697 | 15 | 32.5 | 9.9438 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 19080.8101 | 0.50979 | 0.0086633 | 8.311 | 9.9438 | 82.6425 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 41.541 | 1.7074 | 0.69829 | 35.2544 | 21.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.9438 | 27.4707
CID=-374232294 | 15 | 35 | 11.8586 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 20271.1702 | 0.53653 | 0.0094414 | 7.1768 | 11.8586 | 85.1071 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 44.9077 | 1.833 | 0.71581 | 23.1824 | 25.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.8586 | 33.1342
CID=-374232263 | 15 | 37.5 | 13.9017 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 21130.1154 | 0.58789 | 0.010329 | 6.5599 | 13.9017 | 91.1933 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 47.3782 | 1.9655 | 0.73299 | 51.5162 | 28.8155 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.9017 | 39.38
CID=707497133 | 15 | 40 | 15.8898 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 22255.4641 | 0.62684 | 0.01126 | 5.9801 | 15.8898 | 95.0222 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 49.9468 | 2.1051 | 0.74831 | 41.3607 | 32.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.8898 | 45.3962
CID=707497164 | 15 | 42.5 | 18.2373 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 22992.6638 | 0.6656 | 0.01238 | 5.4028 | 18.2373 | 98.5314 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 52.8184 | 2.2519 | 0.7648 | 60.1017 | 36.2301 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.2373 | 51.5431
CID=707497327 | 15 | 45 | 21.0094 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 24106.3414 | 0.70414 | 0.013729 | 4.8413 | 21.0094 | 101.7136 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 56.0177 | 2.4063 | 0.78224 | 47.7889 | 40.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.0094 | 59.4744
CID=707497358 | 15 | 47.5 | 23.7775 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 24684.202 | 0.74611 | 0.015157 | 4.4195 | 23.7775 | 105.0839 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 58.8682 | 2.5686 | 0.7977 | 66.5078 | 45.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.7775 | 67.6857
CID=707497257 | 15 | 50 | 27.453 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 25541.9883 | 0.82047 | 0.017036 | 4.1006 | 27.453 | 112.5738 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 61.3957 | 2.7389 | 0.81558 | 90.1004 | 51.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.453 | 76.5318
CID=707497288 | 15 | 52.5 | 30.551 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 26328.2048 | 0.8586 | 0.018789 | 3.753 | 30.551 | 114.6571 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 64.3185 | 2.9175 | 0.8286 | 73.266 | 56.0192 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.551 | 82.4122
CID=707497451 | 15 | 55 | 33.9713 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 27361.354 | 0.90285 | 0.020789 | 3.4508 | 33.9714 | 117.2275 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 67.1867 | 3.1047 | 0.8411 | 54.6982 | 61.365 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.9713 | 90.1325
CID=707497482 | 15 | 57.5 | 38.3346 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 27884.6803 | 0.9737 | 0.023332 | 3.2032 | 38.3346 | 122.7947 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 69.8431 | 3.3008 | 0.8546 | 82.9597 | 68.153 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.3346 | 90.1325
CID=707496885 | 15 | 60 | 42.1963 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 29045.494 | 1.0111 | 0.025812 | 2.9316 | 42.1963 | 123.7045 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 72.9624 | 3.5061 | 0.8646 | 54.7832 | 74.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.1963 | 90.1325
CID=707496916 | 15 | 62.5 | 46.6943 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 29466.683 | 1.0747 | 0.028761 | 2.7284 | 46.6943 | 127.3986 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 75.5997 | 3.7208 | 0.87435 | 56.9188 | 81.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.6943 | 90.1325
CID=-504423096 | 15 | 65 | 51.93 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 30119.6715 | 1.1395 | 0.032278 | 2.5169 | 51.93 | 130.7044 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 78.5549 | 3.9453 | 0.88355 | 59.0954 | 89.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51.93 | 90.1325
CID=-504423065 | 15 | 67.5 | 56.5173 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 30724.7061 | 1.2019 | 0.035727 | 2.3568 | 56.5173 | 133.2015 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 81.0057 | 4.1798 | 0.89007 | 62.6993 | 96.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.5173 | 90.1325
CID=-504422902 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504422871 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504422972 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504422941 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504422778 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504422747 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504423344 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504423313 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306083 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306114 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306277 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306308 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306207 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306238 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306401 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577306432 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577305835 | 18 | 32.5 | 9.4876 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 18410.3274 | 0.60404 | 0.0084291 | 10.448 | 9.4876 | 99.1255 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 40.3119 | 1.5499 | 0.6939 | 48.4714 | 20.7737 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.4876 | 22.9766
CID=577305866 | 18 | 35 | 9.6985 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 18503.5895 | 0.51873 | 0.0086724 | 8.5909 | 9.6986 | 83.3192 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 43.7008 | 1.664 | 0.69594 | 39.5045 | 21.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6985 | 28.0193
CID=-568312211 | 18 | 37.5 | 11.8592 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 19926.8531 | 0.55919 | 0.0095324 | 7.4083 | 11.8592 | 87.8564 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 47.0436 | 1.7842 | 0.71582 | 26.1571 | 25.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.8592 | 33.8929
CID=-568312114 | 18 | 40 | 13.906 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 20598.5909 | 0.60203 | 0.010434 | 6.6491 | 13.906 | 92.4626 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 49.8099 | 1.9109 | 0.73302 | 54.3636 | 28.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.906 | 40.396
CID=-568312149 | 18 | 42.5 | 16.0656 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 21865.6924 | 0.65041 | 0.011439 | 6.0738 | 16.0656 | 97.5796 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 52.3263 | 2.0442 | 0.7496 | 33.781 | 32.5628 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.0656 | 47.4637
CID=-568312308 | 18 | 45 | 18.496 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 22493.6979 | 0.70295 | 0.012609 | 5.5658 | 18.496 | 102.9444 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 54.8569 | 2.1844 | 0.76651 | 61.261 | 36.6619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.496 | 52.9123
CID=-568312335 | 18 | 47.5 | 21.5596 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 23633.7919 | 0.75236 | 0.014094 | 4.9846 | 21.5596 | 107.4658 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 58.0061 | 2.3317 | 0.78546 | 51.2497 | 41.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.5596 | 60.9897
CID=-568312238 | 18 | 50 | 24.7665 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 24288.2445 | 0.81548 | 0.015727 | 4.5834 | 24.7665 | 113.5158 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 60.6367 | 2.4862 | 0.80279 | 63.7562 | 46.8726 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.7665 | 69.7483
CID=-568312273 | 18 | 52.5 | 27.8781 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 25078.3679 | 0.85753 | 0.01742 | 4.1691 | 27.8781 | 116.2255 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 63.5956 | 2.6484 | 0.81747 | 78.6093 | 51.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.8781 | 78.6886
CID=-568312432 | 18 | 55 | 31.0948 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 25855.5742 | 0.89944 | 0.019261 | 3.8135 | 31.0948 | 118.5794 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 66.4922 | 2.8184 | 0.83071 | 86.9038 | 56.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.0948 | 88.1043
CID=-568312459 | 18 | 57.5 | 35.0067 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 26759.6033 | 0.9645 | 0.02152 | 3.5296 | 35.0067 | 123.5588 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 69.1446 | 2.9964 | 0.84454 | 66.6222 | 62.978 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.0067 | 90.1325
CID=-568312362 | 18 | 60 | 39.0194 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 27605.784 | 1.026 | 0.023971 | 3.2694 | 39.0194 | 127.5708 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 71.8118 | 3.1827 | 0.8565 | 58.1959 | 69.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.0194 | 90.1325
CID=513416968 | 18 | 62.5 | 43.2784 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 28353.0202 | 1.0746 | 0.0267 | 2.9929 | 43.2784 | 129.5263 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 74.8702 | 3.3776 | 0.86712 | 70.3102 | 75.831 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.2784 | 90.1325
CID=513417065 | 18 | 65 | 48.0659 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 29183.0854 | 1.1468 | 0.029873 | 2.7844 | 48.0659 | 133.8338 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 77.4817 | 3.5814 | 0.87696 | 54.2831 | 83.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.0659 | 90.1326
CID=513417030 | 18 | 67.5 | 53.0188 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 29598.8271 | 1.2161 | 0.033358 | 2.5877 | 53.0189 | 137.1996 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 80.1385 | 3.7943 | 0.88522 | 59.3724 | 90.999 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.0188 | 90.1325
CID=513416871 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513416844 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513416941 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513416906 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513416747 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513416720 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513416817 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171741 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171644 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171679 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171838 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171865 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171768 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171803 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171962 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171989 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406171892 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675557438 | 21 | 35 | 9.9152 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 18283.7083 | 0.68557 | 0.008629 | 11.2426 | 9.9152 | 111.4732 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 42.2265 | 1.5138 | 0.69802 | 52.4002 | 21.582 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2186 | 9.9152 | 20.974
CID=675557535 | 21 | 37.5 | 9.8342 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 18170.506 | 0.56856 | 0.0087954 | 9.1978 | 9.8343 | 90.4539 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 45.4661 | 1.6232 | 0.69724 | 42.5581 | 21.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2629 | 9.8342 | 28.5245
CID=675557500 | 21 | 40 | 12.2151 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 19480.3936 | 0.6128 | 0.0097428 | 7.8042 | 12.2151 | 95.3285 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 48.9262 | 1.7385 | 0.71892 | 25.7842 | 25.815 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.2151 | 34.6277
CID=675557341 | 21 | 42.5 | 14.5417 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 20305.008 | 0.65967 | 0.01076 | 6.8956 | 14.5417 | 100.2743 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 51.8983 | 1.8598 | 0.73806 | 48.6305 | 29.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.5417 | 41.3248
CID=675557314 | 21 | 45 | 16.752 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 21347.5538 | 0.70651 | 0.011809 | 6.2598 | 16.752 | 104.8637 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 54.4747 | 1.9873 | 0.75456 | 44.326 | 33.731 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.752 | 48.6019
CID=675557411 | 21 | 47.5 | 19.0805 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 22241.4036 | 0.75324 | 0.01297 | 5.7169 | 19.0806 | 109.0812 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 57.0148 | 2.1213 | 0.77032 | 49.0224 | 37.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.0805 | 54.2307
CID=675557376 | 21 | 50 | 21.9077 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 23074.2195 | 0.7997 | 0.014395 | 5.1535 | 21.9077 | 112.9013 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 59.9341 | 2.2619 | 0.78746 | 57.0431 | 42.2694 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.9077 | 62.5046
CID=675557217 | 21 | 52.5 | 25.2501 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 24057.2769 | 0.85619 | 0.016114 | 4.6628 | 25.2501 | 117.7368 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 62.8928 | 2.4094 | 0.8052 | 47.5993 | 47.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.2501 | 71.6014
CID=675557190 | 21 | 55 | 28.3799 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 24628.9639 | 0.90177 | 0.017851 | 4.2519 | 28.3799 | 120.6696 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 65.7437 | 2.564 | 0.81966 | 66.5078 | 52.606 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.3799 | 80.9026
CID=675557287 | 21 | 57.5 | 32.5224 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 25438.511 | 0.98552 | 0.02013 | 3.9419 | 32.5225 | 128.2004 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 68.2736 | 2.726 | 0.83603 | 89.8911 | 59.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.5224 | 90.1325
CID=-536362791 | 21 | 60 | 36.0509 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 26161.3449 | 1.0308 | 0.022285 | 3.6119 | 36.0509 | 130.213 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 71.1317 | 2.8955 | 0.84785 | 82.8129 | 64.603 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.0509 | 90.1326
CID=-536362694 | 21 | 62.5 | 39.8051 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 27148.1727 | 1.0767 | 0.024686 | 3.3141 | 39.8051 | 131.9197 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 74.0142 | 3.0728 | 0.85861 | 56.4278 | 70.437 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.8051 | 90.1326
CID=-536362729 | 21 | 65 | 44.3855 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 27711.6615 | 1.1471 | 0.02764 | 3.067 | 44.3855 | 136.1299 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 76.7145 | 3.2582 | 0.86958 | 62.5657 | 77.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44.3855 | 90.1326
CID=-536362888 | 21 | 67.5 | 49.2427 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 28740.7969 | 1.2141 | 0.030942 | 2.8305 | 49.2427 | 139.3816 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 79.5229 | 3.4519 | 0.87908 | 58.028 | 85.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.2427 | 90.1326
CID=-536362915 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-536362818 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-536362853 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-536363012 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-536363039 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-536362942 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366388 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366485 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366450 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366291 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366264 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366361 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366326 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366167 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366140 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545366237 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374222321 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374222224 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-374222259 | 24 | 37.5 | 10.7318 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18282.5476 | 0.80286 | 0.0089538 | 12.0485 | 10.7318 | 129.3013 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 44.2999 | 1.4799 | 0.70568 | 58.8856 | 23.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=-374222418 | 24 | 40 | 10.888 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 18140.5036 | 0.67738 | 0.0092027 | 9.7999 | 10.888 | 106.7018 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 47.5115 | 1.5849 | 0.70711 | 48.847 | 23.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2758 | 10.888 | 28.8692
CID=-374222445 | 24 | 42.5 | 12.5977 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 18962.2998 | 0.67012 | 0.0099699 | 8.19 | 12.5977 | 103.175 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 50.9301 | 1.6955 | 0.7222 | 35.4012 | 26.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.5977 | 35.3309
CID=-374222348 | 24 | 45 | 14.8492 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 20113.684 | 0.69351 | 0.010984 | 7.0235 | 14.8492 | 104.2927 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 54.2986 | 1.8118 | 0.74045 | 23.1822 | 30.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.8492 | 42.1901
CID=-374222383 | 24 | 47.5 | 17.2586 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 20827.2683 | 0.75503 | 0.012127 | 6.4211 | 17.2587 | 110.8203 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 56.7236 | 1.9339 | 0.75813 | 54.3168 | 34.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.2586 | 49.7239
CID=-374222542 | 24 | 50 | 19.8019 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 22004.2708 | 0.81306 | 0.013395 | 5.8772 | 19.8019 | 116.3806 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 59.1913 | 2.0621 | 0.77489 | 33.7811 | 38.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.8019 | 57.9119
CID=-374222569 | 24 | 52.5 | 22.5727 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 22548.5033 | 0.86758 | 0.014832 | 5.3606 | 22.5727 | 121.0024 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 61.8035 | 2.1966 | 0.79119 | 61.2613 | 43.3469 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.5727 | 64.0509
CID=-374222472 | 24 | 55 | 26.0461 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 23667.8908 | 0.91839 | 0.016643 | 4.7874 | 26.0461 | 124.6932 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 64.9756 | 2.3376 | 0.80906 | 51.2497 | 48.9121 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.0461 | 73.2965
CID=707506858 | 24 | 57.5 | 29.3599 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 24216.1151 | 0.97547 | 0.018502 | 4.3871 | 29.36 | 128.8047 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 67.6637 | 2.4852 | 0.8238 | 64.3204 | 54.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.3599 | 83.1958
CID=707506955 | 24 | 60 | 32.9235 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 24979.2916 | 1.0257 | 0.020588 | 3.9964 | 32.9235 | 131.5753 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 70.5641 | 2.6398 | 0.83746 | 78.7903 | 59.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.9235 | 90.1325
CID=707506920 | 24 | 62.5 | 36.5949 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 25717.4626 | 1.0757 | 0.022858 | 3.6591 | 36.5949 | 133.9054 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 73.4072 | 2.8015 | 0.84952 | 88.1696 | 65.4491 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.5949 | 90.1326
CID=707506761 | 24 | 65 | 40.7589 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 26548.0421 | 1.1395 | 0.025512 | 3.3725 | 40.7589 | 137.4611 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 76.1393 | 2.9705 | 0.86107 | 66.6223 | 71.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.7589 | 90.1326
CID=707506734 | 24 | 67.5 | 45.532 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 27407.4453 | 1.2249 | 0.028644 | 3.1411 | 45.532 | 143.0193 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 78.632 | 3.147 | 0.87201 | 54.6984 | 79.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.532 | 90.1326
CID=707506831 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707506796 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707506637 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707506610 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=707506707 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413371 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413274 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413309 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413468 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413495 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413398 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413433 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413592 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413619 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-504413522 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577315808 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577315905 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577315870 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577315711 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577315684 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=577315781 | 27 | 42.5 | 12.0582 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 18278.244 | 0.78888 | 0.0096706 | 10.1996 | 12.0582 | 122.9895 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 49.877 | 1.5489 | 0.71756 | 49.1044 | 25.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.0582 | 29.3459
CID=577315746 | 27 | 45 | 12.2922 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 18408.1045 | 0.68218 | 0.0099756 | 8.4534 | 12.2923 | 103.9119 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 53.1501 | 1.6551 | 0.71959 | 39.5045 | 25.954 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.2922 | 35.9335
CID=577315587 | 27 | 47.5 | 14.8597 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 19737.04 | 0.7304 | 0.011111 | 7.3098 | 14.8597 | 108.6206 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 56.3304 | 1.7667 | 0.74054 | 26.866 | 30.4874 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.8597 | 43.0269
CID=577315560 | 27 | 50 | 17.4382 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 20365.3572 | 0.78621 | 0.012335 | 6.5409 | 17.4382 | 114.0616 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 59.0958 | 1.8839 | 0.75937 | 54.4568 | 34.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.4382 | 50.8249
CID=577315657 | 27 | 52.5 | 19.9821 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 21512.7123 | 0.84196 | 0.013628 | 5.9584 | 19.9821 | 119.062 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 61.628 | 2.0067 | 0.77601 | 37.5113 | 39.1226 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.9821 | 59.2263
CID=-568315410 | 27 | 55 | 22.6823 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 22186.5381 | 0.89756 | 0.015065 | 5.4494 | 22.6823 | 123.6058 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 64.1599 | 2.1355 | 0.7918 | 56.4602 | 43.524 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.6823 | 65.5153
CID=-568315379 | 27 | 57.5 | 26.0535 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 23111.4414 | 0.9528 | 0.016869 | 4.8998 | 26.0535 | 127.6579 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 67.1359 | 2.2704 | 0.8091 | 54.0901 | 48.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.0535 | 74.9452
CID=-568315348 | 27 | 60 | 30.1043 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 23958.3748 | 1.0356 | 0.019079 | 4.4795 | 30.1044 | 134.8517 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 69.8613 | 2.4116 | 0.82683 | 47.5994 | 55.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.1043 | 85.2525
CID=-568315317 | 27 | 62.5 | 33.5524 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 24536.1575 | 1.0813 | 0.021168 | 4.0739 | 33.5525 | 136.6885 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 72.7507 | 2.5593 | 0.83967 | 66.5078 | 60.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.5524 | 90.1325
CID=-568315534 | 27 | 65 | 38.1555 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 25299.4125 | 1.1739 | 0.023923 | 3.7712 | 38.1555 | 143.8921 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 75.3047 | 2.7136 | 0.85409 | 89.774 | 67.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.1555 | 90.1326
CID=-568315503 | 27 | 67.5 | 41.9411 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 25976.6278 | 1.2178 | 0.026485 | 3.4466 | 41.9411 | 144.554 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 78.1928 | 2.875 | 0.86399 | 82.825 | 73.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.9411 | 90.1326
CID=-568315472 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568315441 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568315658 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-568315627 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413769 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413800 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413831 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413862 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413645 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413676 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413707 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413738 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413521 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513413552 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406174940 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406174909 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406174878 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406174847 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406175064 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406175033 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406175002 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-406174971 | 30 | 45 | 12.2153 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 18042.4644 | 0.8677 | 0.0098264 | 10.9562 | 12.2153 | 133.8338 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 51.7948 | 1.515 | 0.71892 | 52.129 | 25.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3242 | 12.2153 | 30.0035
CID=-406175188 | 30 | 47.5 | 12.6305 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 18225.4888 | 0.73469 | 0.010202 | 8.7619 | 12.6305 | 110.6677 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 55.4076 | 1.6171 | 0.72248 | 36.7154 | 26.5614 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.6305 | 36.4854
CID=-406175157 | 30 | 50 | 15.2979 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 19306.2629 | 0.79557 | 0.011398 | 7.6445 | 15.2979 | 116.9444 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 58.3691 | 1.7244 | 0.74389 | 25.6495 | 31.2451 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.2979 | 43.826
CID=675554239 | 30 | 52.5 | 18.16 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 20114.1471 | 0.85629 | 0.012757 | 6.7582 | 18.16 | 122.7296 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 61.275 | 1.8368 | 0.76428 | 45.0637 | 36.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.16 | 51.8244
CID=675554270 | 30 | 55 | 20.8596 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 21010.4719 | 0.91697 | 0.014144 | 6.138 | 20.8596 | 128.037 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 63.8215 | 1.9547 | 0.78135 | 48.2097 | 40.5619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.8596 | 60.4554
CID=675554301 | 30 | 57.5 | 23.677 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 21988.4377 | 0.97752 | 0.015668 | 5.6107 | 23.677 | 132.845 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 66.3278 | 2.0782 | 0.79717 | 41.3219 | 45.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.677 | 68.5376
CID=675554332 | 30 | 60 | 26.9058 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 22585.0689 | 1.0378 | 0.017461 | 5.0967 | 26.9058 | 137.1298 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 69.0347 | 2.2074 | 0.81309 | 62.5903 | 50.2763 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.9058 | 76.6398
CID=675554115 | 30 | 62.5 | 30.8512 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 23631.6353 | 1.0977 | 0.019682 | 4.566 | 30.8512 | 140.8659 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 72.1238 | 2.3426 | 0.82977 | 49.9551 | 56.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.8512 | 87.1331
CID=675554146 | 30 | 65 | 34.4695 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 24106.5349 | 1.1575 | 0.021905 | 4.1806 | 34.4695 | 144.1024 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 74.8257 | 2.4839 | 0.84277 | 64.8839 | 62.1414 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.4695 | 90.1325
CID=675554177 | 30 | 67.5 | 38.5113 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 24843.5555 | 1.217 | 0.024477 | 3.8115 | 38.5113 | 146.7878 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 77.6853 | 2.6315 | 0.85509 | 79.0619 | 68.4275 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.5113 | 90.1325
CID=675554208 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 3.8194 | 4.3303
[37 empty] | 3.8092 | 8.6947
[37 empty] | 4.4307 | 11.0329
[37 empty] | 5.2867 | 13.7049
[37 empty] | 6.1823 | 16.1956
[37 empty] | 7.2299 | 19.3754
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0

## TGH285-noEcon_APower 0 (2)
PN | 2718315
Calculation Type | FROM_POWER
Units | SI
Use Economizer? | FALSE
Compressor | TGH285-E-3-MT-SL
| Step SST | Step SDT | Percent Power |  | Subcooling
| 3 | 2.5 | 0 |  | 6 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 11 | 11
| INPUT BLOCK | [5 empty] | 1: OUTPUT
CID | SST Verd. Temp | SDT Kond. Temperatur | Value Power | SSH Superheat | LLT Leaving Liquid Temp | tapp T approach Economizer | ENTROPY_SUCTION | SPEED_SOUND | DENSITY_SUCTION | ENTHALPY_LIQUID_CONDENSER_EXIT | ENTHALPY_DISCHARGE_ISENTROPIC | ENTHALPY_SUCTION | SPEED_COMPRESSOR | MASS_FLOW_RATE_EVAPORATOR | MASS_FLOW_RATE_MOTOR_COOLING | COEFFICIENT_OF_PERFORMANCE | POWER_INPUT_ELECTRICAL | CAPACITY_EVAPORATOR | TEMPERATURE_SUCT_SAT | TEMPERATURE_DISCH_SAT | TEMPERATURE_SUCT_SUPER_HEAT | TEMPERATURE_CONDENSER_LIQUID_LEAVING | PRESSURE_SUCT_ABSOLUTE | PRESSURE_DISCH_ABSOLUTE | TEMPERATURE_DISCH | PRESSURE_RATIO | POWER_FACTOR | IGV_ANGLE | INPUT_CURRENT | ECON_SAT_TEMP | ECON_INTERSTAGE_P | ECON_CAPACITY | ECON_MASS_FLOW | TEMPERATURE_ECO_LIQUID_LEAVING | ENTHALPY_LIQUID_ECO_EXIT | TOLERANCE | POWER_INPUT_ELECTRICAL | POWER_INPUT_ELECTRICAL
CID=1002403026 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-583883891 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2124796488 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=182279211 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=81522662 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1504764255 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1203916124 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-738601153 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-839357702 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1103162778 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1002406229 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-583880688 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2124799691 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=182282414 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=81525865 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1504761052 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1203919327 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-738597950 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-839354499 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1103157529 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1002400980 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-583885937 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2124794442 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=182277165 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=81520616 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1504766301 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1203914078 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-738603199 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-839359748 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1103160476 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1002403927 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-583882990 | -15 | -5 | 3.8194 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18379.9421 | 0.21348 | 0.0069779 | 10.6284 | 3.8194 | 40.594 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 3.9657 | 1.4946 | 0.6315 | 60.0336 | 9.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=2124797389 | -15 | -2.5 | 3.8092 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 18258.0774 | 0.16427 | 0.0070592 | 8.1171 | 3.8092 | 30.9202 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 8.051 | 1.6437 | 0.63137 | 42.6137 | 9.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1631 | 3.8092 | 8.6947
CID=182280112 | -15 | 0 | 4.4307 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 19735.2322 | 0.1724 | 0.0068375 | 7.198 | 4.4307 | 31.8924 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 12.1262 | 1.804 | 0.63898 | 28.5396 | 10.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.4307 | 11.0329
CID=81523563 | -15 | 2.5 | 5.2867 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 20805.0487 | 0.19271 | 0.0068619 | 6.6252 | 5.2867 | 35.0254 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 15.5052 | 1.9762 | 0.64914 | 54.3169 | 12.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.2867 | 13.7049
CID=-1504763354 | -15 | 5 | 6.1823 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 22223.2326 | 0.21354 | 0.007054 | 6.1652 | 6.1823 | 38.1149 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 18.3245 | 2.1607 | 0.65937 | 46.0636 | 14.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.1823 | 16.1956
CID=1203917025 | -15 | 7.5 | 7.2299 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 23424.1101 | 0.22817 | 0.0073625 | 5.5296 | 7.2299 | 39.9786 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 22.0414 | 2.3583 | 0.67085 | 51.2498 | 16.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.2299 | 19.3754
CID=-738600252 | -15 | 10 | 8.5747 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 24387.515 | 0.25415 | 0.0078105 | 5.0956 | 8.5747 | 43.6936 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 25.1914 | 2.5693 | 0.68485 | 65.3109 | 19.0232 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5747 | 23.0861
CID=-839356801 | -15 | 12.5 | 10.0921 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 25518.2818 | 0.28116 | 0.0083705 | 4.6975 | 10.0921 | 47.408 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 28.3226 | 2.7945 | 0.6997 | 91.1196 | 21.9142 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.0921 | 27.0734
CID=1103163675 | -15 | 15 | 11.5676 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 26685.2565 | 0.30061 | 0.0089729 | 4.2955 | 11.5676 | 49.6882 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 31.6805 | 3.0345 | 0.71324 | 66.6222 | 24.6411 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.5676 | 30.0979
CID=1002407126 | -15 | 17.5 | 13.3575 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 27710.9998 | 0.32719 | 0.0097193 | 3.9669 | 13.3575 | 52.9875 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 34.8318 | 3.2899 | 0.72856 | 62.5656 | 27.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.3575 | 34.2767
CID=-583879791 | -15 | 20 | 15.3391 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 29040.967 | 0.35269 | 0.010579 | 3.6463 | 15.3391 | 55.9317 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 38.2193 | 3.5612 | 0.7442 | 54.2825 | 31.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.3391 | 38.2422
CID=2124800588 | -15 | 22.5 | 17.6718 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 29698.7413 | 0.38822 | 0.011611 | 3.4096 | 17.6718 | 60.2545 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 41.0371 | 3.8493 | 0.76098 | 60.9766 | 35.283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.6718 | 39.9189
CID=182283311 | -15 | 25 | 19.9411 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 30609.0676 | 0.41473 | 0.01268 | 3.1572 | 19.9411 | 62.9588 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 44.2438 | 4.1546 | 0.77576 | 62.7732 | 39.055 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.9411 | 40.1319
CID=81526762 | -15 | 27.5 | 22.9327 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 31266.0418 | 0.45013 | 0.014074 | 2.9126 | 22.9327 | 66.7946 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 47.7398 | 4.4779 | 0.79317 | 73.0309 | 43.9283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9327 | 40.079
CID=-1504760155 | -15 | 30 | 26.5427 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 31930.2043 | 0.49858 | 0.015779 | 2.7227 | 26.5427 | 72.2681 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 50.7324 | 4.8198 | 0.81141 | 97.8722 | 49.7007 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.5427 | 40.0954
CID=1203920224 | -15 | 32.5 | 30.1228 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 32831.9828 | 0.54601 | 0.017566 | 2.5646 | 30.1229 | 77.2539 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 53.36 | 5.1811 | 0.8269 | 86.677 | 55.3476 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.1228 | 40.4314
CID=-738597053 | -15 | 35 | 35.7098 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33545.2398 | 0.627 | 0.020261 | 2.4231 | 35.7098 | 86.5285 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 55.9282 | 5.5624 | 0.84678 | 99.2484 | 64.0724 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.7098 | 39.9119
CID=-839353602 | -15 | 37.5 | 40.2301 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1103166878 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1002410329 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-583876588 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2124803791 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=182286514 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=81529965 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1504756952 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1203923427 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-738593850 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-839350399 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1103161629 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1002405080 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-583881837 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2124798542 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=182281265 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=81524716 | -12 | 0 | 4.1993 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 18384.81 | 0.20856 | 0.0068425 | 9.2921 | 4.1993 | 39.02 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 9.8733 | 1.5931 | 0.63617 | 49.3087 | 10.029 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0431 | 4.1993 | 8.8682
CID=-1504762201 | -12 | 2.5 | 4.6238 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 19195.696 | 0.19506 | 0.0068352 | 7.756 | 4.6238 | 35.862 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 13.8825 | 1.7452 | 0.6413 | 30.941 | 10.9545 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.6238 | 11.4069
CID=1203918178 | -12 | 5 | 5.4802 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 20366.421 | 0.21052 | 0.0069106 | 6.9372 | 5.4802 | 38.0171 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 17.4978 | 1.9081 | 0.65138 | 52.1393 | 12.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.4802 | 14.2089
CID=-738599099 | -12 | 7.5 | 6.3445 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 21855.3975 | 0.2273 | 0.0071228 | 6.3525 | 6.3445 | 40.3034 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 20.473 | 2.0826 | 0.66118 | 33.781 | 14.5792 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.3445 | 17.3877
CID=-839355648 | -12 | 10 | 7.5663 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 22789.9153 | 0.25654 | 0.0074828 | 5.9003 | 7.5663 | 44.6431 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 23.2717 | 2.269 | 0.67443 | 63.2355 | 17.0452 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.5663 | 20.1421
CID=1103148176 | -12 | 12.5 | 8.9351 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 24122.4936 | 0.27743 | 0.0079573 | 5.3005 | 8.9351 | 47.3607 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 26.9004 | 2.4678 | 0.68846 | 47.5994 | 19.7185 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.9351 | 24.0547
CID=1002391627 | -12 | 15 | 10.4239 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 25015.7983 | 0.30209 | 0.0085261 | 4.8509 | 10.424 | 50.566 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 30.0852 | 2.6798 | 0.70282 | 77.5049 | 22.5342 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.4239 | 28.2107
CID=-583895290 | -12 | 17.5 | 11.959 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 26043.1365 | 0.32278 | 0.0091602 | 4.4277 | 11.959 | 52.9514 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 33.3924 | 2.9053 | 0.7167 | 82.8254 | 25.3523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.959 | 32.2434
CID=2124785089 | -12 | 20 | 13.8048 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 27348.2827 | 0.35142 | 0.0099398 | 4.0905 | 13.8048 | 56.4681 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 36.4311 | 3.1449 | 0.73221 | 54.6982 | 28.6453 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.8048 | 36.0111
CID=182267812 | -12 | 22.5 | 15.8745 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 28317.9953 | 0.37886 | 0.010845 | 3.7542 | 15.8745 | 59.5964 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 39.7702 | 3.3993 | 0.7482 | 70.3102 | 32.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.8745 | 40.4827
CID=81511263 | -12 | 25 | 18.0705 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 29290.6412 | 0.40748 | 0.011849 | 3.4705 | 18.0705 | 62.7141 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 42.9138 | 3.6689 | 0.76368 | 56.989 | 35.9514 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.0705 | 44.884
CID=-1504775654 | -12 | 27.5 | 20.8318 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 30111.8936 | 0.44561 | 0.013114 | 3.2191 | 20.8318 | 67.0596 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 46.0335 | 3.9544 | 0.78118 | 59.0954 | 40.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.8318 | 45.1309
CID=1203904725 | -12 | 30 | 23.4146 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 30914.6718 | 0.48505 | 0.014382 | 3.0462 | 23.4146 | 71.3253 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 48.3273 | 4.2564 | 0.79577 | 64.6028 | 44.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.4146 | 44.9448
CID=-738612552 | -12 | 32.5 | 27.064 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 31427.4173 | 0.52296 | 0.016129 | 2.7745 | 27.064 | 75.09 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 52.3393 | 4.5754 | 0.81381 | 85.2528 | 50.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.064 | 44.9312
CID=-839369101 | -12 | 35 | 30.8778 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 32229.4892 | 0.5752 | 0.018039 | 2.6099 | 30.8778 | 80.5883 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 54.986 | 4.9121 | 0.82987 | 93.2704 | 56.5313 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.8778 | 45.1391
CID=1103151375 | -12 | 37.5 | 35.0704 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 33053.8921 | 0.62616 | 0.020208 | 2.4389 | 35.0704 | 85.5323 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 57.9496 | 5.2671 | 0.84474 | 87.0429 | 63.0772 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.0704 | 45.4468
CID=1002394826 | -12 | 40 | 41.392 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 33789.9486 | 0.6761 | 0.023395 | 2.1735 | 41.392 | 89.9669 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 63.3584 | 5.6411 | 0.86265 | 95.4343 | 72.9013 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.392 | 45.2292
CID=-583892091 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2124788288 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=182271011 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=81514462 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1504772455 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1203907924 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-738609353 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-839365902 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225691 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225722 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225629 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225660 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225815 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225846 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225753 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481225784 | -9 | 2.5 | 4.3612 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 18288.7935 | 0.24162 | 0.0068235 | 10.3018 | 4.3612 | 44.9281 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 11.5084 | 1.5462 | 0.63814 | 52.1738 | 10.3836 | 0 | 0 | 0 | 0 | 0 | 0 | 10.295 | 4.3612 | 8.9771
CID=481225443 | -9 | 5 | 4.5803 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 18533.518 | 0.2034 | 0.0068874 | 8.1123 | 4.5803 | 37.1571 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 15.7687 | 1.6906 | 0.64078 | 39.5045 | 10.8603 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.5803 | 11.7505
CID=481225474 | -9 | 7.5 | 5.6398 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 20204.1782 | 0.22482 | 0.0069646 | 7.1517 | 5.6398 | 40.3341 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 19.7753 | 1.8452 | 0.65322 | 23.1821 | 13.1179 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.6398 | 14.6838
CID=288427456 | -9 | 10 | 6.707 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 21263.7005 | 0.25435 | 0.0072281 | 6.6789 | 6.707 | 44.7958 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 22.3465 | 2.0103 | 0.66518 | 48.2233 | 15.3195 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.707 | 18.0132
CID=288427487 | -9 | 12.5 | 7.7039 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 22372.3734 | 0.27146 | 0.0075655 | 6.0891 | 7.7039 | 46.9097 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 25.2658 | 2.1865 | 0.67588 | 55.3675 | 17.3181 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.7039 | 20.8962
CID=288427394 | -9 | 15 | 9.2107 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 23686.4797 | 0.29816 | 0.0080875 | 5.4864 | 9.2107 | 50.5332 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 28.7414 | 2.3743 | 0.69119 | 51.2497 | 20.2465 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.2107 | 24.9456
CID=288427425 | -9 | 17.5 | 10.7125 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 24527.6335 | 0.32266 | 0.0086739 | 5.0042 | 10.7125 | 53.6077 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 31.9 | 2.5741 | 0.7055 | 65.6954 | 23.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7125 | 29.4124
CID=288427580 | -9 | 20 | 12.5811 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 25597.2882 | 0.35679 | 0.0094249 | 4.6163 | 12.5811 | 58.0785 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 34.85 | 2.7864 | 0.72206 | 91.0651 | 26.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.5811 | 34.2136
CID=288427611 | -9 | 22.5 | 14.2865 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 26681.8468 | 0.37698 | 0.010177 | 4.2061 | 14.2866 | 60.0902 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 38.1751 | 3.0118 | 0.73606 | 66.6223 | 29.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.2865 | 37.7584
CID=288427518 | -9 | 25 | 16.365 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 27746.536 | 0.40743 | 0.011103 | 3.8839 | 16.365 | 63.5597 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 41.1947 | 3.2507 | 0.75178 | 62.1583 | 33.0734 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.365 | 42.7201
CID=288427549 | -9 | 27.5 | 18.8057 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 28962.8225 | 0.4412 | 0.012212 | 3.5797 | 18.8057 | 67.3193 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 44.3702 | 3.5036 | 0.76854 | 56.0906 | 37.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.8057 | 47.4545
CID=288427208 | -9 | 30 | 21.4049 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 29571.5695 | 0.47876 | 0.013442 | 3.3358 | 21.4049 | 71.4034 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 47.1897 | 3.7712 | 0.78456 | 59.3723 | 41.4518 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.4049 | 50.6676
CID=288427239 | -9 | 32.5 | 24.4891 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 30428.8418 | 0.52158 | 0.014922 | 3.1028 | 24.4891 | 75.984 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 50.1442 | 4.0538 | 0.80138 | 61.826 | 46.429 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.4891 | 51.064
CID=643366161 | -9 | 35 | 27.363 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 31177.537 | 0.55908 | 0.016403 | 2.9054 | 27.363 | 79.5001 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 52.8305 | 4.3522 | 0.81517 | 68.2381 | 51.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.363 | 50.7666
CID=643366192 | -9 | 37.5 | 31.5427 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 31640.9352 | 0.60314 | 0.018489 | 2.652 | 31.5427 | 83.6509 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 56.7121 | 4.6667 | 0.83241 | 97.4739 | 57.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.5427 | 50.2122
CID=643366099 | -9 | 40 | 35.6622 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 32492.5803 | 0.65925 | 0.020667 | 2.4986 | 35.6622 | 89.1056 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 59.239 | 4.9981 | 0.84663 | 93.2626 | 63.9983 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.6622 | 51.0088
CID=643366130 | -9 | 42.5 | 40.6387 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 33245.1639 | 0.71375 | 0.023335 | 2.3114 | 40.6387 | 93.9328 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 62.6375 | 5.3467 | 0.86077 | 88.7438 | 71.7316 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.6387 | 50.9152
CID=643366285 | -9 | 45 | 47.1582 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 33837.7491 | 0.96844 | 0.026834 | 2.6291 | 47.1582 | 123.9833 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.9529 | 5.7134 | 0.87525 | 108.6144 | 81.862 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=643366316 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643366223 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643366254 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643365913 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643365944 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293962 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293931 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327294024 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293993 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293838 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293807 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293900 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327293869 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327294210 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327294179 | -6 | 5 | 4.7732 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18419.3194 | 0.29704 | 0.0067778 | 11.4983 | 4.7732 | 54.8839 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 13.4304 | 1.5026 | 0.64309 | 58.8967 | 11.277 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=513175111 | -6 | 7.5 | 4.779 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 18319.5431 | 0.23404 | 0.0068993 | 8.8884 | 4.779 | 42.4774 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 17.3585 | 1.64 | 0.64316 | 42.592 | 11.2895 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1863 | 4.779 | 12.0604
CID=513175142 | -6 | 10 | 5.7257 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 19734.3238 | 0.24677 | 0.0070177 | 7.6802 | 5.7257 | 43.9746 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 21.21 | 1.7868 | 0.6542 | 28.0112 | 13.2976 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.7257 | 15.1552
CID=513175049 | -6 | 12.5 | 6.8046 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 20667.1794 | 0.26601 | 0.0072955 | 6.8372 | 6.8046 | 46.524 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 24.6151 | 1.9434 | 0.66625 | 54.3497 | 15.5174 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.8046 | 18.649
CID=513175080 | -6 | 15 | 8.1409 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 22194.077 | 0.30253 | 0.0077208 | 6.376 | 8.1409 | 51.9061 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 27.1073 | 2.1103 | 0.68042 | 33.7812 | 18.1782 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.1409 | 22.5502
CID=513175235 | -6 | 17.5 | 9.4617 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 23058.2835 | 0.32366 | 0.0082154 | 5.7546 | 9.4617 | 54.4482 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 30.2758 | 2.2879 | 0.69365 | 59.3555 | 20.7246 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.4617 | 25.8429
CID=513175266 | -6 | 20 | 11.2332 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 24216.8689 | 0.35614 | 0.0088953 | 5.2271 | 11.2332 | 58.7164 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 33.4764 | 2.4766 | 0.71025 | 47.5997 | 24.0297 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.2332 | 30.5791
CID=513175173 | -6 | 22.5 | 12.9502 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 25104.8106 | 0.38082 | 0.0096171 | 4.7488 | 12.9502 | 61.4981 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 36.7012 | 2.6769 | 0.72518 | 77.9042 | 27.1324 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.9502 | 35.5459
CID=513175204 | -6 | 25 | 14.7519 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 26071.2637 | 0.40403 | 0.010416 | 4.3298 | 14.7519 | 63.8733 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 39.9176 | 2.8892 | 0.7397 | 82.8254 | 30.3004 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.7519 | 40.5021
CID=513174863 | -6 | 27.5 | 16.9384 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 27312.0469 | 0.43761 | 0.011397 | 3.9959 | 16.9384 | 67.6848 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 42.8767 | 3.1141 | 0.75588 | 55.5799 | 34.0466 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.9384 | 44.721
CID=513174894 | -6 | 30 | 19.4722 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 28114.5805 | 0.47549 | 0.01256 | 3.6929 | 19.4722 | 71.9082 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 45.8696 | 3.3519 | 0.77282 | 77.1551 | 38.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.4722 | 50.1265
CID=320376876 | -6 | 32.5 | 22.148 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 29281.6373 | 0.51325 | 0.013842 | 3.4243 | 22.148 | 75.8425 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 48.7912 | 3.6031 | 0.78882 | 57.3728 | 42.6593 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.148 | 55.2599
CID=320376907 | -6 | 35 | 25.0822 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 29912.8608 | 0.55084 | 0.015293 | 3.1687 | 25.0822 | 79.4786 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 51.8504 | 3.8682 | 0.80437 | 60.295 | 47.3769 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.0822 | 56.636
CID=320376814 | -6 | 37.5 | 28.0639 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 30723.6554 | 0.58833 | 0.016844 | 2.9513 | 28.0639 | 82.8253 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 54.6995 | 4.1478 | 0.81828 | 62.9412 | 52.1076 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.0639 | 56.9451
CID=320376845 | -6 | 40 | 31.7052 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 31356.5267 | 0.62966 | 0.018749 | 2.7257 | 31.7053 | 86.4198 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 57.9657 | 4.4423 | 0.83303 | 73.0304 | 57.8268 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.7052 | 56.788
CID=320377000 | -6 | 42.5 | 36.4168 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 31865.6524 | 0.69099 | 0.021208 | 2.5368 | 36.4168 | 92.3811 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 60.9932 | 4.7522 | 0.84898 | 98.6211 | 65.1722 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.4168 | 56.5732
CID=320377031 | -6 | 45 | 40.914 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 32702.6499 | 0.75102 | 0.023721 | 2.3883 | 40.914 | 97.7165 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 63.5103 | 5.0781 | 0.86146 | 88.6684 | 72.159 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.914 | 56.8886
CID=320376938 | -6 | 47.5 | 46.8283 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 33208.5014 | 0.98782 | 0.027314 | 2.6299 | 47.5154 | 124.9625 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 59.4541 | 5.4204 | 0.87593 | 108.0349 | 82.4177 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.8283 | 57.2808
CID=320376969 | -6 | 50 | 53.3934 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34051.8858 | 0.88288 | 0.030801 | 2.0316 | 53.3934 | 108.4757 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 70.5464 | 5.7798 | 0.88577 | 95.3511 | 91.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=320376628 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320376659 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315581 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315612 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315519 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315550 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315705 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315736 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315643 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315674 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315333 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675315364 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295344542 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295344511 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295344604 | -3 | 10 | 5.3391 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 18408.5647 | 0.29119 | 0.0069182 | 9.8323 | 5.3391 | 52.4962 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 19.2343 | 1.5929 | 0.64975 | 49.1469 | 12.4849 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1041 | 5.3391 | 12.2784
CID=-1295344573 | -3 | 12.5 | 5.9798 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 19199.1786 | 0.27618 | 0.0070902 | 8.1737 | 5.9798 | 48.8768 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 23.0434 | 1.7325 | 0.65709 | 32.8298 | 13.8266 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.9798 | 15.6157
CID=-1295344418 | -3 | 15 | 7.1813 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 20396.6364 | 0.29764 | 0.007419 | 7.1972 | 7.1813 | 51.6854 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 26.5009 | 1.8813 | 0.67033 | 44.8285 | 16.2768 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.1813 | 19.2479
CID=-1295344387 | -3 | 17.5 | 8.3228 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 21637.2882 | 0.31903 | 0.007822 | 6.5282 | 8.3228 | 54.3329 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 29.3545 | 2.0396 | 0.68229 | 40.1449 | 18.5335 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.3228 | 23.3226
CID=-1295344480 | -3 | 20 | 9.6291 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 22519.8736 | 0.3442 | 0.0083245 | 5.9677 | 9.6291 | 57.4641 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 32.122 | 2.2079 | 0.69527 | 61.261 | 21.042 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6291 | 26.7511
CID=-1295344449 | -3 | 22.5 | 11.6237 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 23894.3203 | 0.38249 | 0.0090843 | 5.3824 | 11.6237 | 62.563 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 35.4448 | 2.3864 | 0.71374 | 51.2495 | 24.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.6237 | 31.6404
CID=-1295344790 | -3 | 25 | 13.2655 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 24625.7296 | 0.40421 | 0.0097975 | 4.8805 | 13.2655 | 64.7423 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 38.6032 | 2.5757 | 0.7278 | 66.0002 | 27.6927 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.2655 | 36.9411
CID=-1295344759 | -3 | 27.5 | 15.5311 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 25638.1487 | 0.44682 | 0.010768 | 4.5096 | 15.5311 | 70.0394 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 41.3976 | 2.7762 | 0.74564 | 90.8866 | 31.6466 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.5311 | 42.6405
CID=545124531 | -3 | 30 | 17.4826 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 26643.0071 | 0.46769 | 0.011689 | 4.1013 | 17.4826 | 71.7019 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 44.6755 | 2.9882 | 0.75968 | 67.1257 | 34.965 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.4826 | 46.7387
CID=545124562 | -3 | 32.5 | 20.0462 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 27717.1432 | 0.51007 | 0.012884 | 3.8129 | 20.0462 | 76.4344 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 47.3878 | 3.2122 | 0.77641 | 58.7304 | 39.228 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.0462 | 52.5507
CID=545124469 | -3 | 35 | 22.9114 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 28801.2551 | 0.5505 | 0.01426 | 3.5168 | 22.9114 | 80.574 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 50.4262 | 3.4485 | 0.79306 | 70.3081 | 43.894 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9114 | 58.111
CID=545124500 | -3 | 37.5 | 25.5999 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 29461.7927 | 0.57942 | 0.015646 | 3.2334 | 25.5999 | 82.7752 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 53.6227 | 3.6978 | 0.80691 | 56.9188 | 48.2022 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.5999 | 63.3351
CID=545124655 | -3 | 40 | 29.1961 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 30240.1837 | 0.62827 | 0.017469 | 2.9982 | 29.1961 | 87.5361 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 56.6171 | 3.9603 | 0.82312 | 59.0954 | 53.8914 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.1961 | 63.4544
CID=545124686 | -3 | 42.5 | 32.3922 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 30966.3489 | 0.67577 | 0.019234 | 2.8325 | 32.3923 | 91.7519 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 58.8819 | 4.2366 | 0.83556 | 62.6995 | 58.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.3922 | 63.0494
CID=545124593 | -3 | 45 | 36.8219 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 31473.0843 | 0.72125 | 0.02162 | 2.5893 | 36.822 | 95.3437 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 62.545 | 4.5271 | 0.8502 | 85.2522 | 65.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.8219 | 63.027
CID=545124624 | -3 | 47.5 | 41.7507 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 32075.1537 | 0.78677 | 0.024366 | 2.4231 | 41.7507 | 101.1657 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 65.2888 | 4.8323 | 0.86353 | 97.8722 | 73.4583 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.7507 | 63.4939
CID=545124283 | -3 | 50 | 46.6377 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 32873.8902 | 0.85076 | 0.027262 | 2.2793 | 46.6378 | 106.2992 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 67.8048 | 5.1527 | 0.87423 | 86.6769 | 81.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.6377 | 63.7961
CID=545124314 | -3 | 52.5 | 53.5574 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 33345.9168 | 1.1017 | 0.031388 | 2.484 | 53.7902 | 133.6122 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 64.2218 | 5.4887 | 0.88635 | 107.8926 | 92.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.5574 | 63.6127
CID=352326296 | -3 | 55 | 60.1316 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34145.4602 | 0.99407 | 0.035397 | 1.9438 | 60.1316 | 116.8842 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 74.5756 | 5.841 | 0.89438 | 97.0874 | 102.1493 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=352326327 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326234 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326265 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326420 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326451 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326358 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326389 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326048 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352326079 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481231068 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481230909 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481230874 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481230971 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481231192 | 0 | 12.5 | 5.6702 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 18485.4826 | 0.33257 | 0.0069806 | 10.5015 | 5.6702 | 59.5451 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 21.3389 | 1.5491 | 0.65357 | 47.2924 | 13.1814 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.6702 | 13.1874
CID=481231033 | 0 | 15 | 5.883 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 18568.3581 | 0.28471 | 0.0071307 | 8.5041 | 5.883 | 50.0297 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 25.0358 | 1.6821 | 0.65599 | 39.5045 | 13.6257 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.883 | 16.0314
CID=481230998 | 0 | 17.5 | 7.2692 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 20190.9523 | 0.3078 | 0.0074914 | 7.2992 | 7.2692 | 53.059 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 28.9795 | 1.8236 | 0.67127 | 23.4226 | 16.4529 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.2692 | 19.8154
CID=481231095 | 0 | 20 | 8.7353 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 21066.5888 | 0.3513 | 0.0079854 | 6.7972 | 8.7353 | 59.3758 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 31.3481 | 1.9741 | 0.68647 | 54.3168 | 19.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.7353 | 24.0702
CID=481230820 | 0 | 22.5 | 10.1199 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 22327.8968 | 0.37953 | 0.0085287 | 6.212 | 10.1199 | 62.8646 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 34.023 | 2.1337 | 0.69996 | 43.3478 | 21.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.1199 | 28.0987
CID=481230661 | 0 | 25 | 11.7385 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 23272.6667 | 0.40311 | 0.009194 | 5.5715 | 11.7385 | 65.4016 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 37.2499 | 2.303 | 0.71476 | 55.9625 | 24.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.7385 | 32.6801
CID=288432833 | 0 | 27.5 | 13.9765 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 24276.4614 | 0.45002 | 0.010113 | 5.1137 | 13.9765 | 71.4725 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 40.0887 | 2.4822 | 0.73359 | 47.6059 | 28.9469 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.9765 | 38.3214
CID=288432674 | 0 | 30 | 15.9309 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 25154.5739 | 0.47407 | 0.010999 | 4.6238 | 15.9309 | 73.662 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 43.3358 | 2.6717 | 0.74861 | 78.1639 | 32.3325 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.9309 | 44.1758
CID=288432639 | 0 | 32.5 | 18.0018 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 26063.5396 | 0.49915 | 0.011979 | 4.2124 | 18.0018 | 75.8315 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 46.4874 | 2.872 | 0.76322 | 82.8254 | 35.8364 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.0018 | 50.2286
CID=288432736 | 0 | 35 | 20.6907 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 27219.0248 | 0.54458 | 0.013243 | 3.9069 | 20.6907 | 80.8369 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 49.2176 | 3.0833 | 0.78034 | 58.623 | 40.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.6907 | 54.8307
CID=288432957 | 0 | 37.5 | 23.6252 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 27918.5787 | 0.58956 | 0.014672 | 3.6167 | 23.6252 | 85.4458 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 52.0589 | 3.3062 | 0.79689 | 62.5691 | 45.0435 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.6252 | 61.2623
CID=288432798 | 0 | 40 | 26.4682 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 29189.0143 | 0.62014 | 0.016146 | 3.313 | 26.4682 | 87.6881 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 55.309 | 3.5409 | 0.81106 | 54.2825 | 49.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.4682 | 67.1838
CID=288432763 | 0 | 42.5 | 29.9202 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 29704.7489 | 0.67308 | 0.017949 | 3.1009 | 29.9202 | 92.78 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 57.8748 | 3.7879 | 0.82609 | 59.3724 | 55.0294 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.9202 | 70.4572
CID=288432860 | 0 | 45 | 33.7902 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 30489.1136 | 0.72418 | 0.020029 | 2.8775 | 33.7902 | 97.2304 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 60.7993 | 4.0477 | 0.84048 | 61.826 | 61.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.7902 | 71.0175
CID=288432585 | 0 | 47.5 | 37.3283 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 31178.7424 | 0.77375 | 0.022091 | 2.7082 | 37.3283 | 101.0941 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 63.1879 | 4.3205 | 0.85171 | 64.6031 | 66.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 37.3283 | 70.5862
CID=288432426 | 0 | 50 | 42.4342 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 31570.3412 | 0.82097 | 0.024967 | 2.4574 | 42.4343 | 104.2779 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 67.1131 | 4.607 | 0.86517 | 85.2542 | 74.5198 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.4342 | 70.2774
CID=643371538 | 0 | 52.5 | 47.5636 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 32271.7587 | 0.89072 | 0.028034 | 2.31 | 47.5636 | 109.872 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 69.6224 | 4.9075 | 0.87602 | 97.8716 | 82.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.5636 | 70.9719
CID=643371379 | 0 | 55 | 52.837 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 33008.9618 | 0.95869 | 0.031368 | 2.171 | 52.837 | 114.7112 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 72.1322 | 5.2224 | 0.88494 | 86.6769 | 90.7148 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52.837 | 71.2608
CID=643371344 | 0 | 57.5 | 60.8149 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 33491.1567 | 1.191 | 0.036234 | 2.2703 | 60.8149 | 138.0697 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 70.2336 | 5.5522 | 0.89512 | 105.8926 | 103.2244 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.8149 | 71.0549
CID=643371441 | 0 | 60 | 67.3745 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34214.8195 | 1.1117 | 0.040731 | 1.8506 | 67.3745 | 124.6827 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 78.7717 | 5.8975 | 0.90124 | 97.0874 | 113.5826 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=643371662 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643371503 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643371468 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643371565 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643371290 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643371131 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288585 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288744 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288779 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288682 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288461 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288620 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327288655 | 3 | 15 | 6.0686 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 18384.9627 | 0.40183 | 0.007068 | 11.772 | 6.0686 | 71.4398 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 22.8745 | 1.5081 | 0.65809 | 59.0782 | 14.0107 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=-1327288558 | 3 | 17.5 | 6.1159 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 18331.1857 | 0.32299 | 0.0072092 | 9.2124 | 6.1159 | 56.3424 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 26.6839 | 1.635 | 0.65862 | 42.5768 | 14.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2074 | 6.1159 | 16.4081
CID=-1327288833 | 3 | 20 | 7.4444 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 19693.1882 | 0.34241 | 0.0075851 | 7.869 | 7.4444 | 58.5804 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 30.3776 | 1.7699 | 0.67314 | 27.023 | 16.8029 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.4444 | 20.3842
CID=-1327288992 | 3 | 22.5 | 8.8813 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 20564.9261 | 0.36883 | 0.0080861 | 6.9645 | 8.8813 | 61.8543 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 33.5994 | 1.9131 | 0.68793 | 54.495 | 19.6151 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.8813 | 24.8225
CID=513180488 | 3 | 25 | 10.3039 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 21946.8319 | 0.39771 | 0.0086513 | 6.3417 | 10.304 | 65.3443 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 36.2994 | 2.0648 | 0.7017 | 33.781 | 22.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.3039 | 29.7346
CID=513180329 | 3 | 27.5 | 12.151 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 22707.0676 | 0.44139 | 0.0094004 | 5.8442 | 12.151 | 71.0122 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 38.8537 | 2.2255 | 0.71837 | 61.2612 | 25.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.151 | 33.7526
CID=513180294 | 3 | 30 | 14.3139 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 24009.6867 | 0.4743 | 0.010313 | 5.217 | 14.3139 | 74.6758 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 42.2649 | 2.3954 | 0.73627 | 49.6423 | 29.5376 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.3139 | 39.5659
CID=513180391 | 3 | 32.5 | 16.265 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 24683.4774 | 0.50032 | 0.011214 | 4.7366 | 16.265 | 77.041 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 45.323 | 2.575 | 0.75106 | 66.2486 | 32.903 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.265 | 45.7721
CID=513180612 | 3 | 35 | 18.9753 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 25642.0824 | 0.55294 | 0.012442 | 4.3856 | 18.9753 | 83.2171 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 47.9875 | 2.7645 | 0.76964 | 90.637 | 37.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.9753 | 52.4501
CID=513180453 | 3 | 37.5 | 21.2782 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 26570.0719 | 0.57871 | 0.013591 | 3.9978 | 21.2782 | 85.0667 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 51.1215 | 2.9643 | 0.78382 | 69.2762 | 41.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.2782 | 57.13
CID=513180418 | 3 | 40 | 24.2945 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 27655.6085 | 0.63107 | 0.015079 | 3.7266 | 24.2945 | 90.535 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 53.6809 | 3.1747 | 0.80038 | 55.4416 | 46.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.2945 | 63.85
CID=513180515 | 3 | 42.5 | 27.2941 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 28513.2347 | 0.66332 | 0.016645 | 3.4001 | 27.2941 | 92.803 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 56.982 | 3.3962 | 0.81486 | 70.3101 | 50.8911 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.2941 | 70.4485
CID=513180240 | 3 | 45 | 30.628 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 29372.0316 | 0.70848 | 0.018437 | 3.1535 | 30.628 | 96.584 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 59.8106 | 3.6291 | 0.8289 | 57.1748 | 56.1399 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.628 | 77.0074
CID=513180081 | 3 | 47.5 | 34.4646 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 29986.1631 | 0.76022 | 0.020545 | 2.9275 | 34.4646 | 100.8938 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 62.6622 | 3.8738 | 0.84276 | 60.0823 | 62.1337 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.4646 | 78.0241
CID=320382253 | 3 | 50 | 38.3198 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 30714.2625 | 0.81182 | 0.022789 | 2.7346 | 38.3198 | 104.7897 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 65.3102 | 4.1306 | 0.85456 | 63.436 | 68.13 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.3198 | 78.3946
CID=320382094 | 3 | 52.5 | 42.5765 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 31326.8028 | 0.86311 | 0.02535 | 2.5424 | 42.5765 | 108.2449 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 68.17 | 4.4 | 0.8655 | 70.7725 | 74.7407 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.5765 | 78.2557
CID=320382059 | 3 | 55 | 48.3691 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 31713.2052 | 0.92914 | 0.028781 | 2.3381 | 48.3692 | 113.09 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 71.5247 | 4.6823 | 0.87752 | 97.4739 | 83.7468 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.3691 | 77.4469
CID=320382156 | 3 | 57.5 | 53.8459 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 32435.6001 | 1.0031 | 0.032291 | 2.1979 | 53.8459 | 118.3472 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 73.9908 | 4.9781 | 0.88643 | 93.2703 | 92.2918 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.8459 | 78.4246
CID=320382377 | 3 | 60 | 59.7005 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 33115.5477 | 1.0749 | 0.036228 | 2.0565 | 59.7005 | 122.7764 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 76.6431 | 5.2877 | 0.8939 | 87.0428 | 101.4713 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 59.7005 | 78.6223
CID=320382218 | 3 | 62.5 | 68.5754 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 33625.8435 | 1.2619 | 0.041983 | 2.0319 | 68.5754 | 139.3374 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 77.0407 | 5.6115 | 0.90218 | 102.0569 | 115.4862 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.5754 | 77.8125
CID=320382183 | 3 | 65 | 75.117 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34259.8974 | 1.2377 | 0.04694 | 1.7561 | 75.117 | 131.9152 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 83.036 | 5.95 | 0.90655 | 97.0875 | 125.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=320382280 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320382005 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381846 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320958 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320799 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320764 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320861 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675321082 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320923 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320888 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320985 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320710 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675320551 | 6 | 20 | 6.8403 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 18381.545 | 0.39526 | 0.0073763 | 10.0042 | 6.8403 | 68.4315 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 28.6135 | 1.5911 | 0.66664 | 49.0253 | 15.5898 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1591 | 6.8403 | 16.6703
CID=-1295339165 | 6 | 22.5 | 7.7456 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 19160.1475 | 0.37981 | 0.0077111 | 8.3239 | 7.7456 | 64.4739 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 32.2549 | 1.7198 | 0.67631 | 34.3339 | 17.4006 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.7456 | 20.9315
CID=-1295339324 | 6 | 25 | 9.3478 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 20374.258 | 0.40905 | 0.0082768 | 7.2795 | 9.3478 | 68.0478 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 35.5769 | 1.8563 | 0.69254 | 38.6252 | 20.508 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.3478 | 25.5163
CID=-1295339359 | 6 | 27.5 | 10.8391 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 21395.2776 | 0.43826 | 0.0088823 | 6.588 | 10.8391 | 71.4076 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 38.3035 | 2.0007 | 0.70667 | 46.359 | 23.3043 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.8391 | 30.6162
CID=-1295339262 | 6 | 30 | 12.4236 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 22397.9505 | 0.46738 | 0.0095688 | 6.0003 | 12.4236 | 74.5451 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 40.9782 | 2.1535 | 0.72072 | 51.4417 | 26.1903 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.4236 | 34.7884
CID=-1295339041 | 6 | 32.5 | 14.4257 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 23436.6059 | 0.49632 | 0.010444 | 5.3683 | 14.4257 | 77.4421 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 44.2161 | 2.3149 | 0.73716 | 52.944 | 29.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.4257 | 40.7528
CID=-1295339200 | 6 | 35 | 17.097 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 24316.996 | 0.55477 | 0.011611 | 4.95 | 17.097 | 84.6299 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 46.8714 | 2.4852 | 0.757 | 62.5752 | 34.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.097 | 47.374
CID=-1295339235 | 6 | 37.5 | 19.3967 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 25166.2916 | 0.58347 | 0.012717 | 4.4834 | 19.3967 | 86.9627 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 50.0117 | 2.6649 | 0.77234 | 78.3376 | 38.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.3967 | 54.193
CID=-1295339138 | 6 | 40 | 21.7901 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 26025.9846 | 0.61208 | 0.013922 | 4.0874 | 21.7901 | 89.065 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 53.0791 | 2.8541 | 0.78678 | 83.7371 | 42.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.7901 | 61.371
CID=-1295339413 | 6 | 42.5 | 25.0078 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 27095.2485 | 0.6701 | 0.015515 | 3.8038 | 25.0078 | 95.1259 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 55.6517 | 3.0532 | 0.804 | 61.546 | 47.2581 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.0078 | 66.415
CID=-1295339572 | 6 | 45 | 28.0513 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 27865.474 | 0.70924 | 0.017131 | 3.4987 | 28.0513 | 98.1425 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 58.618 | 3.2625 | 0.81823 | 62.5656 | 52.0877 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.0513 | 73.8077
CID=545129908 | 6 | 47.5 | 31.5834 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 29002.4683 | 0.756 | 0.019044 | 3.2259 | 31.5834 | 101.8843 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 61.5859 | 3.4825 | 0.83257 | 56.6601 | 57.6362 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.5834 | 80.6463
CID=545129749 | 6 | 50 | 35.1297 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 29523.2587 | 0.80055 | 0.021076 | 2.9883 | 35.1297 | 104.9764 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 64.443 | 3.7134 | 0.84493 | 56.9188 | 63.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.1297 | 86.4588
CID=545129714 | 6 | 52.5 | 39.549 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 30241.1278 | 0.85772 | 0.023616 | 2.7644 | 39.5491 | 109.3279 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 67.4141 | 3.9556 | 0.85793 | 59.0954 | 70.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.549 | 86.5615
CID=545129811 | 6 | 55 | 43.4253 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 30902.4611 | 0.9131 | 0.02607 | 2.6024 | 43.4253 | 113.0111 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 69.7482 | 4.2094 | 0.86746 | 62.6993 | 76.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.4253 | 85.8853
CID=545130032 | 6 | 57.5 | 48.4863 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 31418.9028 | 0.96592 | 0.029239 | 2.3913 | 48.4864 | 115.9446 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 73.0353 | 4.4753 | 0.87773 | 73.0305 | 83.9293 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.4863 | 86.5751
CID=545129873 | 6 | 60 | 54.7344 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 31845.4985 | 1.0459 | 0.033195 | 2.2218 | 54.7344 | 121.6087 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 75.9374 | 4.7536 | 0.88769 | 98.6211 | 93.6816 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.7344 | 86.0097
CID=545129838 | 6 | 62.5 | 60.5946 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 32567.5523 | 1.124 | 0.037237 | 2.0862 | 60.5947 | 126.4134 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 78.4041 | 5.0447 | 0.89489 | 93.2685 | 102.8779 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.5946 | 87.0244
CID=545129935 | 6 | 65 | 67.1624 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 33194.5677 | 1.1996 | 0.041945 | 1.9402 | 67.1624 | 130.3083 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 81.2524 | 5.349 | 0.90107 | 87.0429 | 113.2467 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.1624 | 87.1744
CID=545129660 | 6 | 67.5 | 76.7476 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 33708.1622 | 1.3621 | 0.048634 | 1.8591 | 76.7476 | 142.6829 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 82.8722 | 5.667 | 0.90746 | 99.979 | 128.4969 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.7476 | 86.2309
CID=545129501 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331673 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331514 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331479 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331576 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331797 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331638 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331603 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331700 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331425 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352331266 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481227869 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481227900 | 9 | 22.5 | 7.3644 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 18477.6118 | 0.4534 | 0.0075368 | 10.5765 | 7.3644 | 77.8896 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 30.8087 | 1.5501 | 0.67229 | 47.882 | 16.6433 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.3644 | 17.597
CID=481227675 | 9 | 25 | 7.5779 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 18557.5134 | 0.38823 | 0.0077355 | 8.6271 | 7.5779 | 65.3753 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 34.3393 | 1.6731 | 0.67455 | 39.5045 | 17.0684 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.5779 | 21.4167
CID=481227706 | 9 | 27.5 | 9.3386 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 20077.7768 | 0.41966 | 0.0083435 | 7.4137 | 9.3386 | 69.2338 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 37.9373 | 1.8033 | 0.69245 | 24.988 | 20.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.3386 | 26.1844
CID=481227993 | 9 | 30 | 11.0478 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 20831.5168 | 0.46091 | 0.0090225 | 6.7391 | 11.0478 | 74.4525 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 40.577 | 1.941 | 0.70857 | 54.3169 | 23.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.0478 | 31.5026
CID=481228024 | 9 | 32.5 | 12.9917 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 22181.171 | 0.51024 | 0.0098384 | 6.2082 | 12.9917 | 80.6554 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 43.0071 | 2.0864 | 0.72553 | 33.7811 | 27.2063 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.9917 | 37.3388
CID=481227799 | 9 | 35 | 15.0271 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 22864.9591 | 0.54896 | 0.010746 | 5.6473 | 15.0271 | 84.863 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 45.7556 | 2.24 | 0.74182 | 63.3535 | 30.7774 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.0271 | 41.988
CID=481227830 | 9 | 37.5 | 17.4302 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 24078.734 | 0.58078 | 0.011842 | 5.0342 | 17.4302 | 87.7465 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 49.1169 | 2.4019 | 0.75932 | 48.6763 | 34.8768 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.4302 | 48.8161
CID=481227621 | 9 | 40 | 19.739 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 24702.0825 | 0.61258 | 0.012971 | 4.5791 | 19.739 | 90.3874 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 52.0836 | 2.5724 | 0.7745 | 66.4607 | 38.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.739 | 55.9939
CID=481227652 | 9 | 42.5 | 22.9419 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 25609.8866 | 0.67689 | 0.014507 | 4.2486 | 22.9419 | 97.4701 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 54.644 | 2.7519 | 0.79322 | 90.3615 | 43.9432 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9419 | 63.7251
CID=288429634 | 9 | 45 | 25.6277 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 26464.8565 | 0.70839 | 0.015929 | 3.8813 | 25.6277 | 99.4691 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 57.6596 | 2.9406 | 0.80705 | 71.3427 | 48.2464 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.6277 | 69.0029
CID=288429665 | 9 | 47.5 | 28.871 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 27523.9272 | 0.75817 | 0.01766 | 3.5926 | 28.8711 | 103.7224 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 60.3796 | 3.1388 | 0.82175 | 54.6982 | 53.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.871 | 76.6845
CID=288429440 | 9 | 50 | 32.4252 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 28207.7606 | 0.80347 | 0.019623 | 3.2998 | 32.4252 | 106.9977 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 63.4034 | 3.3469 | 0.83568 | 75.216 | 58.9523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.4252 | 84.4459
CID=288429471 | 9 | 52.5 | 36.2376 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 29246.1052 | 0.85533 | 0.021818 | 3.0567 | 36.2376 | 110.7677 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 66.2115 | 3.5652 | 0.84843 | 54.2826 | 64.8935 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.2376 | 90.1325
CID=288429758 | 9 | 55 | 40.4435 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 29712.645 | 0.91684 | 0.024324 | 2.852 | 40.4435 | 115.3436 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 68.8158 | 3.794 | 0.86027 | 59.3724 | 71.4284 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.4435 | 90.1325
CID=288429789 | 9 | 57.5 | 45.1717 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 30430.608 | 0.9759 | 0.027231 | 2.6373 | 45.1717 | 119.1331 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 71.7642 | 4.0336 | 0.87126 | 61.8259 | 78.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.1717 | 90.1326
CID=288429564 | 9 | 60 | 49.2777 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 31053.1804 | 1.033 | 0.03004 | 2.4802 | 49.2777 | 122.2168 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 74.1134 | 4.2845 | 0.87915 | 64.6028 | 85.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.2777 | 90.1326
CID=288429595 | 9 | 62.5 | 55.0994 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 31471.6371 | 1.0871 | 0.033884 | 2.2592 | 55.0994 | 124.4798 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 77.6789 | 4.5468 | 0.88819 | 85.2522 | 94.253 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.0994 | 90.1325
CID=288429386 | 9 | 65 | 61.5516 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 31957.1429 | 1.1714 | 0.038328 | 2.1062 | 61.5517 | 129.6423 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 80.3921 | 4.8211 | 0.8959 | 98.6211 | 104.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.5516 | 90.1325
CID=288429417 | 9 | 67.5 | 67.8089 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 32658.3848 | 1.2536 | 0.043007 | 1.9742 | 67.8089 | 133.8671 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 82.8761 | 5.1077 | 0.90159 | 88.6685 | 114.271 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.8089 | 90.1325
CID=643368339 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368370 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368145 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368176 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368463 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368494 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368269 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368300 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368091 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643368122 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327291784 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327291753 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327291978 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327291947 | 12 | 25 | 7.9035 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 18438.9763 | 0.53063 | 0.0077172 | 11.4415 | 7.9035 | 90.4283 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 32.7223 | 1.5117 | 0.67796 | 53.0966 | 17.7122 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0818 | 7.9035 | 14.4449
CID=-1327291660 | 12 | 27.5 | 7.806 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 18284.3624 | 0.43382 | 0.0078523 | 9.281 | 7.806 | 72.4476 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 36.046 | 1.6293 | 0.67695 | 42.5649 | 17.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2314 | 7.806 | 21.8594
CID=-1327291629 | 12 | 30 | 9.6007 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 19608.8265 | 0.46312 | 0.0084889 | 7.8897 | 9.6007 | 75.747 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 39.6085 | 1.7537 | 0.695 | 26.2624 | 20.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6007 | 26.8405
CID=-1327291854 | 12 | 32.5 | 11.4509 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 20431.4528 | 0.49865 | 0.0092275 | 6.9718 | 11.4509 | 79.8337 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 42.6839 | 1.8852 | 0.7122 | 53.8615 | 24.4281 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.4509 | 32.3474
CID=-1327291823 | 12 | 35 | 13.2216 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 21659.5756 | 0.53415 | 0.010005 | 6.3272 | 13.2216 | 83.6563 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 45.3279 | 2.0239 | 0.72744 | 39.208 | 27.6149 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.2216 | 38.3861
CID=-1327292032 | 12 | 37.5 | 15.1077 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 22429.8735 | 0.56956 | 0.010877 | 5.7721 | 15.1078 | 87.2041 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 47.9471 | 2.1702 | 0.74244 | 58.9118 | 30.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.1077 | 43.1811
CID=-1327292001 | 12 | 40 | 17.6528 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 23555.819 | 0.61016 | 0.012041 | 5.1701 | 17.6528 | 91.2663 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 51.1327 | 2.3243 | 0.76085 | 51.2498 | 35.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.6528 | 50.1588
CID=513177289 | 12 | 42.5 | 20.6832 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 24321.719 | 0.67581 | 0.013459 | 4.7712 | 20.6832 | 98.683 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 53.7166 | 2.4864 | 0.78029 | 63.1845 | 40.2733 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.6832 | 57.8258
CID=513177320 | 12 | 45 | 23.3728 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 25140.7489 | 0.71071 | 0.014831 | 4.3313 | 23.3728 | 101.2346 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 56.7549 | 2.6569 | 0.79555 | 78.4721 | 44.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.3728 | 65.6764
CID=513177095 | 12 | 47.5 | 26.1625 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 25958.2587 | 0.7455 | 0.016323 | 3.956 | 26.1625 | 103.4992 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 59.7255 | 2.836 | 0.80962 | 85.3977 | 49.097 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.1625 | 73.9419
CID=513177126 | 12 | 50 | 29.7952 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 26941.9598 | 0.81043 | 0.018249 | 3.6773 | 29.7952 | 109.5661 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 62.2903 | 3.0241 | 0.82558 | 66.622 | 54.8331 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.7952 | 79.5389
CID=513177413 | 12 | 52.5 | 33.0954 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 27766.3824 | 0.8505 | 0.020152 | 3.3801 | 33.0954 | 111.8653 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 65.2183 | 3.2213 | 0.83807 | 61.5464 | 59.9988 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.0954 | 87.9361
CID=513177444 | 12 | 55 | 37.3247 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 28728.6575 | 0.91368 | 0.022577 | 3.1292 | 37.3247 | 116.7959 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 68.0024 | 3.428 | 0.8517 | 70.3095 | 66.5837 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 37.3247 | 90.1325
CID=513177219 | 12 | 57.5 | 41.1087 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 29354.7935 | 0.95453 | 0.024957 | 2.8816 | 41.1087 | 118.457 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 70.9858 | 3.6445 | 0.86195 | 57.0591 | 72.4613 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.1087 | 90.1325
CID=513177250 | 12 | 60 | 45.939 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 29927.5122 | 1.0241 | 0.027982 | 2.6825 | 45.939 | 123.2301 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 73.662 | 3.8712 | 0.87284 | 60.2012 | 79.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.939 | 90.1325
CID=513177041 | 12 | 62.5 | 50.8496 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 30585.7181 | 1.0933 | 0.031253 | 2.5056 | 50.8496 | 127.4111 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 76.2317 | 4.1083 | 0.88182 | 64.1525 | 87.6123 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50.8496 | 90.1325
CID=513177072 | 12 | 65 | 55.6734 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 31177.5767 | 1.1622 | 0.034715 | 2.3525 | 55.6734 | 130.9713 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 78.6196 | 4.3561 | 0.88897 | 64.6088 | 95.1518 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.6734 | 90.1325
CID=320379054 | 12 | 67.5 | 62.1983 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 31505.398 | 1.2172 | 0.039315 | 2.1294 | 62.1984 | 132.4468 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 82.3488 | 4.615 | 0.89656 | 85.2525 | 105.4035 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 62.1983 | 90.1326
CID=320379085 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320378860 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320378891 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320379178 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320379209 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320378984 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320379015 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320378806 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320378837 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675317759 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675317790 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675317565 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675317596 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675317883 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675317914 | 15 | 27.5 | 8.5925 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18438.7117 | 0.6276 | 0.0079495 | 12.3447 | 8.5925 | 106.0713 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 34.7451 | 1.4757 | 0.68503 | 59.7235 | 19.0575 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=675317689 | 15 | 30 | 8.6958 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 18295.1538 | 0.52337 | 0.0081414 | 9.9652 | 8.6958 | 86.6555 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 38.0313 | 1.5883 | 0.68607 | 48.9268 | 19.2574 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2146 | 8.6958 | 22.1642
CID=675317720 | 15 | 32.5 | 9.9438 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 19080.8101 | 0.50979 | 0.0086633 | 8.311 | 9.9438 | 82.6425 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 41.541 | 1.7074 | 0.69829 | 35.2544 | 21.6357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.9438 | 27.4707
CID=675317511 | 15 | 35 | 11.8586 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 20271.1702 | 0.53653 | 0.0094414 | 7.1768 | 11.8586 | 85.1071 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 44.9077 | 1.833 | 0.71581 | 23.1824 | 25.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.8586 | 33.1342
CID=675317542 | 15 | 37.5 | 13.9017 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 21130.1154 | 0.58789 | 0.010329 | 6.5599 | 13.9017 | 91.1933 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 47.3782 | 1.9655 | 0.73299 | 51.5162 | 28.8155 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.9017 | 39.38
CID=-1295342364 | 15 | 40 | 15.8898 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 22255.4641 | 0.62684 | 0.01126 | 5.9801 | 15.8898 | 95.0222 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 49.9468 | 2.1051 | 0.74831 | 41.3607 | 32.2621 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.8898 | 45.3962
CID=-1295342333 | 15 | 42.5 | 18.2373 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 22992.6638 | 0.6656 | 0.01238 | 5.4028 | 18.2373 | 98.5314 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 52.8184 | 2.2519 | 0.7648 | 60.1017 | 36.2301 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.2373 | 51.5431
CID=-1295342558 | 15 | 45 | 21.0094 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 24106.3414 | 0.70414 | 0.013729 | 4.8413 | 21.0094 | 101.7136 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 56.0177 | 2.4063 | 0.78224 | 47.7889 | 40.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.0094 | 59.4744
CID=-1295342527 | 15 | 47.5 | 23.7775 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 24684.202 | 0.74611 | 0.015157 | 4.4195 | 23.7775 | 105.0839 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 58.8682 | 2.5686 | 0.7977 | 66.5078 | 45.2882 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.7775 | 67.6857
CID=-1295342240 | 15 | 50 | 27.453 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 25541.9883 | 0.82047 | 0.017036 | 4.1006 | 27.453 | 112.5738 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 61.3957 | 2.7389 | 0.81558 | 90.1004 | 51.1424 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.453 | 76.5318
CID=-1295342209 | 15 | 52.5 | 30.551 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 26328.2048 | 0.8586 | 0.018789 | 3.753 | 30.551 | 114.6571 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 64.3185 | 2.9175 | 0.8286 | 73.266 | 56.0192 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.551 | 82.4122
CID=-1295342434 | 15 | 55 | 33.9713 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 27361.354 | 0.90285 | 0.020789 | 3.4508 | 33.9714 | 117.2275 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 67.1867 | 3.1047 | 0.8411 | 54.6982 | 61.365 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.9713 | 90.1325
CID=-1295342403 | 15 | 57.5 | 38.3346 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 27884.6803 | 0.9737 | 0.023332 | 3.2032 | 38.3346 | 122.7947 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 69.8431 | 3.3008 | 0.8546 | 82.9597 | 68.153 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.3346 | 90.1325
CID=-1295342612 | 15 | 60 | 42.1963 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 29045.494 | 1.0111 | 0.025812 | 2.9316 | 42.1963 | 123.7045 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 72.9624 | 3.5061 | 0.8646 | 54.7832 | 74.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.1963 | 90.1325
CID=-1295342581 | 15 | 62.5 | 46.6943 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 29466.683 | 1.0747 | 0.028761 | 2.7284 | 46.6943 | 127.3986 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 75.5997 | 3.7208 | 0.87435 | 56.9188 | 81.1403 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.6943 | 90.1325
CID=545126709 | 15 | 65 | 51.93 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 30119.6715 | 1.1395 | 0.032278 | 2.5169 | 51.93 | 130.7044 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 78.5549 | 3.9453 | 0.88355 | 59.0954 | 89.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51.93 | 90.1325
CID=545126740 | 15 | 67.5 | 56.5173 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 30724.7061 | 1.2019 | 0.035727 | 2.3568 | 56.5173 | 133.2015 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 81.0057 | 4.1798 | 0.89007 | 62.6993 | 96.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.5173 | 90.1325
CID=545126515 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126546 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126833 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126864 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126639 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126670 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126461 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545126492 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328474 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328505 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328280 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328311 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328598 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328629 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328404 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328435 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352328226 | 18 | 32.5 | 9.4876 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 18410.3274 | 0.60404 | 0.0084291 | 10.448 | 9.4876 | 99.1255 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 40.3119 | 1.5499 | 0.6939 | 48.4714 | 20.7737 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.4876 | 22.9766
CID=352328257 | 18 | 35 | 9.6985 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 18503.5895 | 0.51873 | 0.0086724 | 8.5909 | 9.6986 | 83.3192 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 43.7008 | 1.664 | 0.69594 | 39.5045 | 21.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6985 | 28.0193
CID=481233238 | 18 | 37.5 | 11.8592 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 19926.8531 | 0.55919 | 0.0095324 | 7.4083 | 11.8592 | 87.8564 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 47.0436 | 1.7842 | 0.71582 | 26.1571 | 25.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.8592 | 33.8929
CID=481233079 | 18 | 40 | 13.906 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 20598.5909 | 0.60203 | 0.010434 | 6.6491 | 13.906 | 92.4626 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 49.8099 | 1.9109 | 0.73302 | 54.3636 | 28.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.906 | 40.396
CID=481233176 | 18 | 42.5 | 16.0656 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 21865.6924 | 0.65041 | 0.011439 | 6.0738 | 16.0656 | 97.5796 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 52.3263 | 2.0442 | 0.7496 | 33.781 | 32.5628 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.0656 | 47.4637
CID=481233273 | 18 | 45 | 18.496 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 22493.6979 | 0.70295 | 0.012609 | 5.5658 | 18.496 | 102.9444 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 54.8569 | 2.1844 | 0.76651 | 61.261 | 36.6619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.496 | 52.9123
CID=481233114 | 18 | 47.5 | 21.5596 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 23633.7919 | 0.75236 | 0.014094 | 4.9846 | 21.5596 | 107.4658 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 58.0061 | 2.3317 | 0.78546 | 51.2497 | 41.7037 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.5596 | 60.9897
CID=481232955 | 18 | 50 | 24.7665 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 24288.2445 | 0.81548 | 0.015727 | 4.5834 | 24.7665 | 113.5158 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 60.6367 | 2.4862 | 0.80279 | 63.7562 | 46.8726 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.7665 | 69.7483
CID=481233052 | 18 | 52.5 | 27.8781 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 25078.3679 | 0.85753 | 0.01742 | 4.1691 | 27.8781 | 116.2255 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 63.5956 | 2.6484 | 0.81747 | 78.6093 | 51.8143 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.8781 | 78.6886
CID=481233149 | 18 | 55 | 31.0948 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 25855.5742 | 0.89944 | 0.019261 | 3.8135 | 31.0948 | 118.5794 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 66.4922 | 2.8184 | 0.83071 | 86.9038 | 56.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.0948 | 88.1043
CID=481232990 | 18 | 57.5 | 35.0067 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 26759.6033 | 0.9645 | 0.02152 | 3.5296 | 35.0067 | 123.5588 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 69.1446 | 2.9964 | 0.84454 | 66.6222 | 62.978 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.0067 | 90.1325
CID=481232831 | 18 | 60 | 39.0194 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 27605.784 | 1.026 | 0.023971 | 3.2694 | 39.0194 | 127.5708 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 71.8118 | 3.1827 | 0.8565 | 58.1959 | 69.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.0194 | 90.1325
CID=288435003 | 18 | 62.5 | 43.2784 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 28353.0202 | 1.0746 | 0.0267 | 2.9929 | 43.2784 | 129.5263 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 74.8702 | 3.3776 | 0.86712 | 70.3102 | 75.831 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.2784 | 90.1325
CID=288434844 | 18 | 65 | 48.0659 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 29183.0854 | 1.1468 | 0.029873 | 2.7844 | 48.0659 | 133.8338 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 77.4817 | 3.5814 | 0.87696 | 54.2831 | 83.2746 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.0659 | 90.1326
CID=288434941 | 18 | 67.5 | 53.0188 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 29598.8271 | 1.2161 | 0.033358 | 2.5877 | 53.0189 | 137.1996 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 80.1385 | 3.7943 | 0.88522 | 59.3724 | 90.999 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.0188 | 90.1325
CID=288435038 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288434879 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288434720 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288434817 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288434914 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288434755 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288434596 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373708 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373549 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373646 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373743 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373584 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373425 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373522 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373619 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373460 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643373301 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327286415 | 21 | 35 | 9.9152 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 18283.7083 | 0.68557 | 0.008629 | 11.2426 | 9.9152 | 111.4732 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 42.2265 | 1.5138 | 0.69802 | 52.4002 | 21.582 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2186 | 9.9152 | 20.974
CID=-1327286574 | 21 | 37.5 | 9.8342 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 18170.506 | 0.56856 | 0.0087954 | 9.1978 | 9.8343 | 90.4539 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 45.4661 | 1.6232 | 0.69724 | 42.5581 | 21.4295 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2629 | 9.8342 | 28.5245
CID=-1327286477 | 21 | 40 | 12.2151 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 19480.3936 | 0.6128 | 0.0097428 | 7.8042 | 12.2151 | 95.3285 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 48.9262 | 1.7385 | 0.71892 | 25.7842 | 25.815 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.2151 | 34.6277
CID=-1327286380 | 21 | 42.5 | 14.5417 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 20305.008 | 0.65967 | 0.01076 | 6.8956 | 14.5417 | 100.2743 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 51.8983 | 1.8598 | 0.73806 | 48.6305 | 29.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.5417 | 41.3248
CID=-1327286539 | 21 | 45 | 16.752 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 21347.5538 | 0.70651 | 0.011809 | 6.2598 | 16.752 | 104.8637 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 54.4747 | 1.9873 | 0.75456 | 44.326 | 33.731 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.752 | 48.6019
CID=-1327286698 | 21 | 47.5 | 19.0805 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 22241.4036 | 0.75324 | 0.01297 | 5.7169 | 19.0806 | 109.0812 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 57.0148 | 2.1213 | 0.77032 | 49.0224 | 37.6334 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.0805 | 54.2307
CID=-1327286601 | 21 | 50 | 21.9077 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 23074.2195 | 0.7997 | 0.014395 | 5.1535 | 21.9077 | 112.9013 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 59.9341 | 2.2619 | 0.78746 | 57.0431 | 42.2694 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.9077 | 62.5046
CID=-1327286504 | 21 | 52.5 | 25.2501 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 24057.2769 | 0.85619 | 0.016114 | 4.6628 | 25.2501 | 117.7368 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 62.8928 | 2.4094 | 0.8052 | 47.5993 | 47.6447 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.2501 | 71.6014
CID=-1327286663 | 21 | 55 | 28.3799 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 24628.9639 | 0.90177 | 0.017851 | 4.2519 | 28.3799 | 120.6696 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 65.7437 | 2.564 | 0.81966 | 66.5078 | 52.606 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.3799 | 80.9026
CID=-1327286822 | 21 | 57.5 | 32.5224 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 25438.511 | 0.98552 | 0.02013 | 3.9419 | 32.5225 | 128.2004 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 68.2736 | 2.726 | 0.83603 | 89.8911 | 59.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.5224 | 90.1325
CID=513182658 | 21 | 60 | 36.0509 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 26161.3449 | 1.0308 | 0.022285 | 3.6119 | 36.0509 | 130.213 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 71.1317 | 2.8955 | 0.84785 | 82.8129 | 64.603 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.0509 | 90.1326
CID=513182499 | 21 | 62.5 | 39.8051 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 27148.1727 | 1.0767 | 0.024686 | 3.3141 | 39.8051 | 131.9197 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 74.0142 | 3.0728 | 0.85861 | 56.4278 | 70.437 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.8051 | 90.1326
CID=513182596 | 21 | 65 | 44.3855 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 27711.6615 | 1.1471 | 0.02764 | 3.067 | 44.3855 | 136.1299 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 76.7145 | 3.2582 | 0.86958 | 62.5657 | 77.5509 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44.3855 | 90.1326
CID=513182693 | 21 | 67.5 | 49.2427 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 28740.7969 | 1.2141 | 0.030942 | 2.8305 | 49.2427 | 139.3816 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 79.5229 | 3.4519 | 0.87908 | 58.028 | 85.1074 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.2427 | 90.1326
CID=513182534 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513182375 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513182472 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513182569 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513182410 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513182251 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384423 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384264 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384361 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384458 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384299 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384140 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384237 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384334 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384175 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320384016 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675323128 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675322969 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675323066 | 24 | 37.5 | 10.7318 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18282.5476 | 0.80286 | 0.0089538 | 12.0485 | 10.7318 | 129.3013 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 44.2999 | 1.4799 | 0.70568 | 58.8856 | 23.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=675323163 | 24 | 40 | 10.888 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 18140.5036 | 0.67738 | 0.0092027 | 9.7999 | 10.888 | 106.7018 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 47.5115 | 1.5849 | 0.70711 | 48.847 | 23.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2758 | 10.888 | 28.8692
CID=675323004 | 24 | 42.5 | 12.5977 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 18962.2998 | 0.67012 | 0.0099699 | 8.19 | 12.5977 | 103.175 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 50.9301 | 1.6955 | 0.7222 | 35.4012 | 26.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.5977 | 35.3309
CID=675322845 | 24 | 45 | 14.8492 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 20113.684 | 0.69351 | 0.010984 | 7.0235 | 14.8492 | 104.2927 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 54.2986 | 1.8118 | 0.74045 | 23.1822 | 30.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.8492 | 42.1901
CID=675322942 | 24 | 47.5 | 17.2586 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 20827.2683 | 0.75503 | 0.012127 | 6.4211 | 17.2587 | 110.8203 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 56.7236 | 1.9339 | 0.75813 | 54.3168 | 34.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.2586 | 49.7239
CID=675323039 | 24 | 50 | 19.8019 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 22004.2708 | 0.81306 | 0.013395 | 5.8772 | 19.8019 | 116.3806 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 59.1913 | 2.0621 | 0.77489 | 33.7811 | 38.8258 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.8019 | 57.9119
CID=675322880 | 24 | 52.5 | 22.5727 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 22548.5033 | 0.86758 | 0.014832 | 5.3606 | 22.5727 | 121.0024 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 61.8035 | 2.1966 | 0.79119 | 61.2613 | 43.3469 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.5727 | 64.0509
CID=675322721 | 24 | 55 | 26.0461 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 23667.8908 | 0.91839 | 0.016643 | 4.7874 | 26.0461 | 124.6932 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 64.9756 | 2.3376 | 0.80906 | 51.2497 | 48.9121 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.0461 | 73.2965
CID=-1295336995 | 24 | 57.5 | 29.3599 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 24216.1151 | 0.97547 | 0.018502 | 4.3871 | 29.36 | 128.8047 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 67.6637 | 2.4852 | 0.8238 | 64.3204 | 54.1491 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.3599 | 83.1958
CID=-1295337154 | 24 | 60 | 32.9235 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 24979.2916 | 1.0257 | 0.020588 | 3.9964 | 32.9235 | 131.5753 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 70.5641 | 2.6398 | 0.83746 | 78.7903 | 59.7305 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.9235 | 90.1325
CID=-1295337057 | 24 | 62.5 | 36.5949 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 25717.4626 | 1.0757 | 0.022858 | 3.6591 | 36.5949 | 133.9054 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 73.4072 | 2.8015 | 0.84952 | 88.1696 | 65.4491 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.5949 | 90.1326
CID=-1295336960 | 24 | 65 | 40.7589 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 26548.0421 | 1.1395 | 0.025512 | 3.3725 | 40.7589 | 137.4611 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 76.1393 | 2.9705 | 0.86107 | 66.6223 | 71.9181 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.7589 | 90.1326
CID=-1295337119 | 24 | 67.5 | 45.532 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 27407.4453 | 1.2249 | 0.028644 | 3.1411 | 45.532 | 143.0193 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 78.632 | 3.147 | 0.87201 | 54.6984 | 79.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.532 | 90.1326
CID=-1295337278 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295337181 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295337084 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295337243 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295337402 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545132078 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131919 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545132016 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545132113 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131954 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131795 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131892 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131989 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131830 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545131671 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352333843 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352333684 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352333781 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352333878 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352333719 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352333560 | 27 | 42.5 | 12.0582 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 18278.244 | 0.78888 | 0.0096706 | 10.1996 | 12.0582 | 122.9895 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 49.877 | 1.5489 | 0.71756 | 49.1044 | 25.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.0582 | 29.3459
CID=352333657 | 27 | 45 | 12.2922 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 18408.1045 | 0.68218 | 0.0099756 | 8.4534 | 12.2923 | 103.9119 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 53.1501 | 1.6551 | 0.71959 | 39.5045 | 25.954 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.2922 | 35.9335
CID=352333754 | 27 | 47.5 | 14.8597 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 19737.04 | 0.7304 | 0.011111 | 7.3098 | 14.8597 | 108.6206 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 56.3304 | 1.7667 | 0.74054 | 26.866 | 30.4874 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.8597 | 43.0269
CID=352333595 | 27 | 50 | 17.4382 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 20365.3572 | 0.78621 | 0.012335 | 6.5409 | 17.4382 | 114.0616 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 59.0958 | 1.8839 | 0.75937 | 54.4568 | 34.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.4382 | 50.8249
CID=352333436 | 27 | 52.5 | 19.9821 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 21512.7123 | 0.84196 | 0.013628 | 5.9584 | 19.9821 | 119.062 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 61.628 | 2.0067 | 0.77601 | 37.5113 | 39.1226 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.9821 | 59.2263
CID=481230039 | 27 | 55 | 22.6823 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 22186.5381 | 0.89756 | 0.015065 | 5.4494 | 22.6823 | 123.6058 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 64.1599 | 2.1355 | 0.7918 | 56.4602 | 43.524 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.6823 | 65.5153
CID=481230070 | 27 | 57.5 | 26.0535 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 23111.4414 | 0.9528 | 0.016869 | 4.8998 | 26.0535 | 127.6579 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 67.1359 | 2.2704 | 0.8091 | 54.0901 | 48.9239 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.0535 | 74.9452
CID=481229977 | 27 | 60 | 30.1043 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 23958.3748 | 1.0356 | 0.019079 | 4.4795 | 30.1044 | 134.8517 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 69.8613 | 2.4116 | 0.82683 | 47.5994 | 55.3185 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.1043 | 85.2525
CID=481230008 | 27 | 62.5 | 33.5524 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 24536.1575 | 1.0813 | 0.021168 | 4.0739 | 33.5525 | 136.6885 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 72.7507 | 2.5593 | 0.83967 | 66.5078 | 60.7119 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.5524 | 90.1325
CID=481229915 | 27 | 65 | 38.1555 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 25299.4125 | 1.1739 | 0.023923 | 3.7712 | 38.1555 | 143.8921 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 75.3047 | 2.7136 | 0.85409 | 89.774 | 67.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.1555 | 90.1326
CID=481229946 | 27 | 67.5 | 41.9411 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 25976.6278 | 1.2178 | 0.026485 | 3.4466 | 41.9411 | 144.554 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 78.1928 | 2.875 | 0.86399 | 82.825 | 73.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.9411 | 90.1326
CID=481229853 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481229884 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481229791 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481229822 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431804 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431835 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431742 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431773 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431680 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431711 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431618 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431649 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431556 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288431587 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370509 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370540 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370447 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370478 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370385 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370416 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370323 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643370354 | 30 | 45 | 12.2153 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 18042.4644 | 0.8677 | 0.0098264 | 10.9562 | 12.2153 | 133.8338 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 51.7948 | 1.515 | 0.71892 | 52.129 | 25.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3242 | 12.2153 | 30.0035
CID=643370261 | 30 | 47.5 | 12.6305 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 18225.4888 | 0.73469 | 0.010202 | 8.7619 | 12.6305 | 110.6677 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 55.4076 | 1.6171 | 0.72248 | 36.7154 | 26.5614 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.6305 | 36.4854
CID=643370292 | 30 | 50 | 15.2979 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 19306.2629 | 0.79557 | 0.011398 | 7.6445 | 15.2979 | 116.9444 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 58.3691 | 1.7244 | 0.74389 | 25.6495 | 31.2451 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.2979 | 43.826
CID=-1327289614 | 30 | 52.5 | 18.16 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 20114.1471 | 0.85629 | 0.012757 | 6.7582 | 18.16 | 122.7296 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 61.275 | 1.8368 | 0.76428 | 45.0637 | 36.1011 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.16 | 51.8244
CID=-1327289583 | 30 | 55 | 20.8596 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 21010.4719 | 0.91697 | 0.014144 | 6.138 | 20.8596 | 128.037 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 63.8215 | 1.9547 | 0.78135 | 48.2097 | 40.5619 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.8596 | 60.4554
CID=-1327289676 | 30 | 57.5 | 23.677 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 21988.4377 | 0.97752 | 0.015668 | 5.6107 | 23.677 | 132.845 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 66.3278 | 2.0782 | 0.79717 | 41.3219 | 45.1267 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.677 | 68.5376
CID=-1327289645 | 30 | 60 | 26.9058 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 22585.0689 | 1.0378 | 0.017461 | 5.0967 | 26.9058 | 137.1298 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 69.0347 | 2.2074 | 0.81309 | 62.5903 | 50.2763 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.9058 | 76.6398
CID=-1327289738 | 30 | 62.5 | 30.8512 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 23631.6353 | 1.0977 | 0.019682 | 4.566 | 30.8512 | 140.8659 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 72.1238 | 2.3426 | 0.82977 | 49.9551 | 56.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.8512 | 87.1331
CID=-1327289707 | 30 | 65 | 34.4695 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 24106.5349 | 1.1575 | 0.021905 | 4.1806 | 34.4695 | 144.1024 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 74.8257 | 2.4839 | 0.84277 | 64.8839 | 62.1414 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.4695 | 90.1325
CID=-1327289800 | 30 | 67.5 | 38.5113 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 24843.5555 | 1.217 | 0.024477 | 3.8115 | 38.5113 | 146.7878 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 77.6853 | 2.6315 | 0.85509 | 79.0619 | 68.4275 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.5113 | 90.1325
CID=-1327289769 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327289862 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327289831 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179459 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179490 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179397 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179428 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179335 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179366 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179273 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179304 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179211 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513179242 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381224 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381255 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381162 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381193 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381100 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381131 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381038 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381069 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320380976 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320381007 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319929 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319960 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319867 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319898 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319805 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319836 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319743 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319774 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319681 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675319712 | -15 | -5 | 3.9471 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18380.2462 | 0.22923 | 0.0068733 | 11.0433 | 3.9471 | 43.5892 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 3.8238 | 1.4946 | 0.63308 | 70.2252 | 9.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=-1295340194 | -15 | -2.5 | 5.0306 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 18829.9892 | 0.27063 | 0.0066312 | 10.1259 | 5.0306 | 50.9395 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 7.1053 | 1.6437 | 0.64614 | 110 | 11.8291 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3.8092 | 8.6947
CID=-1295340163 | -15 | 0 | 6.0812 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 20218.6796 | 0.30032 | 0.006794 | 9.1358 | 6.0812 | 55.557 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 9.9373 | 1.804 | 0.65823 | 110 | 14.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.4307 | 11.0329
CID=-1295340256 | -15 | 2.5 | 7.3913 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 21597.7062 | 0.3337 | 0.0071293 | 8.2055 | 7.3913 | 60.6491 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 12.8908 | 1.9762 | 0.67257 | 110 | 16.6969 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.2867 | 13.7049
CID=-1295340225 | -15 | 5 | 8.6856 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 22802.0017 | 0.36283 | 0.0075498 | 7.4562 | 8.6856 | 64.7615 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 15.5699 | 2.1607 | 0.68597 | 110 | 19.2377 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1823 | 16.1956
CID=-1295340318 | -15 | 7.5 | 10.2662 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 23989.4647 | 0.3988 | 0.0081024 | 6.8062 | 10.2662 | 69.8743 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 18.2552 | 2.3583 | 0.70134 | 110 | 22.24 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2299 | 19.3754
CID=-1295340287 | -15 | 10 | 12.2026 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 25209.0134 | 0.4401 | 0.008812 | 6.2005 | 12.2026 | 75.6616 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 21.0937 | 2.5693 | 0.71881 | 110 | 25.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5747 | 23.0861
CID=-1295340380 | -15 | 12.5 | 14.3375 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 26349.5855 | 0.48304 | 0.0096372 | 5.6807 | 14.3375 | 81.4473 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 23.8575 | 2.7945 | 0.73646 | 110 | 29.5787 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0921 | 27.0734
CID=-1295340349 | -15 | 15 | 16.2001 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 27266.8225 | 0.5131 | 0.010426 | 5.2351 | 16.2001 | 84.8092 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 26.472 | 3.0345 | 0.75059 | 110 | 32.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.5676 | 30.0979
CID=-1295340442 | -15 | 17.5 | 18.5873 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 28227.5446 | 0.55472 | 0.011433 | 4.8331 | 18.5873 | 89.834 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 29.1555 | 3.2899 | 0.76711 | 110 | 36.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.3575 | 34.2767
CID=-1295340411 | -15 | 20 | 21.0649 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 29134.8893 | 0.59274 | 0.012524 | 4.4624 | 21.0649 | 94.0005 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 31.9001 | 3.5612 | 0.78256 | 110 | 40.8973 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3391 | 38.2422
CID=545128879 | -15 | 22.5 | 23.2336 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 29901.6279 | 0.61628 | 0.013562 | 4.1169 | 23.2336 | 95.6509 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 34.7172 | 3.8493 | 0.7948 | 110 | 44.4133 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6718 | 39.9189
CID=545128910 | -15 | 25 | 24.9888 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 30564.1437 | 0.62816 | 0.014502 | 3.8161 | 24.9888 | 95.3599 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 37.4245 | 4.1546 | 0.8039 | 109.8133 | 47.2277 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8667 | 19.9411 | 40.1319
CID=545128817 | -15 | 27.5 | 27.2193 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 31281.1654 | 0.65152 | 0.015665 | 3.5518 | 27.2193 | 96.6784 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 40.0829 | 4.4779 | 0.81452 | 109.4768 | 50.7727 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3524 | 22.9327 | 40.079
CID=545128848 | -15 | 30 | 29.9309 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 32048.9088 | 0.6806 | 0.017073 | 3.296 | 29.9309 | 98.6528 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 42.9363 | 4.8198 | 0.82613 | 109.1206 | 55.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.5427 | 40.0954
CID=545128755 | -15 | 32.5 | 32.7 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 32764.8099 | 0.70779 | 0.018578 | 3.0625 | 32.7 | 100.1434 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 45.8014 | 5.1811 | 0.83667 | 108.5976 | 59.3814 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.1228 | 40.4314
CID=545128786 | -15 | 35 | 36.7603 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33589.2282 | 0.60011 | 0.020316 | 2.3103 | 35.8474 | 82.8181 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 58.2873 | 5.5624 | 0.84722 | 95.8907 | 64.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.7098 | 39.9119
CID=545128693 | -15 | 37.5 | 39.8194 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545128724 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545128631 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545128662 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330644 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330675 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330582 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330613 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330520 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330551 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330458 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330489 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330396 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352330427 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481235416 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481235257 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=481235222 | -12 | 0 | 5.3665 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 18591.7333 | 0.30652 | 0.0066669 | 10.6863 | 5.3665 | 57.3484 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 9.4251 | 1.5931 | 0.65006 | 110 | 12.5427 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.1993 | 8.8682
CID=481235319 | -12 | 2.5 | 6.3196 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 19804.7468 | 0.32768 | 0.0068662 | 9.5327 | 6.3196 | 60.2425 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 12.1487 | 1.7452 | 0.6609 | 110 | 14.528 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.6238 | 11.4069
CID=481235292 | -12 | 5 | 7.6624 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 21155.7337 | 0.36406 | 0.0072308 | 8.5802 | 7.6624 | 65.7446 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 14.918 | 1.9081 | 0.67544 | 110 | 17.2358 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4802 | 14.2089
CID=481235133 | -12 | 7.5 | 9.1053 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 22386.4326 | 0.39711 | 0.0077037 | 7.7332 | 9.1053 | 70.4129 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 17.6842 | 2.0826 | 0.69015 | 110 | 20.0449 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.3445 | 17.3877
CID=481235098 | -12 | 10 | 10.7102 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 23540.8968 | 0.43321 | 0.0082805 | 7.0389 | 10.7102 | 75.3883 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 20.323 | 2.269 | 0.70548 | 110 | 23.0658 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5663 | 20.1421
CID=481235195 | -12 | 12.5 | 12.715 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 24737.8273 | 0.47781 | 0.0090269 | 6.4151 | 12.715 | 81.5685 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 23.0538 | 2.4678 | 0.7232 | 110 | 26.7125 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9351 | 24.0547
CID=481235168 | -12 | 15 | 14.8706 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 25854.46 | 0.52108 | 0.0098749 | 5.8655 | 14.8707 | 87.2232 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 25.7736 | 2.6798 | 0.74062 | 110 | 30.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.4239 | 28.2107
CID=481235009 | -12 | 17.5 | 17.0301 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 26829.7142 | 0.55959 | 0.010776 | 5.3904 | 17.0301 | 91.7989 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 28.4181 | 2.9053 | 0.75653 | 110 | 34.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.959 | 32.2434
CID=288437181 | -12 | 20 | 19.3564 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 27743.2558 | 0.5993 | 0.011782 | 4.9751 | 19.3564 | 96.299 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 31.0224 | 3.1449 | 0.77209 | 110 | 38.0902 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.8048 | 36.0111
CID=288437022 | -12 | 22.5 | 22.0266 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 28660.2222 | 0.64247 | 0.01296 | 4.5883 | 22.0266 | 101.0652 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 33.7383 | 3.3993 | 0.78813 | 110 | 42.4623 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8745 | 40.4827
CID=288436987 | -12 | 25 | 24.7739 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 29508.5316 | 0.68347 | 0.014227 | 4.246 | 24.7739 | 105.1911 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 36.4169 | 3.6689 | 0.80282 | 110 | 46.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0705 | 44.884
CID=288437084 | -12 | 27.5 | 26.9065 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 30197.9486 | 0.70095 | 0.015332 | 3.9204 | 26.9065 | 105.4852 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 39.2043 | 3.9544 | 0.81309 | 110 | 50.2775 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8318 | 45.1309
CID=288437057 | -12 | 30 | 28.7972 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 30825.5772 | 0.71295 | 0.016402 | 3.6406 | 28.7972 | 104.8384 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 41.8593 | 4.2564 | 0.82144 | 109.0298 | 53.2635 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.4146 | 44.9448
CID=288436898 | -12 | 32.5 | 31.5308 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 31561.0993 | 0.7439 | 0.017854 | 3.3876 | 31.5308 | 106.814 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 44.5423 | 4.5754 | 0.83237 | 109.5574 | 57.5538 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9306 | 27.064 | 44.9312
CID=288436863 | -12 | 35 | 34.4431 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 32281.6496 | 0.77366 | 0.019453 | 3.147 | 34.4431 | 108.3922 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 47.3469 | 4.9121 | 0.84268 | 109.0577 | 62.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.8778 | 45.1391
CID=288436960 | -12 | 37.5 | 37.6645 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 32983.1733 | 0.80682 | 0.021267 | 2.9261 | 37.6645 | 110.2091 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 50.18 | 5.2671 | 0.85269 | 108.5522 | 67.1118 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.0704 | 45.4468
CID=288436933 | -12 | 40 | 42.3513 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 33790.8619 | 0.67548 | 0.023397 | 2.1712 | 41.3982 | 89.8843 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 63.413 | 5.6411 | 0.86267 | 95.3718 | 72.911 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.392 | 45.2292
CID=288436774 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375886 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375727 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375692 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375789 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375762 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375603 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375568 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375665 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375638 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643375479 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327284237 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327284396 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327284431 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327284334 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327284361 | -9 | 2.5 | 5.5152 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 18440.1156 | 0.33453 | 0.006713 | 11.2786 | 5.5152 | 62.2033 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 11.572 | 1.5462 | 0.65178 | 99.9314 | 12.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.3612 | 8.9771
CID=-1327284520 | -9 | 5 | 6.3729 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 19259.8333 | 0.34914 | 0.0069174 | 10.0083 | 6.3729 | 63.7819 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 14.1724 | 1.6906 | 0.6615 | 109.932 | 14.6374 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1701 | 4.5803 | 11.7505
CID=-1327284555 | -9 | 7.5 | 7.9008 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 20674.8964 | 0.39219 | 0.0073299 | 8.9056 | 7.9008 | 70.3617 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 17.0952 | 1.8452 | 0.67793 | 110 | 17.7068 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6398 | 14.6838
CID=-1327284458 | -9 | 10 | 9.5336 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 21971.7802 | 0.43381 | 0.0078662 | 8.0138 | 9.5336 | 76.4003 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 19.8339 | 2.0103 | 0.69435 | 110 | 20.861 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.707 | 18.0132
CID=-1327284485 | -9 | 12.5 | 11.002 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 23036.4243 | 0.46305 | 0.0084209 | 7.273 | 11.002 | 80.0178 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 22.4017 | 2.1865 | 0.70815 | 110 | 23.6047 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7039 | 20.8962
CID=-1327284644 | -9 | 15 | 13.1444 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 24234.0523 | 0.51398 | 0.0092223 | 6.6272 | 13.1444 | 87.111 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 25.0688 | 2.3743 | 0.7268 | 110 | 27.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2107 | 24.9456
CID=513184836 | -9 | 17.5 | 15.3875 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 25345.011 | 0.55939 | 0.010113 | 6.0398 | 15.3875 | 92.9371 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 27.7922 | 2.5741 | 0.74456 | 110 | 31.3995 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7125 | 29.4124
CID=513184677 | -9 | 20 | 17.9892 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 26429.8595 | 0.61162 | 0.011176 | 5.5344 | 17.9892 | 99.56 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 30.4815 | 2.7864 | 0.76313 | 110 | 35.8153 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5811 | 34.2136
CID=513184642 | -9 | 22.5 | 20.1545 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 27284.1895 | 0.64515 | 0.012149 | 5.1024 | 20.1545 | 102.837 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 33.0327 | 3.0118 | 0.77708 | 110 | 39.4061 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.2865 | 37.7584
CID=513184739 | -9 | 25 | 22.9538 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 28183.877 | 0.69375 | 0.013394 | 4.715 | 22.9538 | 108.2263 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 35.6308 | 3.2507 | 0.79329 | 110 | 43.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.365 | 42.7201
CID=513184712 | -9 | 27.5 | 25.9679 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 29065.428 | 0.74052 | 0.014782 | 4.3512 | 25.9679 | 112.9909 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 38.342 | 3.5036 | 0.80869 | 110 | 48.7877 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.8057 | 47.4545
CID=513184553 | -9 | 30 | 28.7206 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 29818.294 | 0.77498 | 0.016143 | 4.0244 | 28.7205 | 115.5828 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 41.0379 | 3.7712 | 0.82111 | 110 | 53.1428 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4049 | 50.6676
CID=513184518 | -9 | 32.5 | 31.1328 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 30492.4181 | 0.79753 | 0.017445 | 3.7319 | 31.1328 | 116.1856 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 43.701 | 4.0538 | 0.83086 | 110 | 56.9308 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.4891 | 51.064
CID=513184615 | -9 | 35 | 33.2139 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 31090.0652 | 0.81108 | 0.018686 | 3.4725 | 33.2139 | 115.3339 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 46.2982 | 4.3522 | 0.83849 | 109.7311 | 60.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7859 | 27.363 | 50.7666
CID=513184588 | -9 | 37.5 | 36.2101 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 31799.3574 | 0.84283 | 0.020361 | 3.2282 | 36.2101 | 116.8933 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 49.014 | 4.6667 | 0.84834 | 109.5704 | 64.8506 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.5427 | 50.2122
CID=513184429 | -9 | 40 | 39.4988 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 32493.7689 | 0.87744 | 0.02225 | 3.0025 | 39.4988 | 118.5963 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 51.771 | 4.9981 | 0.85779 | 108.6441 | 69.9614 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.6622 | 51.0088
CID=320386601 | -9 | 42.5 | 43.2078 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 33180.2667 | 0.91721 | 0.024425 | 2.7937 | 43.2078 | 120.7103 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 54.5685 | 5.3467 | 0.86696 | 108.546 | 75.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.6387 | 50.9152
CID=320386442 | -9 | 45 | 47.9355 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 33906.9765 | 0.9865 | 0.027174 | 2.6347 | 47.9355 | 126.2951 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.8841 | 5.7134 | 0.87672 | 108.8188 | 83.0716 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=320386407 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386504 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386477 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386318 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386283 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386380 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386353 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320386194 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675325306 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675325147 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675325112 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675325209 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675325182 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675325023 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675324988 | -6 | 5 | 5.1995 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18460.9125 | 0.33481 | 0.0067499 | 11.8977 | 5.1995 | 61.8626 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 13.4113 | 1.5026 | 0.64812 | 74.9461 | 12.1889 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=675325085 | -6 | 7.5 | 6.5993 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 18862.216 | 0.3807 | 0.0069965 | 10.47 | 6.5993 | 69.0947 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 16.3854 | 1.64 | 0.664 | 109.3422 | 15.1003 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7022 | 4.779 | 12.0604
CID=675325058 | -6 | 10 | 8.0831 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 20204.1341 | 0.42286 | 0.0074203 | 9.3227 | 8.0831 | 75.3556 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 19.1323 | 1.7868 | 0.67982 | 110 | 18.0649 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7257 | 15.1552
CID=675324899 | -6 | 12.5 | 9.7657 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 21470.2729 | 0.46449 | 0.0079824 | 8.3186 | 9.7657 | 81.2368 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 21.9228 | 1.9434 | 0.69659 | 110 | 21.3001 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8046 | 18.649
CID=-1295334817 | -6 | 15 | 11.7432 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 22721.7999 | 0.51402 | 0.0086954 | 7.5099 | 11.7432 | 88.19 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 24.6061 | 2.1103 | 0.7148 | 110 | 24.9608 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.1409 | 22.5502
CID=-1295334976 | -6 | 17.5 | 13.557 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 23747.8417 | 0.55123 | 0.0094177 | 6.8402 | 13.557 | 92.7327 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 27.134 | 2.2879 | 0.7302 | 110 | 28.2085 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4617 | 25.8429
CID=-1295335011 | -6 | 20 | 16.0696 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 24905.1927 | 0.60747 | 0.010411 | 6.2324 | 16.0696 | 100.1522 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 29.8092 | 2.4766 | 0.74963 | 110 | 32.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.2332 | 30.5791
CID=-1295334914 | -6 | 22.5 | 18.5991 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 25942.3537 | 0.65656 | 0.011469 | 5.7007 | 18.5991 | 106.0275 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 32.4559 | 2.6769 | 0.76719 | 110 | 36.8336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9502 | 35.5459
CID=-1295334941 | -6 | 25 | 21.1895 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 26866.2562 | 0.70302 | 0.012607 | 5.2451 | 21.1895 | 111.1408 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 35.0263 | 2.8892 | 0.7833 | 110 | 41.1006 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7519 | 40.5021
CID=-1295335100 | -6 | 27.5 | 23.884 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 27720.091 | 0.74824 | 0.01384 | 4.8455 | 23.884 | 115.7304 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 37.5591 | 3.1141 | 0.79825 | 110 | 45.4592 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9384 | 44.721
CID=-1295335135 | -6 | 30 | 27.1358 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 28606.4572 | 0.80248 | 0.01534 | 4.4723 | 27.1358 | 121.3602 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 40.2096 | 3.3519 | 0.81414 | 110 | 50.6406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.4722 | 50.1265
CID=-1295335038 | -6 | 32.5 | 30.426 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 29425.6553 | 0.85286 | 0.016933 | 4.1421 | 30.426 | 126.0266 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 42.8199 | 3.6031 | 0.82811 | 110 | 55.8231 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.148 | 55.2599
CID=-1295335065 | -6 | 35 | 32.9707 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 30078.4506 | 0.874 | 0.018322 | 3.8248 | 32.9707 | 126.1064 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 45.5628 | 3.8682 | 0.83763 | 110 | 59.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0822 | 56.636
CID=-1295335224 | -6 | 37.5 | 35.2842 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 30686.0627 | 0.8903 | 0.019693 | 3.5522 | 35.2842 | 125.3364 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 48.1791 | 4.1478 | 0.84543 | 109.8299 | 63.4101 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7005 | 28.0639 | 56.9451
CID=545134256 | -6 | 40 | 37.9759 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 31315.9718 | 0.91597 | 0.021292 | 3.3104 | 37.9759 | 125.7158 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 50.7442 | 4.4423 | 0.85358 | 109.6736 | 67.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9568 | 31.7052 | 56.788
CID=545134097 | -6 | 42.5 | 41.4559 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 32015.2893 | 0.95373 | 0.023312 | 3.0757 | 41.4559 | 127.5068 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 53.4849 | 4.7522 | 0.86281 | 109.3203 | 73.0005 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.4168 | 56.5732
CID=545134062 | -6 | 45 | 44.9076 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 32664.3617 | 0.98752 | 0.025436 | 2.8612 | 44.9076 | 128.4879 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 56.2256 | 5.0781 | 0.8707 | 108.6335 | 78.3623 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.914 | 56.8886
CID=545134159 | -6 | 47.5 | 49.4415 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 33360.9258 | 1.0419 | 0.028167 | 2.6659 | 49.4415 | 131.8061 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 58.964 | 5.4204 | 0.87943 | 108.5979 | 85.417 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.8283 | 57.2808
CID=545134132 | -6 | 50 | 54.1753 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34051.8889 | 0.88287 | 0.030801 | 2.0316 | 53.3935 | 108.4754 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 70.5466 | 5.7798 | 0.88577 | 95.3498 | 91.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=545133973 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545133938 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545134035 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545134008 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545133849 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352336021 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335862 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335827 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335924 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335897 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335738 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335703 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335800 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335773 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352335614 | -3 | 10 | 7.0739 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 18648.0611 | 0.4289 | 0.0071258 | 10.9307 | 7.0739 | 77.3233 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 18.7484 | 1.5929 | 0.66917 | 110 | 16.0612 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.3391 | 12.2784
CID=481232217 | -3 | 12.5 | 8.3887 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 19807.929 | 0.45838 | 0.0075429 | 9.6704 | 8.3888 | 81.1228 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 21.3921 | 1.7325 | 0.68296 | 110 | 18.662 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9798 | 15.6157
CID=481232248 | -3 | 15 | 10.1979 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 21083.2307 | 0.50631 | 0.0081566 | 8.6214 | 10.1979 | 87.9207 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 24.1151 | 1.8813 | 0.7007 | 110 | 22.1123 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.1813 | 19.2479
CID=481232023 | -3 | 17.5 | 12.0727 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 22243.2529 | 0.55058 | 0.008857 | 7.7669 | 12.0727 | 93.7678 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 26.723 | 2.0396 | 0.71769 | 110 | 25.558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3228 | 23.3226
CID=481232054 | -3 | 20 | 13.9096 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 23257.4991 | 0.58721 | 0.0095996 | 7.0479 | 13.9096 | 98.0335 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 29.2591 | 2.2079 | 0.73305 | 110 | 28.8294 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6291 | 26.7511
CID=481232093 | -3 | 22.5 | 16.6279 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 24427.2058 | 0.65247 | 0.010676 | 6.4183 | 16.6279 | 106.7233 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 31.8912 | 2.3864 | 0.75367 | 110 | 33.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.6237 | 31.6404
CID=481232124 | -3 | 25 | 19.1844 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 25439.9823 | 0.70164 | 0.011762 | 5.858 | 19.1844 | 112.3817 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 34.5225 | 2.5757 | 0.77099 | 110 | 37.8055 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2655 | 36.9411
CID=481231899 | -3 | 27.5 | 22.3085 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 26472.7212 | 0.76441 | 0.013105 | 5.3711 | 22.3085 | 119.8221 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 37.1536 | 2.7762 | 0.78972 | 110 | 42.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.5311 | 42.6405
CID=481231930 | -3 | 30 | 24.7967 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 27268.7662 | 0.80172 | 0.01429 | 4.9568 | 24.7967 | 122.9119 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 39.6493 | 2.9882 | 0.80294 | 110 | 46.9209 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4826 | 46.7387
CID=481231969 | -3 | 32.5 | 28.1723 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 28136.2987 | 0.86174 | 0.015864 | 4.5836 | 28.1723 | 129.1319 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 42.1956 | 3.2122 | 0.81876 | 110 | 52.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0462 | 52.5507
CID=481232000 | -3 | 35 | 31.7113 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 28970.8044 | 0.91719 | 0.017583 | 4.2334 | 31.7113 | 134.2462 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 44.843 | 3.4485 | 0.83305 | 110 | 57.8363 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9114 | 58.111
CID=288433982 | -3 | 37.5 | 35.0337 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 29700.3907 | 0.96285 | 0.019308 | 3.9263 | 35.0337 | 137.5531 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 47.4185 | 3.6978 | 0.84462 | 110 | 63.02 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.5999 | 63.3351
CID=288434013 | -3 | 40 | 37.7607 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 30323.7062 | 0.98538 | 0.020888 | 3.6358 | 37.7607 | 137.2919 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 50.0871 | 3.9603 | 0.85296 | 110 | 67.2612 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1961 | 63.4544
CID=288433788 | -3 | 42.5 | 40.0565 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 30879.9494 | 0.99744 | 0.022379 | 3.3809 | 40.0565 | 135.4264 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 52.6694 | 4.2366 | 0.85927 | 108.9171 | 70.8275 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5818 | 32.3922 | 63.0494
CID=288433819 | -3 | 45 | 43.3732 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 31529.6657 | 1.034 | 0.024387 | 3.1513 | 43.3732 | 136.681 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 55.2434 | 4.5271 | 0.86734 | 109.3326 | 75.9782 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.8219 | 63.027
CID=288433858 | -3 | 47.5 | 47.1865 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 32199.4875 | 1.0747 | 0.026729 | 2.9285 | 47.1865 | 138.1871 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 57.9725 | 4.8323 | 0.8753 | 109.1095 | 81.9059 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.7507 | 63.4939
CID=288433889 | -3 | 50 | 50.9273 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 32817.5788 | 1.1103 | 0.029183 | 2.724 | 50.9273 | 138.7278 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 60.7064 | 5.1527 | 0.88194 | 108.6414 | 87.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.6377 | 63.7961
CID=288433664 | -3 | 52.5 | 56.0712 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 33499.0187 | 1.1756 | 0.032441 | 2.5428 | 56.0712 | 142.5764 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 63.3604 | 5.4887 | 0.8895 | 108.6279 | 95.775 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.5574 | 63.6127
CID=288433695 | -3 | 55 | 60.4418 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34145.4634 | 0.99406 | 0.035397 | 1.9438 | 60.1317 | 116.8839 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 74.5757 | 5.841 | 0.89438 | 97.0873 | 102.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=288433734 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288433765 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372687 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372718 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372493 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372524 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372563 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372594 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372369 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372400 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372439 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643372470 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327287436 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1327287405 | 0 | 12.5 | 7.5495 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 18516.3195 | 0.48065 | 0.0072693 | 11.3994 | 7.5495 | 86.0596 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 21.1104 | 1.5491 | 0.67425 | 106.4161 | 17.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2421 | 5.6702 | 13.1874
CID=-1327287630 | 0 | 15 | 8.4201 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 19271.967 | 0.48468 | 0.0076042 | 10.115 | 8.4201 | 85.1694 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 23.4693 | 1.6821 | 0.68328 | 109.9537 | 18.723 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1157 | 5.883 | 16.0314
CID=-1327287599 | 0 | 17.5 | 10.4057 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 20590.1414 | 0.53988 | 0.0082742 | 8.9436 | 10.4057 | 93.0644 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 26.2694 | 1.8236 | 0.70265 | 110 | 22.5003 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2692 | 19.8154
CID=-1327287560 | 0 | 20 | 12.569 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 21827.1678 | 0.59512 | 0.0090733 | 8.0028 | 12.569 | 100.5876 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 28.9622 | 1.9741 | 0.72196 | 110 | 26.4512 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.7353 | 24.0702
CID=-1327287529 | 0 | 22.5 | 14.6146 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 22886.2577 | 0.64041 | 0.0098978 | 7.2583 | 14.6146 | 106.077 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 31.461 | 2.1337 | 0.73863 | 110 | 30.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1199 | 28.0987
CID=-1327287754 | 0 | 25 | 16.9739 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 23908.1067 | 0.69241 | 0.010877 | 6.6182 | 16.9739 | 112.3371 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 33.9579 | 2.303 | 0.75613 | 110 | 34.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7385 | 32.6801
CID=-1327287723 | 0 | 27.5 | 20.0627 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 25025.6749 | 0.76184 | 0.012162 | 6.031 | 20.0627 | 120.9977 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 36.5947 | 2.4822 | 0.77651 | 110 | 39.2552 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9765 | 38.3214
CID=-1327287684 | 0 | 30 | 22.9922 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 25991.2362 | 0.81702 | 0.013461 | 5.5215 | 22.9922 | 126.9511 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 39.1847 | 2.6717 | 0.79349 | 110 | 44.0242 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9309 | 44.1758
CID=-1327287653 | 0 | 32.5 | 26.0585 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 26867.1099 | 0.87253 | 0.014879 | 5.0868 | 26.0585 | 132.5555 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 41.6978 | 2.872 | 0.80912 | 110 | 48.9318 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0018 | 50.2286
CID=513181637 | 0 | 35 | 29.2257 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 27681.838 | 0.92532 | 0.016408 | 4.6997 | 29.2257 | 137.3531 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 44.2056 | 3.0833 | 0.82324 | 110 | 53.938 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6907 | 54.8307
CID=513181668 | 0 | 37.5 | 33.0345 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 28520.1275 | 0.99022 | 0.018265 | 4.3444 | 33.0345 | 143.5137 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 46.7817 | 3.3062 | 0.83786 | 110 | 59.9037 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6252 | 61.2623
CID=513181443 | 0 | 40 | 36.6471 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 29274.4388 | 1.0415 | 0.020143 | 4.0185 | 36.6471 | 147.2679 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 49.3933 | 3.5409 | 0.84968 | 110 | 65.5303 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4682 | 67.1838
CID=513181474 | 0 | 42.5 | 40.0544 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 29945.1405 | 1.0806 | 0.022042 | 3.719 | 40.0544 | 148.9611 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 52.0472 | 3.7879 | 0.85926 | 110 | 70.8242 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9202 | 70.4572
CID=513181513 | 0 | 45 | 43.097 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 30553.824 | 1.1087 | 0.023895 | 3.4541 | 43.097 | 148.8614 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 54.639 | 4.0477 | 0.86671 | 110 | 75.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7902 | 71.0175
CID=513181544 | 0 | 47.5 | 45.6428 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 31086.6509 | 1.1237 | 0.025645 | 3.2166 | 45.6428 | 146.8133 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 57.1856 | 4.3205 | 0.87223 | 109.5872 | 79.505 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0599 | 37.3283 | 70.5862
CID=513181319 | 0 | 50 | 49.395 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 31725.8486 | 1.1646 | 0.028032 | 2.9948 | 49.395 | 147.9292 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 59.8017 | 4.607 | 0.87935 | 109.6194 | 85.3447 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8941 | 42.4342 | 70.2774
CID=513181350 | 0 | 52.5 | 53.4157 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 32354.6013 | 1.206 | 0.03069 | 2.785 | 53.4157 | 148.7637 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 62.4995 | 4.9075 | 0.88581 | 109.1982 | 91.6191 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.5636 | 70.9719
CID=513181389 | 0 | 55 | 57.4429 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 32942.4873 | 1.2433 | 0.033525 | 2.5898 | 57.4429 | 148.7681 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 65.2302 | 5.2224 | 0.89124 | 108.6055 | 97.9256 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52.837 | 71.2608
CID=513181420 | 0 | 57.5 | 63.3749 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 33618.2671 | 1.3242 | 0.037473 | 2.4222 | 63.3749 | 153.5074 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 67.7954 | 5.5522 | 0.89772 | 108.689 | 107.2589 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.8149 | 71.0549
CID=320383402 | 0 | 60 | 67.6436 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34214.8219 | 1.1117 | 0.040731 | 1.8506 | 67.3745 | 124.6825 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 78.7718 | 5.8975 | 0.90124 | 97.0873 | 113.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=320383433 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383208 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383239 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383278 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383309 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383084 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383115 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383154 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320383185 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675322107 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675322138 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675321913 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675321944 | 3 | 15 | 6.9904 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 18490.0739 | 0.47546 | 0.0072103 | 12.0922 | 6.9904 | 84.5289 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 22.9369 | 1.5081 | 0.66827 | 80.1642 | 15.893 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=675321983 | 3 | 17.5 | 8.689 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 18880.4041 | 0.52419 | 0.0077257 | 10.5237 | 8.689 | 91.4399 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 25.7247 | 1.635 | 0.686 | 108.8988 | 19.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2157 | 6.1159 | 16.4081
CID=675322014 | 3 | 20 | 10.6794 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 20163.124 | 0.5809 | 0.008414 | 9.3059 | 10.6794 | 99.3815 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 28.4166 | 1.7699 | 0.70519 | 109.6728 | 23.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3272 | 7.4444 | 20.3842
CID=675321789 | 3 | 22.5 | 12.8666 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 21367.5375 | 0.63738 | 0.0092352 | 8.3076 | 12.8666 | 106.8904 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 31.0615 | 1.9131 | 0.72448 | 110 | 26.9833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.8813 | 24.8225
CID=675321820 | 3 | 25 | 15.1616 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 22468.9089 | 0.68999 | 0.010154 | 7.4773 | 15.1616 | 113.3673 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 33.6599 | 2.0648 | 0.74285 | 110 | 31.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.3039 | 29.7346
CID=675321859 | 3 | 27.5 | 17.5514 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 23470.3395 | 0.74189 | 0.011161 | 6.8005 | 17.5514 | 119.3586 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 36.1493 | 2.2255 | 0.76015 | 110 | 35.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.151 | 33.7526
CID=675321890 | 3 | 30 | 20.6269 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 24539.2362 | 0.81183 | 0.012463 | 6.1966 | 20.6269 | 127.8176 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 38.7234 | 2.3954 | 0.77995 | 110 | 40.1812 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.3139 | 39.5659
CID=-1295338016 | 3 | 32.5 | 23.6418 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 25494.7475 | 0.86955 | 0.013815 | 5.6635 | 23.6418 | 133.8957 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 41.3017 | 2.575 | 0.79698 | 110 | 45.0701 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.265 | 45.7721
CID=-1295337985 | 3 | 35 | 27.344 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 26478.5453 | 0.94419 | 0.015491 | 5.1968 | 27.344 | 142.1002 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 43.8902 | 2.7645 | 0.81508 | 110 | 50.97 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.9753 | 52.4501
CID=-1295338210 | 3 | 37.5 | 30.2412 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 27231.9375 | 0.98754 | 0.016953 | 4.8001 | 30.2412 | 145.1614 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 46.3515 | 2.9643 | 0.82737 | 110 | 55.5332 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.2782 | 57.13
CID=-1295338179 | 3 | 40 | 34.1834 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 28056.7211 | 1.0584 | 0.018897 | 4.4419 | 34.1834 | 151.8404 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 48.8573 | 3.1747 | 0.84182 | 110 | 61.6955 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.2945 | 63.85
CID=-1295338140 | 3 | 42.5 | 38.0827 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 28822.187 | 1.1188 | 0.02093 | 4.1102 | 38.0827 | 156.5272 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 51.4206 | 3.3962 | 0.85389 | 110 | 67.7616 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2941 | 70.4485
CID=-1295338109 | 3 | 45 | 42.2228 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 29554.4842 | 1.1813 | 0.023176 | 3.814 | 42.2228 | 161.0376 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 53.9629 | 3.6291 | 0.86467 | 110 | 74.1915 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.628 | 77.0074
CID=-1295338334 | 3 | 47.5 | 45.3544 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 30140.0453 | 1.2057 | 0.025125 | 3.5282 | 45.3545 | 160.0186 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 56.6349 | 3.8738 | 0.87164 | 110 | 79.0568 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4646 | 78.0241
CID=-1295338303 | 3 | 50 | 48.3385 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 30699.4656 | 1.2282 | 0.027126 | 3.2797 | 48.3385 | 158.5354 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 59.2084 | 4.1306 | 0.87746 | 109.8806 | 83.699 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1942 | 38.3198 | 78.3946
CID=-1295338264 | 3 | 52.5 | 51.4963 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 31249.6122 | 1.2551 | 0.029329 | 3.0565 | 51.4963 | 157.4004 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 61.7451 | 4.4 | 0.88286 | 109.7519 | 88.6213 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7331 | 42.5765 | 78.2557
CID=-1295338233 | 3 | 55 | 55.6386 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 31871.7192 | 1.2993 | 0.032126 | 2.8424 | 55.6386 | 158.1479 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 64.4017 | 4.6823 | 0.88892 | 109.5749 | 95.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.3691 | 77.4469
CID=545131057 | 3 | 57.5 | 59.9906 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 32471.5715 | 1.3443 | 0.035209 | 2.6438 | 59.9906 | 158.6037 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 67.0843 | 4.9781 | 0.89423 | 108.9042 | 101.9275 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.8459 | 78.4246
CID=545131088 | 3 | 60 | 64.4309 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 33038.4534 | 1.3864 | 0.03855 | 2.4577 | 64.4309 | 158.3546 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 69.8098 | 5.2877 | 0.89871 | 108.5365 | 108.9262 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 59.7005 | 78.6223
CID=545130863 | 3 | 62.5 | 70.8847 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 33681.8935 | 1.1962 | 0.042237 | 1.9122 | 69.075 | 132.0841 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 79.5947 | 5.6115 | 0.90256 | 98.2763 | 116.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.5754 | 77.8125
CID=545130894 | 3 | 65 | 75.3522 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34259.8998 | 1.2377 | 0.04694 | 1.7561 | 75.117 | 131.9149 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 83.0361 | 5.95 | 0.90655 | 97.0873 | 125.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=545130933 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545130964 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545130739 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545130770 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545130809 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545130840 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332822 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332853 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332628 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332659 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332698 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332729 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352332504 | 6 | 20 | 9.2978 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 18676.7161 | 0.58596 | 0.0079397 | 10.9111 | 9.2978 | 101.4492 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 28.1173 | 1.5911 | 0.69205 | 109.4597 | 20.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3829 | 6.8403 | 16.6703
CID=352332535 | 6 | 22.5 | 11.0421 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 19777.4091 | 0.62628 | 0.008584 | 9.6279 | 11.0421 | 106.3122 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 30.6959 | 1.7198 | 0.70852 | 110 | 23.6785 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7456 | 20.9315
CID=352332574 | 6 | 25 | 13.3899 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 20978.6024 | 0.68805 | 0.0094719 | 8.5482 | 13.3899 | 114.4594 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 33.3703 | 1.8563 | 0.72883 | 110 | 27.9132 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3478 | 25.5163
CID=352332605 | 6 | 27.5 | 15.7834 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 22073.7407 | 0.74591 | 0.010441 | 7.7002 | 15.7834 | 121.5346 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 35.8939 | 2.0007 | 0.74752 | 110 | 32.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.8391 | 30.6162
CID=481220194 | 6 | 30 | 18.0148 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 23012.5094 | 0.78962 | 0.011415 | 6.9909 | 18.0148 | 125.9406 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 38.3479 | 2.1535 | 0.7633 | 110 | 35.8582 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4236 | 34.7884
CID=481220035 | 6 | 32.5 | 21.0075 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 24024.9428 | 0.85885 | 0.012709 | 6.3791 | 21.0075 | 134.0091 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 40.8311 | 2.3149 | 0.78222 | 110 | 40.8036 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.4257 | 40.7528
CID=481220132 | 6 | 35 | 24.6663 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 25086.7257 | 0.94042 | 0.014314 | 5.8161 | 24.6663 | 143.462 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 43.4364 | 2.4852 | 0.80228 | 110 | 46.7124 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.097 | 47.374
CID=481220229 | 6 | 37.5 | 28.0958 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 26001.7107 | 1.0053 | 0.015922 | 5.3328 | 28.0958 | 149.8298 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 45.9789 | 2.6649 | 0.81842 | 110 | 52.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.3967 | 54.193
CID=481220318 | 6 | 40 | 31.6853 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 26833.3442 | 1.0708 | 0.017676 | 4.9176 | 31.6853 | 155.8153 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 48.4592 | 2.8541 | 0.83295 | 110 | 57.7956 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.7901 | 61.371
CID=481220159 | 6 | 42.5 | 35.3596 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 27609.8616 | 1.132 | 0.019559 | 4.5445 | 35.3596 | 160.6908 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 50.9502 | 3.0532 | 0.84567 | 110 | 63.5274 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0078 | 66.415
CID=481220256 | 6 | 45 | 39.4904 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 28371.1075 | 1.1996 | 0.02173 | 4.2035 | 39.4904 | 165.9971 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 53.4869 | 3.2625 | 0.85777 | 110 | 69.9483 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0513 | 73.8077
CID=481220353 | 6 | 47.5 | 43.8491 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 29114.7275 | 1.2648 | 0.024118 | 3.8871 | 43.8491 | 170.448 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 56.0918 | 3.4825 | 0.8684 | 110 | 76.7175 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5834 | 80.6463
CID=481220442 | 6 | 50 | 47.962 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 29767.283 | 1.3192 | 0.026541 | 3.6067 | 47.962 | 172.9856 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 58.6505 | 3.7134 | 0.87677 | 110 | 83.1128 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.1297 | 86.4588
CID=481220283 | 6 | 52.5 | 51.3022 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 30326.3683 | 1.3465 | 0.028771 | 3.3454 | 51.3021 | 171.6265 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 61.258 | 3.9556 | 0.88255 | 110 | 88.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.549 | 86.5615
CID=288421959 | 6 | 55 | 54.0403 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 30824.7824 | 1.3585 | 0.03087 | 3.1113 | 54.0403 | 168.133 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 63.8223 | 4.2094 | 0.88671 | 109.1986 | 92.5958 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4989 | 43.4253 | 85.8853
CID=288421800 | 6 | 57.5 | 58.0085 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 31398.601 | 1.4017 | 0.033682 | 2.9005 | 58.0085 | 168.2521 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 66.3608 | 4.4753 | 0.89193 | 109.5999 | 98.8132 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5331 | 48.4863 | 86.5751
CID=288421897 | 6 | 60 | 62.5532 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 32001.4385 | 1.4493 | 0.036964 | 2.6939 | 62.5532 | 168.5139 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 69.0529 | 4.7536 | 0.89692 | 109.4546 | 105.9628 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.7344 | 86.0097
CID=288421994 | 6 | 62.5 | 67.2021 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 32570.9823 | 1.4967 | 0.040532 | 2.5049 | 67.2021 | 168.3315 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 71.732 | 5.0447 | 0.9011 | 108.6584 | 113.3095 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.5946 | 87.0244
CID=288422083 | 6 | 65 | 72.1654 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 33124.0635 | 1.5459 | 0.044529 | 2.327 | 72.1654 | 167.9264 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 74.4573 | 5.349 | 0.90473 | 108.5532 | 121.1896 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.1624 | 87.1744
CID=288421924 | 6 | 67.5 | 79.1185 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 33761.0786 | 1.2926 | 0.048822 | 1.7562 | 77.0983 | 135.3988 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 85.2725 | 5.667 | 0.90765 | 95.9768 | 129.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.7476 | 86.2309
CID=288422021 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288422118 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288422207 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288422048 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360664 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360505 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360602 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360699 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360788 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360629 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360726 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360823 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643360912 | 9 | 22.5 | 9.9226 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 18527.9406 | 0.65272 | 0.0081692 | 11.3008 | 9.9225 | 112.1327 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 30.5222 | 1.5501 | 0.69809 | 107.2698 | 21.5957 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2316 | 7.3644 | 17.597
CID=643360753 | 9 | 25 | 11.0376 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 19251.1085 | 0.65819 | 0.008652 | 10.0416 | 11.0376 | 110.8349 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 32.8278 | 1.6731 | 0.70848 | 109.9601 | 23.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0998 | 7.5779 | 21.4167
CID=-1327299459 | 9 | 27.5 | 13.5501 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 20484.9236 | 0.72856 | 0.0096013 | 8.8703 | 13.5501 | 120.193 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 35.5211 | 1.8033 | 0.73014 | 110 | 28.1963 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3386 | 26.1844
CID=-1327299618 | 9 | 30 | 16.1615 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 21613.5583 | 0.79365 | 0.010656 | 7.9326 | 16.1615 | 128.2019 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 38.1238 | 1.941 | 0.75031 | 110 | 32.7265 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.0478 | 31.5026
CID=-1327299521 | 9 | 32.5 | 19.0785 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 22703.8782 | 0.86571 | 0.011881 | 7.1728 | 19.0785 | 136.8455 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 40.6434 | 2.0864 | 0.77031 | 110 | 37.63 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9917 | 37.3388
CID=-1327299424 | 9 | 35 | 21.7673 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 23613.0221 | 0.92103 | 0.013096 | 6.5411 | 21.7673 | 142.3814 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 43.0703 | 2.24 | 0.78665 | 110 | 42.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.0271 | 41.988
CID=-1327299335 | 9 | 37.5 | 25.2767 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 24605.5658 | 0.99834 | 0.014676 | 5.9672 | 25.2767 | 150.8313 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 45.605 | 2.4019 | 0.80533 | 110 | 47.6872 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4302 | 48.8161
CID=-1327299494 | 9 | 40 | 28.8027 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 25509.9736 | 1.066 | 0.016348 | 5.4607 | 28.8027 | 157.2845 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 48.1493 | 2.5724 | 0.82146 | 110 | 53.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.739 | 55.9939
CID=-1327299397 | 9 | 42.5 | 33.1377 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 26447.5262 | 1.1539 | 0.018423 | 5.0141 | 33.1377 | 166.1572 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 50.7113 | 2.7519 | 0.83822 | 110 | 60.0648 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9419 | 63.7251
CID=-1327299300 | 9 | 45 | 36.4715 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 27160.3404 | 1.2039 | 0.020215 | 4.6349 | 36.4715 | 169.0405 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 53.1541 | 2.9406 | 0.84914 | 110 | 65.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6277 | 69.0029
CID=-1327299211 | 9 | 47.5 | 40.8244 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 27921.2647 | 1.2816 | 0.022523 | 4.2947 | 40.8244 | 175.3271 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 55.6139 | 3.1388 | 0.86124 | 110 | 72.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.871 | 76.6845
CID=-1327299370 | 9 | 50 | 45.4304 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 28662.5545 | 1.3561 | 0.025071 | 3.9752 | 45.4304 | 180.5945 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 58.1589 | 3.3469 | 0.8718 | 110 | 79.1748 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.4252 | 84.4459
CID=513169614 | 9 | 52.5 | 49.7113 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 29320.8694 | 1.415 | 0.027631 | 3.6861 | 49.7113 | 183.2406 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 60.7022 | 3.5652 | 0.8799 | 110 | 85.8375 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2376 | 90.1325
CID=513169455 | 9 | 55 | 52.8657 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 29844.9276 | 1.4339 | 0.029847 | 3.4121 | 52.8657 | 180.3857 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 63.3311 | 3.794 | 0.88499 | 110 | 90.7597 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.4435 | 90.1325
CID=513169552 | 9 | 57.5 | 56.4119 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 30397.6898 | 1.4641 | 0.032387 | 3.1683 | 56.4119 | 178.7324 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 65.9209 | 4.0336 | 0.88994 | 109.8977 | 96.3089 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2791 | 45.1717 | 90.1326
CID=513169649 | 9 | 60 | 59.4914 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 30894.859 | 1.481 | 0.034876 | 2.9452 | 59.4914 | 175.216 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 68.5097 | 4.2845 | 0.89367 | 108.3788 | 101.1426 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.2777 | 90.1326
CID=513169738 | 9 | 62.5 | 63.8577 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 31454.4741 | 1.5302 | 0.038172 | 2.744 | 63.8577 | 175.225 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 71.0697 | 4.5468 | 0.89817 | 109.1371 | 108.021 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.0994 | 90.1325
CID=513169579 | 9 | 65 | 68.6969 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 32030.0326 | 1.5808 | 0.04195 | 2.5466 | 68.6969 | 174.9438 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 73.7746 | 4.8211 | 0.90227 | 109.0637 | 115.6788 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.5516 | 90.1325
CID=513169676 | 9 | 67.5 | 73.3898 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 32563.9815 | 1.6251 | 0.04594 | 2.3647 | 73.3898 | 173.5454 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 76.4739 | 5.1077 | 0.90551 | 108.3512 | 123.1392 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.8089 | 90.1325
CID=513169773 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513169862 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513169703 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371379 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371220 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371317 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371414 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371503 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371344 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371441 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371538 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371627 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320371468 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=675310084 | 12 | 25 | 9.5389 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 18463.1265 | 0.66709 | 0.0081306 | 11.918 | 9.5389 | 113.684 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 32.5557 | 1.5117 | 0.6944 | 87.9195 | 20.8711 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.9035 | 14.4449
CID=675309925 | 12 | 27.5 | 11.3194 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 18854.2365 | 0.70562 | 0.0088072 | 10.4103 | 11.3194 | 117.8382 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 35.1172 | 1.6293 | 0.71103 | 108.6671 | 24.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5322 | 7.806 | 21.8594
CID=675310022 | 12 | 30 | 13.9106 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 20081.7812 | 0.78071 | 0.0097988 | 9.1795 | 13.9106 | 127.6927 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 37.7658 | 1.7537 | 0.73306 | 109.5578 | 28.8312 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4422 | 9.6007 | 26.8405
CID=675310119 | 12 | 32.5 | 16.675 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 21221.8392 | 0.85468 | 0.010923 | 8.2059 | 16.675 | 136.8335 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 40.3171 | 1.8852 | 0.75401 | 110 | 33.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4509 | 32.3474
CID=675310208 | 12 | 35 | 19.5127 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 22248.2572 | 0.91966 | 0.012142 | 7.3815 | 19.5127 | 144.0326 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 42.8656 | 2.0239 | 0.77308 | 110 | 38.3487 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2216 | 38.3861
CID=675310049 | 12 | 37.5 | 22.1261 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 23128.1646 | 0.97009 | 0.013351 | 6.7128 | 22.1261 | 148.5281 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 45.2982 | 2.1702 | 0.78869 | 110 | 42.6237 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1077 | 43.1811
CID=675310146 | 12 | 40 | 25.7793 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 24112.3631 | 1.0563 | 0.015009 | 6.1287 | 25.7793 | 157.9932 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 47.7772 | 2.3243 | 0.80778 | 110 | 48.4877 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6528 | 50.1588
CID=675310243 | 12 | 42.5 | 29.9688 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 25105.0145 | 1.1482 | 0.016962 | 5.5944 | 29.9688 | 167.6571 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 50.3501 | 2.4864 | 0.82628 | 110 | 55.1057 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6832 | 57.8258
CID=675310332 | 12 | 45 | 33.9487 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 25974.1414 | 1.2243 | 0.018941 | 5.1368 | 33.9487 | 174.3887 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 52.8613 | 2.6569 | 0.84102 | 110 | 61.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3728 | 65.6764
CID=675310173 | 12 | 47.5 | 38.1073 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 26764.7905 | 1.3008 | 0.021102 | 4.739 | 38.1073 | 180.5908 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 55.3332 | 2.836 | 0.85396 | 110 | 67.7999 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.1625 | 73.9419
CID=-1295350039 | 12 | 50 | 42.2311 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 27493.4573 | 1.3683 | 0.023373 | 4.3804 | 42.2311 | 184.9875 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 57.8187 | 3.0241 | 0.86469 | 110 | 74.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.7952 | 79.5389
CID=-1295350198 | 12 | 52.5 | 46.8056 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 28199.8401 | 1.443 | 0.025969 | 4.055 | 46.8056 | 189.7965 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 60.3288 | 3.2213 | 0.87456 | 110 | 81.3134 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.0954 | 87.9361
CID=-1295350101 | 12 | 55 | 50.5267 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 28795.9677 | 1.4838 | 0.028349 | 3.7539 | 50.5267 | 189.6746 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 62.8804 | 3.428 | 0.88128 | 110 | 87.1087 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3247 | 90.1325
CID=-1295350004 | 12 | 57.5 | 53.3646 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 29289.323 | 1.496 | 0.030482 | 3.4789 | 53.3646 | 185.6517 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 65.4446 | 3.6445 | 0.88573 | 110 | 91.5393 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.1087 | 90.1325
CID=-1295349915 | 12 | 60 | 56.9874 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 29838.5297 | 1.5264 | 0.033123 | 3.2232 | 56.9874 | 183.6796 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 68.0703 | 3.8712 | 0.89067 | 109.4676 | 97.2111 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6463 | 45.939 | 90.1325
CID=-1295350074 | 12 | 62.5 | 60.6703 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 30387.6848 | 1.557 | 0.035975 | 2.9907 | 60.6703 | 181.4448 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 70.6918 | 4.1083 | 0.89497 | 108.8148 | 102.9969 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50.8496 | 90.1325
CID=-1295349977 | 12 | 65 | 64.2882 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 30895.0886 | 1.5847 | 0.039001 | 2.7778 | 64.2882 | 178.5808 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 73.3113 | 4.3561 | 0.89858 | 108.7887 | 108.7007 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.6734 | 90.1325
CID=-1295349880 | 12 | 67.5 | 69.1819 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 31449.2875 | 1.6441 | 0.042915 | 2.5859 | 69.1819 | 178.8982 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 75.8926 | 4.615 | 0.90264 | 108.9916 | 116.4483 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 62.1983 | 90.1326
CID=-1295349791 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295349950 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119034 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545118875 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545118972 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119069 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119158 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545118999 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119096 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119193 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119282 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545119123 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352320799 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352320640 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=352320737 | 15 | 27.5 | 9.0807 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18440.3682 | 0.67545 | 0.0080757 | 12.5714 | 9.0807 | 114.1576 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 34.6266 | 1.4757 | 0.68991 | 70.5114 | 19.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=352320834 | 15 | 30 | 12.0629 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 18648.7816 | 0.78282 | 0.0091074 | 10.7448 | 12.0629 | 129.613 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 37.5355 | 1.5883 | 0.7176 | 109.0461 | 25.5402 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7138 | 8.6958 | 22.1642
CID=352320923 | 15 | 32.5 | 14.3255 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 19703.0782 | 0.83753 | 0.01002 | 9.4776 | 14.3255 | 135.771 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 40.0731 | 1.7074 | 0.73637 | 110 | 29.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9438 | 27.4707
CID=352320764 | 15 | 35 | 17.1775 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 20806.7034 | 0.91174 | 0.011194 | 8.4195 | 17.1775 | 144.6263 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 42.6691 | 1.833 | 0.75756 | 110 | 34.4508 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8586 | 33.1342
CID=352320861 | 15 | 37.5 | 20.2713 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 21864.8565 | 0.98854 | 0.012525 | 7.5645 | 20.2712 | 153.3421 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 45.2013 | 1.9655 | 0.77779 | 110 | 39.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9017 | 39.38
CID=352320958 | 15 | 40 | 23.2664 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 22800.815 | 1.0553 | 0.013897 | 6.8755 | 23.2664 | 159.9675 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 47.618 | 2.1051 | 0.79498 | 110 | 44.4662 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8898 | 45.3962
CID=352321047 | 15 | 42.5 | 26.5637 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 23689.0733 | 1.1264 | 0.015458 | 6.2772 | 26.5637 | 166.747 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 50.043 | 2.2519 | 0.8115 | 110 | 49.734 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2373 | 51.5431
CID=352320888 | 15 | 45 | 30.6256 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 24629.9245 | 1.2154 | 0.017399 | 5.7326 | 30.6256 | 175.5644 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 52.5614 | 2.4063 | 0.82889 | 110 | 56.1362 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.0094 | 59.4744
CID=481216995 | 15 | 47.5 | 34.7545 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 25493.1933 | 1.2959 | 0.019474 | 5.2515 | 34.7545 | 182.5151 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 55.0906 | 2.5686 | 0.84371 | 110 | 62.5853 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.7775 | 67.6857
CID=481217026 | 15 | 50 | 39.7227 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 26379.6229 | 1.3966 | 0.022009 | 4.8241 | 39.7227 | 191.6277 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 57.644 | 2.7389 | 0.85839 | 110 | 70.309 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.453 | 76.5318
CID=481216933 | 15 | 52.5 | 43.5163 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 27053.6383 | 1.4538 | 0.0242 | 4.4613 | 43.5163 | 194.1372 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 60.0868 | 2.9175 | 0.86766 | 110 | 76.2005 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.551 | 82.4122
CID=481216964 | 15 | 55 | 48.0116 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 27729.5605 | 1.5308 | 0.026826 | 4.1398 | 48.0116 | 198.7576 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 62.5108 | 3.1047 | 0.87686 | 110 | 83.1902 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.9713 | 90.1325
CID=481217119 | 15 | 57.5 | 51.2841 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 28271.4174 | 1.5576 | 0.029072 | 3.8302 | 51.2841 | 196.4258 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 65.0455 | 3.3008 | 0.88252 | 110 | 88.2901 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3346 | 90.1325
CID=481217150 | 15 | 60 | 54.1803 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 28777.8857 | 1.5682 | 0.031293 | 3.5412 | 54.1803 | 191.8627 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 67.6466 | 3.5061 | 0.88691 | 110 | 92.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.1963 | 90.1325
CID=481217057 | 15 | 62.5 | 57.5539 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 29301.6959 | 1.5905 | 0.033891 | 3.276 | 57.5539 | 188.5443 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 70.2833 | 3.7208 | 0.89138 | 108.941 | 98.0997 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.6943 | 90.1325
CID=481217088 | 15 | 65 | 61.4806 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 29846.0134 | 1.6274 | 0.036944 | 3.0363 | 61.4806 | 186.6709 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 72.9118 | 3.9453 | 0.89583 | 108.1136 | 104.2726 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51.93 | 90.1325
CID=481217243 | 15 | 67.5 | 64.9211 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 30364.5413 | 1.6473 | 0.039979 | 2.812 | 64.9211 | 182.5598 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 75.5854 | 4.1798 | 0.89915 | 106.2411 | 109.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.5173 | 90.1325
CID=481217274 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418760 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418791 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418698 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418729 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418884 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418915 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418822 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288418853 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288419008 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=288419039 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643357465 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643357496 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643357403 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643357434 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643357589 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=643357620 | 18 | 32.5 | 12.8598 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 18482.8707 | 0.86764 | 0.0094355 | 11.072 | 12.8598 | 142.3832 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 39.9803 | 1.5499 | 0.72442 | 108.2569 | 26.9712 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0633 | 9.4876 | 22.9766
CID=643357527 | 18 | 35 | 14.2787 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 19189.4776 | 0.8764 | 0.010098 | 9.8586 | 14.2787 | 140.7685 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 42.2632 | 1.664 | 0.736 | 109.9182 | 29.4761 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2046 | 9.6985 | 28.0193
CID=643357558 | 18 | 37.5 | 17.3676 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 20340.5446 | 0.96411 | 0.011366 | 8.7217 | 17.3676 | 151.4754 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 44.8728 | 1.7842 | 0.75888 | 110 | 34.7714 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8592 | 33.8929
CID=643357713 | 18 | 40 | 20.5285 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 21389.2772 | 1.0431 | 0.012742 | 7.8042 | 20.5285 | 160.2091 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 47.4205 | 1.9109 | 0.77936 | 110 | 40.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.906 | 40.396
CID=643357744 | 18 | 42.5 | 23.9151 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 22382.9475 | 1.1242 | 0.01428 | 7.0524 | 23.9151 | 168.6595 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 49.9115 | 2.0442 | 0.79842 | 110 | 45.5091 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0656 | 47.4637
CID=-1327302658 | 18 | 45 | 27.1001 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 23233.7789 | 1.1895 | 0.015828 | 6.4279 | 27.1001 | 174.1977 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 52.3301 | 2.1844 | 0.81398 | 110 | 50.584 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.496 | 52.9123
CID=-1327302627 | 18 | 47.5 | 31.4171 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 24177.0295 | 1.2914 | 0.017903 | 5.8712 | 31.4171 | 184.456 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 54.8154 | 2.3317 | 0.83194 | 110 | 57.3759 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.5596 | 60.9897
CID=-1327302720 | 18 | 50 | 36.0119 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 25083.0737 | 1.3886 | 0.020207 | 5.3677 | 36.0119 | 193.2999 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 57.3608 | 2.4862 | 0.84773 | 110 | 64.5424 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7665 | 69.7483
CID=-1327302689 | 18 | 52.5 | 40.5807 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 25908.6176 | 1.4772 | 0.022634 | 4.9337 | 40.5807 | 200.215 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 59.8626 | 2.6484 | 0.86062 | 110 | 71.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8781 | 78.6886
CID=-1327302534 | 18 | 55 | 45.3472 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 26660.2157 | 1.5658 | 0.025289 | 4.5522 | 45.3472 | 206.4314 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 62.345 | 2.8184 | 0.87162 | 110 | 79.0455 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.0948 | 88.1043
CID=-1327302503 | 18 | 57.5 | 48.7881 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 27242.0656 | 1.6021 | 0.027529 | 4.2067 | 48.7881 | 205.2363 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 64.8349 | 2.9964 | 0.87828 | 110 | 84.3992 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0067 | 90.1325
CID=-1327302596 | 18 | 60 | 51.7977 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 27739.168 | 1.6267 | 0.029717 | 3.905 | 51.7977 | 202.2718 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 67.2655 | 3.1827 | 0.88334 | 110 | 89.0917 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.0194 | 90.1325
CID=-1327302565 | 18 | 62.5 | 54.9919 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 28278.5951 | 1.6421 | 0.032139 | 3.5995 | 54.992 | 197.9426 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 69.9206 | 3.3776 | 0.88805 | 109.6356 | 94.0848 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6441 | 43.2784 | 90.1325
CID=-1327302410 | 18 | 65 | 58.5825 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 28808.1608 | 1.6706 | 0.034921 | 3.3279 | 58.5825 | 194.9575 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 72.5494 | 3.5814 | 0.89262 | 109.1752 | 99.7145 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.0659 | 90.1326
CID=-1327302379 | 18 | 67.5 | 62.2973 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 29328.289 | 1.7005 | 0.037968 | 3.0796 | 62.2972 | 191.8521 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 75.192 | 3.7943 | 0.89666 | 108.2993 | 105.5594 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.0188 | 90.1325
CID=513166415 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166446 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166353 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166384 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166539 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166570 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166477 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166508 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166663 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=513166694 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368180 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368211 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368118 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368149 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368304 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368335 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368242 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=320368273 | 21 | 35 | 12.6799 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 18375.0039 | 0.90377 | 0.0094664 | 11.5894 | 12.6799 | 146.9527 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 42.1652 | 1.5138 | 0.7229 | 93.6662 | 26.6498 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.9152 | 20.974
CID=320368428 | 21 | 37.5 | 14.5068 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 18773.0487 | 0.93004 | 0.01027 | 10.1996 | 14.5068 | 147.963 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 44.5777 | 1.6232 | 0.73779 | 108.5017 | 29.874 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8215 | 9.8342 | 28.5245
CID=320368459 | 21 | 40 | 17.8183 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 19954.4404 | 1.0292 | 0.011636 | 8.9854 | 17.8182 | 160.1039 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 47.2003 | 1.7385 | 0.76197 | 109.5788 | 35.5288 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4212 | 12.2151 | 34.6277
CID=675306885 | 21 | 42.5 | 21.2374 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 21025.2198 | 1.1211 | 0.013128 | 8.0244 | 21.2374 | 170.4182 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 49.7394 | 1.8598 | 0.78358 | 110 | 41.1789 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.5417 | 41.3248
CID=675306916 | 21 | 45 | 24.7145 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 21995.3423 | 1.2046 | 0.01473 | 7.2343 | 24.7145 | 178.7925 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 52.2305 | 1.9873 | 0.80253 | 110 | 46.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.752 | 48.6019
CID=675306823 | 21 | 47.5 | 27.8681 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 22822.7215 | 1.2663 | 0.0163 | 6.5803 | 27.8681 | 183.3805 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 54.6522 | 2.1213 | 0.81742 | 110 | 51.7984 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0805 | 54.2307
CID=675306854 | 21 | 50 | 32.0569 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 23720.3018 | 1.365 | 0.018365 | 6.0116 | 32.0569 | 192.7135 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 57.099 | 2.2619 | 0.83433 | 110 | 58.3767 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9077 | 62.5046
CID=675307009 | 21 | 52.5 | 36.8379 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 24628.7948 | 1.4711 | 0.02079 | 5.4914 | 36.8379 | 202.2911 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 59.6325 | 2.4094 | 0.85025 | 110 | 65.827 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.2501 | 71.6014
CID=675307040 | 21 | 55 | 41.5106 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 25439.6585 | 1.562 | 0.023313 | 5.0352 | 41.5106 | 209.0143 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 62.1596 | 2.564 | 0.86295 | 110 | 73.0854 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.3799 | 80.9026
CID=675306947 | 21 | 57.5 | 46.9249 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 26255.7019 | 1.6691 | 0.026309 | 4.627 | 46.9249 | 217.1205 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 64.7157 | 2.726 | 0.8748 | 110 | 81.499 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.5224 | 90.1325
CID=675306978 | 21 | 60 | 49.5713 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 26745.2919 | 1.6819 | 0.028265 | 4.2858 | 49.5713 | 212.455 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 67.1264 | 2.8955 | 0.87966 | 110 | 85.6193 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.0509 | 90.1326
CID=675307133 | 21 | 62.5 | 52.3869 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 27239.1761 | 1.6932 | 0.030429 | 3.9599 | 52.387 | 207.447 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 69.6492 | 3.0728 | 0.88426 | 109.9972 | 90.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 5.028 | 39.8051 | 90.1326
CID=675307164 | 21 | 65 | 55.8222 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 27787.5095 | 1.7215 | 0.033035 | 3.6598 | 55.8222 | 204.301 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 72.2197 | 3.2582 | 0.88917 | 109.4687 | 95.3849 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5013 | 44.3855 | 90.1326
CID=-1295353238 | 21 | 67.5 | 59.4652 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 28316.7866 | 1.7499 | 0.03593 | 3.3782 | 59.4652 | 200.8866 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 74.8653 | 3.4519 | 0.89364 | 108.7621 | 101.1014 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.2427 | 90.1326
CID=-1295353207 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295353300 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295353269 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295353114 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295353083 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295353176 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295353145 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295352990 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1295352959 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115835 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115866 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115773 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115804 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115959 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115990 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115897 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545115928 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545116083 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=545116114 | 24 | 37.5 | 11.9787 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18330.6423 | 0.90686 | 0.0093367 | 12.1925 | 11.9787 | 146.0512 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 44.2901 | 1.4799 | 0.71687 | 75.2392 | 25.388 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=352317600 | 24 | 40 | 15.3833 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 18557.6232 | 1.0248 | 0.010665 | 10.4938 | 15.3833 | 161.4293 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 47.0216 | 1.5849 | 0.74453 | 108.7066 | 31.3923 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0333 | 10.888 | 28.8692
CID=352317631 | 24 | 42.5 | 18.281 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 19580.5709 | 1.0992 | 0.011918 | 9.2576 | 18.281 | 169.2384 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 49.5472 | 1.6955 | 0.76509 | 110 | 36.3032 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5977 | 35.3309
CID=352317538 | 24 | 45 | 21.6844 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 20597.7948 | 1.1877 | 0.013432 | 8.2366 | 21.6844 | 178.6064 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 52.0958 | 1.8118 | 0.78618 | 110 | 41.9067 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8492 | 42.1901
CID=352317569 | 24 | 47.5 | 25.375 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 21583.1542 | 1.2799 | 0.015144 | 7.4035 | 25.375 | 187.8637 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 54.605 | 1.9339 | 0.80581 | 110 | 47.8438 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2586 | 49.7239
CID=352317724 | 24 | 50 | 29.3294 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 22521.2655 | 1.377 | 0.017056 | 6.7204 | 29.3294 | 197.1062 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 57.0517 | 2.0621 | 0.82367 | 110 | 54.101 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8019 | 57.9119
CID=352317755 | 24 | 52.5 | 32.9423 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 23309.1106 | 1.4505 | 0.018943 | 6.141 | 32.9423 | 202.2976 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 59.4568 | 2.1966 | 0.83753 | 110 | 59.7597 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5727 | 64.0509
CID=352317662 | 24 | 55 | 37.8587 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 24197.1453 | 1.5642 | 0.021476 | 5.6099 | 37.8587 | 212.3832 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 61.9637 | 2.3376 | 0.85325 | 110 | 67.4136 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0461 | 73.2965
CID=352317693 | 24 | 57.5 | 42.8189 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 25020.9934 | 1.6652 | 0.024179 | 5.135 | 42.8189 | 219.8734 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 64.504 | 2.4852 | 0.86607 | 110 | 75.1172 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.3599 | 83.1958
CID=352317848 | 24 | 60 | 47.2258 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 25733.0962 | 1.7398 | 0.02681 | 4.7259 | 47.2257 | 223.1845 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 66.9944 | 2.6398 | 0.87538 | 110 | 81.967 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.9235 | 90.1325
CID=352317879 | 24 | 62.5 | 49.9793 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 26234.803 | 1.7482 | 0.028867 | 4.354 | 49.9793 | 217.6085 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 69.5077 | 2.8015 | 0.88036 | 110 | 86.2552 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5949 | 90.1326
CID=210088567 | 24 | 65 | 53.1023 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 26771.6114 | 1.7666 | 0.031235 | 4.0134 | 53.1023 | 213.1197 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 72.0696 | 2.9705 | 0.88534 | 109.8298 | 91.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8511 | 40.7589 | 90.1326
CID=1514050482 | 24 | 67.5 | 56.6821 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 27302.7466 | 1.8032 | 0.033991 | 3.7143 | 56.6821 | 210.5326 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 74.5937 | 3.147 | 0.89029 | 109.5588 | 96.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4117 | 45.532 | 90.1326
CID=1332482029 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658523352 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710791797 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593170118 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411601665 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715563580 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631672161 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327710246 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210089592 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514051507 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332483054 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658522327 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710790772 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593171143 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411602690 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715564605 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631671136 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327709221 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210086521 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514048436 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332479983 | 27 | 42.5 | 16.3801 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 18375.4032 | 1.1314 | 0.011115 | 10.7686 | 16.3801 | 176.3904 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 49.5072 | 1.5489 | 0.75189 | 109.3849 | 33.0992 | 0 | 0 | 0 | 0 | 0 | 0 | 5.728 | 12.0582 | 29.3459
CID=-1658525398 | 27 | 45 | 18.2026 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 19084.7921 | 1.1475 | 0.012019 | 9.6027 | 18.2026 | 174.7941 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 51.8034 | 1.6551 | 0.76456 | 109.8191 | 36.1722 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4522 | 12.2922 | 35.9335
CID=-710793843 | 27 | 47.5 | 21.9015 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 20153.0321 | 1.2541 | 0.013663 | 8.5158 | 21.9015 | 186.5085 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 54.3607 | 1.7667 | 0.78742 | 110 | 42.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8597 | 43.0269
CID=593168072 | 27 | 50 | 25.7848 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 21152.5879 | 1.3554 | 0.015477 | 7.6259 | 25.7848 | 196.6319 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 56.8914 | 1.8839 | 0.80781 | 110 | 48.4966 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4382 | 50.8249
CID=411599619 | 27 | 52.5 | 29.7932 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 22072.7561 | 1.4511 | 0.017446 | 6.8876 | 29.7932 | 205.2048 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 59.3899 | 2.0067 | 0.82557 | 110 | 54.8299 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9821 | 59.2263
CID=1715561534 | 27 | 55 | 33.3906 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 22849.325 | 1.5221 | 0.019366 | 6.2774 | 33.3906 | 209.6067 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 61.8181 | 2.1355 | 0.83911 | 110 | 60.4593 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.6823 | 65.5153
CID=-1631674207 | 27 | 57.5 | 38.2764 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 23709.0403 | 1.64 | 0.021937 | 5.7406 | 38.2765 | 219.7287 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 64.2827 | 2.2704 | 0.85443 | 110 | 68.0627 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0535 | 74.9452
CID=-327712292 | 27 | 60 | 43.8914 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 24589.7761 | 1.7674 | 0.024979 | 5.2436 | 43.8914 | 230.147 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 66.8464 | 2.4116 | 0.8685 | 110 | 76.7832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1043 | 85.2525
CID=210087546 | 27 | 62.5 | 47.6975 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 25223.1295 | 1.8168 | 0.027414 | 4.8152 | 47.6975 | 229.6749 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 69.3566 | 2.5593 | 0.87627 | 110 | 82.7011 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.5524 | 90.1325
CID=1514049461 | 27 | 65 | 51.1498 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 25801.7022 | 1.8457 | 0.029849 | 4.423 | 51.1498 | 226.233 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 71.9214 | 2.7136 | 0.88231 | 109.9939 | 88.0806 | 0 | 0 | 0 | 0 | 0 | 0 | 5.061 | 38.1555 | 90.1326
CID=1332481008 | 27 | 67.5 | 53.9889 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 26299.3514 | 1.853 | 0.032165 | 4.0739 | 53.9889 | 219.9436 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 74.4805 | 2.875 | 0.88664 | 109.9226 | 92.5155 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8719 | 41.9411 | 90.1326
CID=-1658524373 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710792818 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593169097 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411600644 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715562559 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631673182 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327711267 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210092667 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514054582 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332486129 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658519252 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710787697 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593174218 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411605765 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715567680 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631668061 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327706146 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210093692 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514055607 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332487154 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658518227 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710786672 | 30 | 45 | 16.6623 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 18220.0506 | 1.2057 | 0.011333 | 11.1605 | 16.6623 | 185.9604 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 51.8526 | 1.515 | 0.75392 | 100.8166 | 33.5789 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.2153 | 30.0035
CID=593175243 | 30 | 47.5 | 18.5942 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 18710.4632 | 1.2217 | 0.012294 | 9.8966 | 18.5942 | 184.0198 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 54.1883 | 1.6171 | 0.76716 | 109.5487 | 36.8255 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6072 | 12.6305 | 36.4854
CID=411606790 | 30 | 50 | 22.4299 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 19776.7451 | 1.3341 | 0.01402 | 8.7427 | 22.4299 | 196.0987 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 56.7599 | 1.7244 | 0.7904 | 109.5925 | 43.1159 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4075 | 15.2979 | 43.826
CID=1715568705 | 30 | 52.5 | 26.5761 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 20783.7997 | 1.4472 | 0.01597 | 7.805 | 26.5761 | 207.4256 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 59.3081 | 1.8368 | 0.81156 | 110 | 49.7537 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.16 | 51.8244
CID=-1631667036 | 30 | 55 | 30.7585 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 21697.5373 | 1.5502 | 0.018052 | 7.0372 | 30.7585 | 216.4526 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 61.8102 | 1.9547 | 0.82941 | 110 | 56.3445 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8596 | 60.4554
CID=-327705121 | 30 | 57.5 | 34.8921 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 22526.1861 | 1.6436 | 0.020239 | 6.4016 | 34.8921 | 223.3641 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 64.2582 | 2.0782 | 0.84416 | 110 | 62.7996 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.677 | 68.5376
CID=210090621 | 30 | 60 | 39.3393 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 23310.0786 | 1.7418 | 0.022692 | 5.8505 | 39.3393 | 230.1539 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 66.7093 | 2.2074 | 0.85736 | 110 | 69.7136 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.9058 | 76.6398
CID=1514052536 | 30 | 62.5 | 44.9216 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 24152.3377 | 1.871 | 0.025795 | 5.3451 | 44.9216 | 240.1118 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 69.2481 | 2.3426 | 0.87073 | 110 | 78.3841 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.8512 | 87.1331
CID=1332484083 | 30 | 65 | 48.3853 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 24744.3505 | 1.907 | 0.028146 | 4.9066 | 48.3853 | 237.406 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 71.7471 | 2.4839 | 0.87755 | 110 | 83.7718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4695 | 90.1325
CID=-1658521298 | 30 | 67.5 | 51.4166 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 25291.0383 | 1.9174 | 0.030459 | 4.4978 | 51.4166 | 231.264 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 74.3302 | 2.6315 | 0.88274 | 110 | 88.497 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.5113 | 90.1325
CID=-710789743 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593172172 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411603719 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715565634 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631670107 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327708192 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210091646 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514053561 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332485108 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658520273 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710788718 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593173197 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411604744 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715566659 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631669082 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327707167 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210080367 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514042282 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332473829 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658531552 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710799997 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593161918 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411593465 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715555380 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631680361 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327718446 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210081392 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514043307 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332474854 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658530527 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710798972 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593162943 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411594490 | -15 | -5 | 4.0748 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18380.4164 | 0.23896 | 0.0067931 | 11.1511 | 4.0748 | 45.4388 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 3.9871 | 1.4946 | 0.63465 | 76.7496 | 9.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=1715556405 | -15 | -2.5 | 6.252 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 20105.0809 | 0.33078 | 0.0066978 | 9.9586 | 6.252 | 62.2612 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 8.4037 | 1.6437 | 0.66015 | 110 | 14.389 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3.8092 | 8.6947
CID=-1631679336 | -15 | 0 | 7.7318 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 21567.3881 | 0.37164 | 0.007073 | 8.8919 | 7.7318 | 68.7501 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 11.3408 | 1.804 | 0.67617 | 110 | 17.3733 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.4307 | 11.0329
CID=-327717421 | -15 | 2.5 | 9.4958 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 22994.5031 | 0.4185 | 0.0076129 | 8.01 | 9.4958 | 76.0614 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 14.1713 | 1.9762 | 0.69398 | 110 | 20.7894 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.2867 | 13.7049
CID=-2114218606 | -15 | 5 | 11.1889 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 24161.7548 | 0.4565 | 0.0082043 | 7.2821 | 11.1889 | 81.4789 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 16.7962 | 2.1607 | 0.70985 | 110 | 23.9485 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1823 | 16.1956
CID=-2013462057 | -15 | 7.5 | 13.3026 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 25372.5136 | 0.50099 | 0.0089673 | 6.5987 | 13.3026 | 87.78 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 19.6323 | 2.3583 | 0.72811 | 110 | 27.7586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2299 | 19.3754
CID=-991825144 | -15 | 10 | 15.8304 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 26623.5971 | 0.55102 | 0.0099097 | 5.9842 | 15.8304 | 94.7322 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 22.58 | 2.5693 | 0.74787 | 110 | 32.1604 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5747 | 23.0861
CID=594461773 | -15 | 12.5 | 18.5828 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 27789.3446 | 0.60072 | 0.010979 | 5.4507 | 18.5828 | 101.29 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 25.5151 | 2.7945 | 0.76708 | 110 | 36.8064 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0921 | 27.0734
CID=1259868326 | -15 | 15 | 20.8327 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 28622.5114 | 0.63435 | 0.01194 | 5.033 | 20.8327 | 104.8502 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 28.0917 | 3.0345 | 0.78119 | 110 | 40.518 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.5676 | 30.0979
CID=1360624875 | -15 | 17.5 | 23.8171 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 29585.1341 | 0.67943 | 0.013195 | 4.6198 | 23.8171 | 110.0312 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 30.9826 | 3.2899 | 0.7979 | 110 | 45.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.3575 | 34.2767
CID=-1912705508 | -15 | 20 | 26.7907 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 30452.4537 | 0.72008 | 0.014509 | 4.2624 | 26.7907 | 114.1937 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 33.7892 | 3.5612 | 0.81256 | 110 | 50.0939 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3391 | 38.2422
CID=-326418591 | -15 | 22.5 | 28.7954 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 31037.1238 | 0.74144 | 0.015539 | 3.9963 | 28.7954 | 115.0756 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 36.0641 | 3.8493 | 0.82143 | 110 | 53.2607 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6718 | 39.9189
CID=338987962 | -15 | 25 | 30.0365 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 31477.7074 | 0.74452 | 0.01634 | 3.7629 | 30.0365 | 113.0232 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 38.1988 | 4.1546 | 0.82655 | 110 | 55.212 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9411 | 40.1319
CID=439744511 | -15 | 27.5 | 31.5058 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 31981.7835 | 0.74849 | 0.017267 | 3.5253 | 31.5058 | 111.0668 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 40.5723 | 4.4779 | 0.83228 | 110 | 57.5148 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9327 | 40.079
CID=-2114217581 | -15 | 30 | 33.319 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 32554.1474 | 0.75687 | 0.018372 | 3.2926 | 33.319 | 109.7078 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 43.1263 | 4.8198 | 0.83886 | 110 | 60.3477 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.5427 | 40.0954
CID=-2013461032 | -15 | 32.5 | 35.2771 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 33105.6948 | 0.76617 | 0.019591 | 3.0729 | 35.2771 | 108.4041 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 45.7694 | 5.1811 | 0.84541 | 109.4721 | 63.399 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3873 | 30.1228 | 40.4314
CID=-991824119 | -15 | 35 | 37.8109 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33589.2282 | 0.60011 | 0.020316 | 2.3103 | 35.8474 | 82.8181 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 58.2873 | 5.5624 | 0.84722 | 95.8907 | 64.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.7098 | 39.9119
CID=594462798 | -15 | 37.5 | 39.4087 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1259869351 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360625900 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912704483 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326417566 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=338988987 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439745536 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114220652 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013464103 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991827190 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594459727 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1259866280 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360622829 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912707554 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326420637 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=338985916 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439742465 | -12 | 0 | 6.5338 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 19733.4433 | 0.36296 | 0.0067773 | 10.3934 | 6.5338 | 67.908 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 10.6469 | 1.5931 | 0.66328 | 110 | 14.9666 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.1993 | 8.8682
CID=-2114219627 | -12 | 2.5 | 8.0154 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 21126.7329 | 0.40432 | 0.0071777 | 9.2738 | 8.0154 | 74.3326 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 13.4321 | 1.7452 | 0.67912 | 110 | 17.9321 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.6238 | 11.4069
CID=-2013463078 | -12 | 5 | 9.8445 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 22514.8934 | 0.45259 | 0.0077511 | 8.3024 | 9.8445 | 81.7328 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 16.2659 | 1.9081 | 0.69734 | 110 | 21.4489 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4802 | 14.2089
CID=-991826165 | -12 | 7.5 | 11.8661 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 23817.235 | 0.5019 | 0.0084486 | 7.4999 | 11.8661 | 88.9939 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 18.9902 | 2.0826 | 0.71588 | 110 | 25.1839 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.3445 | 17.3877
CID=594460752 | -12 | 10 | 13.8542 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 24907.6312 | 0.54312 | 0.0091928 | 6.8221 | 13.8542 | 94.5142 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 21.6116 | 2.269 | 0.73261 | 110 | 28.732 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5663 | 20.1421
CID=1259867305 | -12 | 12.5 | 16.4949 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 26114.3688 | 0.5976 | 0.010187 | 6.1849 | 16.4949 | 102.0186 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 24.4729 | 2.4678 | 0.75272 | 110 | 33.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9351 | 24.0547
CID=1360623854 | -12 | 15 | 19.3173 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 27267.8578 | 0.64966 | 0.011297 | 5.6294 | 19.3174 | 108.7449 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 27.3336 | 2.6798 | 0.77184 | 110 | 38.0257 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.4239 | 28.2107
CID=-1912706529 | -12 | 17.5 | 22.1012 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 28245.0241 | 0.69564 | 0.012453 | 5.1634 | 22.1012 | 114.1179 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 30.0651 | 2.9053 | 0.78855 | 110 | 42.5834 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.959 | 32.2434
CID=-326419612 | -12 | 20 | 24.9079 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 29106.7829 | 0.738 | 0.013673 | 4.7609 | 24.9079 | 118.5854 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 32.7246 | 3.1449 | 0.8035 | 110 | 47.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.8048 | 36.0111
CID=338986941 | -12 | 22.5 | 28.1786 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 30013.2019 | 0.78327 | 0.015115 | 4.3726 | 28.1786 | 123.2133 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 35.6137 | 3.3993 | 0.81878 | 110 | 52.2885 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8745 | 40.4827
CID=439743490 | -12 | 25 | 31.4773 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 30817.6328 | 0.8286 | 0.016637 | 4.0514 | 31.4773 | 127.5273 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 38.2952 | 3.6689 | 0.83217 | 110 | 57.47 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0705 | 44.884
CID=-2114214506 | -12 | 27.5 | 32.9813 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 31245.7826 | 0.83968 | 0.017571 | 3.8313 | 32.9813 | 126.3619 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 40.2607 | 3.9544 | 0.83767 | 110 | 59.8207 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8318 | 45.1309
CID=-2013457957 | -12 | 30 | 34.1797 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 31663.5239 | 0.83634 | 0.018435 | 3.5981 | 34.1797 | 122.9824 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 42.4983 | 4.2564 | 0.8418 | 110 | 61.6898 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.4146 | 44.9448
CID=-991821044 | -12 | 32.5 | 35.9976 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 32193.4095 | 0.84464 | 0.019584 | 3.3691 | 35.9976 | 121.2794 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 44.9104 | 4.5754 | 0.84768 | 110 | 64.5202 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.064 | 44.9312
CID=594465873 | -12 | 35 | 38.0084 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 32739.1116 | 0.85361 | 0.020871 | 3.1465 | 38.0084 | 119.5935 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 47.473 | 4.9121 | 0.85367 | 110 | 67.6463 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.8778 | 45.1391
CID=1259872426 | -12 | 37.5 | 40.2586 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 33281.12 | 0.86516 | 0.022326 | 2.9355 | 40.2586 | 118.179 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 50.1318 | 5.2671 | 0.85979 | 109.3271 | 71.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 9.725 | 35.0704 | 45.4468
CID=1360628975 | -12 | 40 | 43.3106 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 33790.8619 | 0.67548 | 0.023397 | 2.1712 | 41.3982 | 89.8843 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 63.413 | 5.6411 | 0.86267 | 95.3718 | 72.911 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.392 | 45.2292
CID=-1912701408 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326414491 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=338992062 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439748611 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114213481 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013456932 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991820019 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594466898 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1259873451 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360630000 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912700383 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326413466 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=338993087 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439749636 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114216552 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013460003 | -9 | 2.5 | 6.6692 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 19236.5003 | 0.39096 | 0.0068401 | 10.9003 | 6.6692 | 72.6956 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 12.755 | 1.5462 | 0.66477 | 110 | 15.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.3612 | 8.9771
CID=-991823090 | -9 | 5 | 8.1654 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 20599.5458 | 0.43259 | 0.0072567 | 9.6782 | 8.1654 | 79.0266 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 15.4957 | 1.6906 | 0.68067 | 110 | 18.2262 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5803 | 11.7505
CID=594463827 | -9 | 7.5 | 10.1618 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 22033.0626 | 0.48853 | 0.0078853 | 8.625 | 10.1618 | 87.6457 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 18.3355 | 1.8452 | 0.70036 | 110 | 22.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6398 | 14.6838
CID=1259870380 | -9 | 10 | 12.3601 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 23366.9016 | 0.54361 | 0.0086475 | 7.7457 | 12.3601 | 95.7381 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 21.1041 | 2.0103 | 0.72017 | 110 | 26.0761 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.707 | 18.0132
CID=1360626929 | -9 | 12.5 | 14.3001 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 24400.3758 | 0.58424 | 0.0093919 | 7.0601 | 14.3001 | 100.9606 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 23.5865 | 2.1865 | 0.73616 | 110 | 29.5134 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7039 | 20.8962
CID=-1912703454 | -9 | 15 | 17.0781 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 25609.7064 | 0.64333 | 0.010445 | 6.3844 | 17.0781 | 109.0332 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 26.4257 | 2.3743 | 0.75686 | 110 | 34.283 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2107 | 24.9456
CID=-326416537 | -9 | 17.5 | 20.0625 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 26766.2313 | 0.70083 | 0.011626 | 5.8037 | 20.0625 | 116.436 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 29.2417 | 2.5741 | 0.77651 | 110 | 39.2548 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7125 | 29.4124
CID=338990016 | -9 | 20 | 23.3974 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 27874.0912 | 0.76041 | 0.012986 | 5.2903 | 23.3974 | 123.779 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 32.1006 | 2.7864 | 0.79568 | 110 | 44.677 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5811 | 34.2136
CID=439746565 | -9 | 22.5 | 26.0225 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 28644.7838 | 0.79903 | 0.014168 | 4.8945 | 26.0225 | 127.3663 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 34.5847 | 3.0118 | 0.80895 | 110 | 48.8745 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.2865 | 37.7584
CID=-2114215527 | -9 | 25 | 29.5425 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 29549.8185 | 0.85251 | 0.015725 | 4.5017 | 29.5425 | 132.9927 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 37.3606 | 3.2507 | 0.82455 | 110 | 54.4361 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.365 | 42.7201
CID=-2013458978 | -9 | 27.5 | 33.1301 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 30391.2254 | 0.90116 | 0.017384 | 4.1504 | 33.1301 | 137.5016 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 40.1454 | 3.5036 | 0.83819 | 110 | 60.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.8057 | 47.4545
CID=-991822065 | -9 | 30 | 36.0362 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 31033.6297 | 0.93603 | 0.018869 | 3.874 | 36.0362 | 139.603 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 42.5681 | 3.7712 | 0.8478 | 110 | 64.5802 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4049 | 50.6676
CID=594464852 | -9 | 32.5 | 37.7765 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 31473.9565 | 0.94816 | 0.019984 | 3.6565 | 37.7765 | 138.1303 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 44.6209 | 4.0538 | 0.85301 | 110 | 67.2859 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.4891 | 51.064
CID=1259871405 | -9 | 35 | 39.0648 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 31877.104 | 0.94344 | 0.020978 | 3.4342 | 39.0648 | 134.156 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 46.8728 | 4.3522 | 0.85662 | 110 | 69.2873 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.363 | 50.7666
CID=1360627954 | -9 | 37.5 | 40.8774 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 32369.0448 | 0.94848 | 0.022238 | 3.2181 | 40.8774 | 131.5459 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 49.2616 | 4.6667 | 0.86137 | 110 | 72.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5427 | 50.2122
CID=-1912702429 | -9 | 40 | 43.3355 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 32918.127 | 0.96389 | 0.023835 | 3.0063 | 43.3355 | 130.2807 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 51.8212 | 4.9981 | 0.86725 | 110 | 75.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.6622 | 51.0088
CID=-326415512 | -9 | 42.5 | 45.777 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 33436.2724 | 0.97542 | 0.025517 | 2.8043 | 45.777 | 128.3702 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 54.4805 | 5.3467 | 0.87251 | 109.2261 | 79.7136 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.6387 | 50.9152
CID=338991041 | -9 | 45 | 48.7127 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 33977.0399 | 1.0043 | 0.027513 | 2.6395 | 48.7127 | 128.5775 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.8269 | 5.7134 | 0.87814 | 108.973 | 84.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=439747590 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114226806 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013470257 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991833344 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594453573 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1259860126 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360616675 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912713708 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326426791 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=338979762 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439736311 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114225781 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013469232 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991832319 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594454598 | -6 | 5 | 5.6259 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18461.2591 | 0.36214 | 0.0067615 | 11.8938 | 5.6259 | 66.9129 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 13.7337 | 1.5026 | 0.65306 | 88.3144 | 13.0886 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=1259861151 | -6 | 7.5 | 8.4197 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 20165.1234 | 0.46787 | 0.0073623 | 10.0854 | 8.4197 | 84.916 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 17.6507 | 1.64 | 0.68327 | 110 | 18.7221 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.779 | 12.0604
CID=1360617700 | -6 | 10 | 10.4404 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 21560.1712 | 0.52331 | 0.0080132 | 8.9322 | 10.4404 | 93.256 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 20.4844 | 1.7868 | 0.70298 | 110 | 22.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7257 | 15.1552
CID=-1912712683 | -6 | 12.5 | 12.7268 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 22878.6268 | 0.58301 | 0.0088145 | 8.012 | 12.7268 | 101.9665 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 23.1923 | 1.9434 | 0.7233 | 110 | 26.7336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8046 | 18.649
CID=-326425766 | -6 | 15 | 15.3455 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 24143.069 | 0.64623 | 0.0097802 | 7.2251 | 15.3455 | 110.8733 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 25.9036 | 2.1103 | 0.74425 | 110 | 31.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.1409 | 22.5502
CID=338980787 | -6 | 17.5 | 17.6523 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 25127.6655 | 0.69134 | 0.010706 | 6.5885 | 17.6523 | 116.303 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 28.42 | 2.2879 | 0.76084 | 110 | 35.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4617 | 25.8429
CID=439737336 | -6 | 20 | 20.9061 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 26287.5821 | 0.75775 | 0.011994 | 5.9757 | 20.9061 | 124.9279 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 31.2259 | 2.4766 | 0.78162 | 110 | 40.638 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.2332 | 30.5791
CID=-516701907 | -6 | 22.5 | 24.2481 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 27361.6229 | 0.81865 | 0.01338 | 5.4521 | 24.2481 | 132.2031 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 33.9782 | 2.6769 | 0.80015 | 110 | 46.043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9502 | 35.5459
CID=787260008 | -6 | 25 | 27.627 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 28299.1953 | 0.87448 | 0.014847 | 5.004 | 27.627 | 138.2463 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 36.66 | 2.8892 | 0.81635 | 110 | 51.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7519 | 40.5021
CID=1170341559 | -6 | 27.5 | 30.8297 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 29088.679 | 0.92189 | 0.016322 | 4.6251 | 30.8297 | 142.5891 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 39.2129 | 3.1141 | 0.82969 | 110 | 56.4559 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9384 | 44.721
CID=-1820663822 | -6 | 30 | 34.7994 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 29965.3974 | 0.978 | 0.018153 | 4.2502 | 34.7994 | 147.9031 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 42.0431 | 3.3519 | 0.84386 | 110 | 62.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.4722 | 50.1265
CID=-1437582271 | -6 | 32.5 | 38.704 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 30735.2357 | 1.0316 | 0.020051 | 3.9387 | 38.704 | 152.4422 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 44.6806 | 3.6031 | 0.85563 | 110 | 68.7268 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.148 | 55.2599
CID=-133620356 | -6 | 35 | 40.8591 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 31199.2669 | 1.0505 | 0.021369 | 3.7098 | 40.8591 | 151.5795 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 46.7909 | 3.8682 | 0.86133 | 110 | 72.0738 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0822 | 56.636
CID=249461195 | -6 | 37.5 | 42.5045 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 31605.995 | 1.0549 | 0.022554 | 3.494 | 42.5045 | 148.5124 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 48.9281 | 4.1478 | 0.86533 | 110 | 74.629 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0639 | 56.9451
CID=1553423110 | -6 | 40 | 44.2466 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 32040.2636 | 1.0569 | 0.023844 | 3.2784 | 44.2466 | 145.059 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 51.2352 | 4.4423 | 0.86928 | 110 | 77.3351 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.7052 | 56.788
CID=1936504661 | -6 | 42.5 | 46.495 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 32553.0612 | 1.0669 | 0.025418 | 3.0677 | 46.495 | 142.6332 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 53.6886 | 4.7522 | 0.87395 | 110 | 80.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.4168 | 56.5732
CID=-1054500720 | -6 | 45 | 48.9013 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 33045.1788 | 1.078 | 0.027153 | 2.8683 | 48.9013 | 140.2643 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 56.2111 | 5.0781 | 0.87848 | 109.8406 | 84.5755 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3282 | 40.914 | 56.8886
CID=-516700882 | -6 | 47.5 | 52.0546 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 33587.5185 | 1.1023 | 0.029323 | 2.6788 | 52.0546 | 139.4444 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 58.8238 | 5.4204 | 0.88374 | 109.2283 | 89.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.8283 | 57.2808
CID=787261033 | -6 | 50 | 54.9572 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34051.8889 | 0.88287 | 0.030801 | 2.0316 | 53.3935 | 108.4754 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 70.5466 | 5.7798 | 0.88577 | 95.3498 | 91.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=1170342584 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820662797 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437581246 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133619331 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249462220 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553424135 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936505686 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054499695 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516703953 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787257962 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170339513 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820665868 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437584317 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133622402 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249459149 | -3 | 10 | 8.8088 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 19821.8027 | 0.511 | 0.0075042 | 10.4583 | 8.8088 | 92.1242 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 19.9412 | 1.5929 | 0.6872 | 110 | 19.4754 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.3391 | 12.2784
CID=1553421064 | -3 | 12.5 | 10.7977 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 21136.4906 | 0.56562 | 0.0081662 | 9.2706 | 10.7977 | 100.1016 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 22.6357 | 1.7325 | 0.70629 | 110 | 23.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9798 | 15.6157
CID=1936502615 | -3 | 15 | 13.2146 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 22441.9641 | 0.62961 | 0.0090218 | 8.2737 | 13.2146 | 109.333 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 25.3567 | 1.8813 | 0.72738 | 110 | 27.6025 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.1813 | 19.2479
CID=-1054502766 | -3 | 17.5 | 15.8227 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 23659.5429 | 0.69257 | 0.010001 | 7.4545 | 15.8227 | 117.9506 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 27.998 | 2.0396 | 0.74781 | 110 | 32.1471 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3228 | 23.3226
CID=-516702928 | -3 | 20 | 18.1901 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 24632.977 | 0.74124 | 0.010962 | 6.8031 | 18.1901 | 123.7486 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 30.4337 | 2.2079 | 0.76448 | 110 | 36.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6291 | 26.7511
CID=787258987 | -3 | 22.5 | 21.6321 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 25793.9458 | 0.81433 | 0.012332 | 6.1575 | 21.6321 | 133.1995 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 33.2174 | 2.3864 | 0.78588 | 110 | 41.8215 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.6237 | 31.6404
CID=1170340538 | -3 | 25 | 25.1033 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 26865.4491 | 0.87944 | 0.013784 | 5.6112 | 25.1033 | 140.8598 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 35.9324 | 2.5757 | 0.80447 | 110 | 47.4106 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2655 | 36.9411
CID=-1820664843 | -3 | 27.5 | 29.0858 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 27918.9399 | 0.95011 | 0.015489 | 5.1204 | 29.0858 | 148.9312 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 38.7267 | 2.7762 | 0.82266 | 110 | 53.7179 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.5311 | 42.6405
CID=-1437583292 | -3 | 30 | 32.1107 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 28633.6872 | 0.99403 | 0.016931 | 4.746 | 32.1107 | 152.396 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 41.1405 | 2.9882 | 0.83453 | 110 | 58.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4826 | 46.7387
CID=-133621377 | -3 | 32.5 | 36.2985 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 29499.7156 | 1.0584 | 0.018878 | 4.3692 | 36.2985 | 158.5955 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 43.8546 | 3.2122 | 0.84861 | 110 | 64.9882 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0462 | 52.5507
CID=249460174 | -3 | 35 | 40.5112 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 30304.1927 | 1.1149 | 0.020933 | 4.028 | 40.5112 | 163.1779 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 46.604 | 3.4485 | 0.86044 | 110 | 71.5336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9114 | 58.111
CID=1553422089 | -3 | 37.5 | 44.4675 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 30989.9366 | 1.1663 | 0.022994 | 3.7468 | 44.4675 | 166.611 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 49.1296 | 3.6978 | 0.86976 | 110 | 77.6783 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.5999 | 63.3351
CID=1936503640 | -3 | 40 | 46.3252 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 31369.0493 | 1.1794 | 0.024322 | 3.5471 | 46.3252 | 164.322 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 51.0799 | 3.9603 | 0.87362 | 110 | 80.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1961 | 63.4544
CID=-1054501741 | -3 | 42.5 | 47.7208 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 31730.7959 | 1.1721 | 0.025534 | 3.3349 | 47.7208 | 159.1437 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 53.2863 | 4.2366 | 0.87632 | 110 | 82.7375 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.3922 | 63.0494
CID=-516697807 | -3 | 45 | 49.9245 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 32191.0141 | 1.1807 | 0.027159 | 3.1262 | 49.9245 | 156.0745 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 55.6416 | 4.5271 | 0.88027 | 110 | 86.1698 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.8219 | 63.027
CID=787264108 | -3 | 47.5 | 52.6223 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 32710.3176 | 1.1955 | 0.029096 | 2.9212 | 52.6223 | 153.7215 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 58.1527 | 4.8323 | 0.88462 | 110 | 90.3794 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.7507 | 63.4939
CID=1170345659 | -3 | 50 | 55.2169 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 33176.8625 | 1.2073 | 0.031106 | 2.7319 | 55.2169 | 150.8466 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 60.6659 | 5.1527 | 0.88835 | 109.7429 | 94.437 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0608 | 46.6377 | 63.7961
CID=-1820659722 | -3 | 52.5 | 58.585 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 33690.8979 | 1.2337 | 0.033603 | 2.5539 | 58.585 | 149.6195 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 63.2299 | 5.4887 | 0.89262 | 109.1715 | 99.7185 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.5574 | 63.6127
CID=-1437578171 | -3 | 55 | 60.752 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34145.4634 | 0.99406 | 0.035397 | 1.9438 | 60.1317 | 116.8839 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 74.5757 | 5.841 | 0.89438 | 97.0873 | 102.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=-133616256 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249465295 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553427210 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936508761 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054496620 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516696782 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787265133 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170346684 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820658697 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437577146 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133615231 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249466320 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553428235 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936509786 | 0 | 12.5 | 9.4288 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 19616.8232 | 0.56627 | 0.0077106 | 10.7532 | 9.4288 | 101.3897 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 22.4146 | 1.5491 | 0.69333 | 110 | 20.6621 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6702 | 13.1874
CID=-1054495595 | 0 | 15 | 10.9572 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 20621.0722 | 0.6012 | 0.0082687 | 9.6415 | 10.9572 | 105.6438 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 24.7486 | 1.6821 | 0.70775 | 110 | 23.5222 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.883 | 16.0314
CID=-516699853 | 0 | 17.5 | 13.5423 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 21959.5491 | 0.67324 | 0.0091864 | 8.5697 | 13.5423 | 116.0537 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 27.4709 | 1.8236 | 0.73008 | 110 | 28.1825 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2692 | 19.8154
CID=787262062 | 0 | 20 | 16.4027 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 23227.0031 | 0.74544 | 0.01026 | 7.6813 | 16.4027 | 125.9944 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 30.1553 | 1.9741 | 0.75206 | 110 | 33.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.7353 | 24.0702
CID=1170343613 | 0 | 22.5 | 19.1093 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 24268.7522 | 0.80521 | 0.011349 | 6.9796 | 19.1093 | 133.3751 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 32.6443 | 2.1337 | 0.77051 | 110 | 37.681 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1199 | 28.0987
CID=-1820661768 | 0 | 25 | 22.2093 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 25298.4136 | 0.8682 | 0.012628 | 6.3423 | 22.2093 | 140.858 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 35.246 | 2.303 | 0.78916 | 110 | 42.7586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7385 | 32.6801
CID=-1437580217 | 0 | 27.5 | 26.149 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 26412.4265 | 0.94821 | 0.014264 | 5.7592 | 26.149 | 150.5971 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 37.9982 | 2.4822 | 0.80955 | 110 | 49.0756 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9765 | 38.3214
CID=-133618302 | 0 | 30 | 30.0534 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 27413.8596 | 1.0187 | 0.01597 | 5.2671 | 30.0534 | 158.2933 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 40.6645 | 2.6717 | 0.82662 | 110 | 55.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9309 | 44.1758
CID=249463249 | 0 | 32.5 | 34.1152 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 28317.0528 | 1.0861 | 0.01782 | 4.8368 | 34.1152 | 165.0074 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 43.3126 | 2.872 | 0.84159 | 110 | 61.5892 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0018 | 50.2286
CID=1553425164 | 0 | 35 | 37.7607 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 29049.7535 | 1.139 | 0.019607 | 4.4773 | 37.7607 | 169.0656 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 45.803 | 3.0833 | 0.85296 | 110 | 67.2613 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6907 | 54.8307
CID=1936506715 | 0 | 37.5 | 42.4438 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 29881.0692 | 1.207 | 0.021885 | 4.1214 | 42.4437 | 174.9297 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 48.5489 | 3.3062 | 0.86519 | 110 | 74.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6252 | 61.2623
CID=-1054498666 | 0 | 40 | 46.826 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 30601.0465 | 1.2655 | 0.024164 | 3.8214 | 46.826 | 178.9391 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 51.1384 | 3.5409 | 0.8746 | 110 | 81.3451 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4682 | 67.1838
CID=-516698828 | 0 | 42.5 | 50.1887 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 31141.5435 | 1.303 | 0.026152 | 3.5787 | 50.1887 | 179.6107 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 53.4464 | 3.7879 | 0.88072 | 110 | 86.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9202 | 70.4572
CID=787263087 | 0 | 45 | 52.4038 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 31541.9144 | 1.3184 | 0.027774 | 3.3778 | 52.4038 | 177.0108 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 55.5181 | 4.0477 | 0.88428 | 110 | 90.0382 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7902 | 71.0175
CID=1170344638 | 0 | 47.5 | 53.9572 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 31899.5848 | 1.3108 | 0.029207 | 3.174 | 53.9572 | 171.262 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 57.7592 | 4.3205 | 0.88659 | 110 | 92.4659 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3283 | 70.5862
CID=-1820660743 | 0 | 50 | 56.3558 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 32353.0018 | 1.3199 | 0.031101 | 2.9749 | 56.3558 | 167.6548 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 60.129 | 4.607 | 0.88987 | 110 | 96.221 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.4342 | 70.2774
CID=-1437579192 | 0 | 52.5 | 59.2677 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 32840.6873 | 1.3353 | 0.033349 | 2.779 | 59.2677 | 164.7067 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 62.6511 | 4.9075 | 0.89341 | 110 | 100.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.5636 | 70.9719
CID=-133617277 | 0 | 55 | 62.0489 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 33286.8057 | 1.3462 | 0.035683 | 2.596 | 62.0489 | 161.0769 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 65.1998 | 5.2224 | 0.89641 | 109.5007 | 105.1679 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1289 | 52.837 | 71.2608
CID=249464274 | 0 | 57.5 | 65.9349 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 33793.3116 | 1.3826 | 0.038711 | 2.4308 | 65.9349 | 160.2737 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 67.6922 | 5.5522 | 0.90004 | 109.1806 | 111.3036 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.8149 | 71.0549
CID=1553426189 | 0 | 60 | 67.9128 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34214.8219 | 1.1117 | 0.040731 | 1.8506 | 67.3745 | 124.6825 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 78.7718 | 5.8975 | 0.90124 | 97.0873 | 113.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=1936507740 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054497641 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516710107 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787251808 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170333359 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820672022 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437590471 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133628556 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249452995 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553414910 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936496461 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054508920 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516709082 | 3 | 15 | 7.9121 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 18683.6109 | 0.52738 | 0.0073993 | 11.8501 | 7.9121 | 93.7596 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 23.4771 | 1.5081 | 0.67805 | 89.9521 | 17.7291 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=787252833 | 3 | 17.5 | 11.262 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 20197.5837 | 0.64599 | 0.0084152 | 10.006 | 11.262 | 112.6879 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 26.9497 | 1.635 | 0.71051 | 110 | 24.0825 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1159 | 16.4081
CID=1170334384 | 3 | 20 | 13.9143 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 21519.8504 | 0.71916 | 0.0093691 | 8.8424 | 13.9143 | 123.0355 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 29.687 | 1.7699 | 0.73309 | 110 | 28.8377 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.4444 | 20.3842
CID=-1820670997 | 3 | 22.5 | 16.8519 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 22754.8874 | 0.79549 | 0.010484 | 7.9163 | 16.8519 | 133.4045 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 32.3238 | 1.9131 | 0.75527 | 110 | 33.9003 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.8813 | 24.8225
CID=-1437589446 | 3 | 25 | 20.0193 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 23906.8686 | 0.87176 | 0.011742 | 7.1548 | 20.0193 | 143.2332 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 34.8878 | 2.0648 | 0.77624 | 110 | 39.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.3039 | 29.7346
CID=-133627531 | 3 | 27.5 | 22.9518 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 24842.5966 | 0.93135 | 0.012987 | 6.5284 | 22.9518 | 149.8387 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 37.3308 | 2.2255 | 0.79327 | 110 | 43.959 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.151 | 33.7526
CID=249454020 | 3 | 30 | 26.9399 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 25910.3476 | 1.0145 | 0.014666 | 5.9289 | 26.9399 | 159.7231 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 40.0128 | 2.3954 | 0.81325 | 110 | 50.3303 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.3139 | 39.5659
CID=1553415935 | 3 | 32.5 | 31.0186 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 26921.74 | 1.0902 | 0.016463 | 5.412 | 31.0186 | 167.8726 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 42.6692 | 2.575 | 0.83042 | 110 | 56.7519 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.265 | 45.7721
CID=1936497486 | 3 | 35 | 35.7127 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 27924.4953 | 1.1733 | 0.018579 | 4.9445 | 35.7127 | 176.5815 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 45.4102 | 2.7645 | 0.84679 | 110 | 64.0769 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.9753 | 52.4501
CID=-1054507895 | 3 | 37.5 | 39.2041 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 28595.9089 | 1.2237 | 0.020347 | 4.5883 | 39.2041 | 179.8783 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 47.7868 | 2.9643 | 0.857 | 110 | 69.5036 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.2782 | 57.13
CID=1453958216 | 3 | 40 | 44.0722 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 29417.8707 | 1.299 | 0.022743 | 4.2285 | 44.0722 | 186.3602 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 50.4461 | 3.1747 | 0.8689 | 110 | 77.0642 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.2945 | 63.85
CID=1554714765 | 3 | 42.5 | 48.8713 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 30175.6267 | 1.3625 | 0.02524 | 3.9004 | 48.8713 | 190.618 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 53.1497 | 3.3962 | 0.87843 | 110 | 84.5287 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2941 | 70.4485
CID=-1153965614 | 3 | 45 | 53.8177 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 30867.5149 | 1.43 | 0.027935 | 3.6223 | 53.8177 | 194.9441 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 55.7101 | 3.6291 | 0.88639 | 110 | 92.2477 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.628 | 77.0074
CID=432321303 | 3 | 47.5 | 56.2443 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 31256.4923 | 1.4486 | 0.029719 | 3.4182 | 56.2443 | 192.256 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 57.7783 | 3.8738 | 0.88972 | 110 | 96.0462 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4646 | 78.0241
CID=533077852 | 3 | 50 | 58.3572 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 31628.1725 | 1.4553 | 0.031474 | 3.2191 | 58.3572 | 187.8555 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 59.9374 | 4.1306 | 0.89235 | 110 | 99.3606 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3198 | 78.3946
CID=633834401 | 3 | 52.5 | 60.4161 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 32010.2156 | 1.4552 | 0.033314 | 3.0207 | 60.4161 | 182.4998 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 62.2409 | 4.4 | 0.89469 | 110 | 102.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.5765 | 78.2557
CID=-2074845978 | 3 | 55 | 62.908 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 32445.7176 | 1.4625 | 0.035474 | 2.8296 | 62.908 | 178.0057 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 64.6346 | 4.6823 | 0.89727 | 110 | 106.5224 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3691 | 77.4469
CID=-488559061 | 3 | 57.5 | 66.1352 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 32919.1489 | 1.4808 | 0.03813 | 2.6417 | 66.1352 | 174.7078 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 67.1747 | 4.9781 | 0.90021 | 110 | 111.6206 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.8459 | 78.4246
CID=-387802512 | 3 | 60 | 69.1614 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 33353.5073 | 1.4914 | 0.040874 | 2.4631 | 69.1614 | 170.3489 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 69.778 | 5.2877 | 0.90263 | 109.3285 | 116.4158 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 59.7005 | 78.6223
CID=-287045963 | 3 | 62.5 | 73.194 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 33681.8935 | 1.1962 | 0.042237 | 1.9122 | 69.075 | 132.0841 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 79.5947 | 5.6115 | 0.90256 | 98.2763 | 116.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.5754 | 77.8125
CID=1453959241 | 3 | 65 | 75.5873 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34259.8998 | 1.2377 | 0.04694 | 1.7561 | 75.117 | 131.9149 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 83.0361 | 5.95 | 0.90655 | 97.0873 | 125.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=1554715790 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153964589 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432322328 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533078877 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=633835426 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074844953 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488558036 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387801487 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-287044938 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1453956170 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554712719 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153967660 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432319257 | 6 | 20 | 11.7553 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 19866.6283 | 0.70174 | 0.0086205 | 10.3352 | 11.7553 | 121.494 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 29.2698 | 1.5911 | 0.71491 | 110 | 24.9828 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8403 | 16.6703
CID=533075806 | 6 | 22.5 | 14.3386 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 21105.9685 | 0.77238 | 0.0095728 | 9.1442 | 14.3386 | 131.1142 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 31.893 | 1.7198 | 0.73647 | 110 | 29.5806 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7456 | 20.9315
CID=633832355 | 6 | 25 | 17.432 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 22331.6662 | 0.85514 | 0.010756 | 8.1607 | 17.432 | 142.2568 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 34.5213 | 1.8563 | 0.75933 | 110 | 34.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3478 | 25.5163
CID=-2074848024 | 6 | 27.5 | 20.7277 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 23476.3686 | 0.93503 | 0.012077 | 7.3501 | 20.7277 | 152.3499 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 37.0947 | 2.0007 | 0.78056 | 110 | 40.3461 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.8391 | 30.6162
CID=-488561107 | 6 | 30 | 23.606 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 24374.124 | 0.99439 | 0.013325 | 6.7186 | 23.606 | 158.6 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 39.4469 | 2.1535 | 0.79679 | 110 | 45.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4236 | 34.7884
CID=-387804558 | 6 | 32.5 | 27.5893 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 25418.8369 | 1.0776 | 0.015029 | 6.0946 | 27.5893 | 168.1464 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 42.092 | 2.3149 | 0.81619 | 110 | 51.3579 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.4257 | 40.7528
CID=-287048009 | 6 | 35 | 32.2355 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 26481.5296 | 1.1709 | 0.017061 | 5.5412 | 32.2355 | 178.6223 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 44.8014 | 2.4852 | 0.83499 | 110 | 58.6558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.097 | 47.374
CID=1453957195 | 6 | 37.5 | 36.7948 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 27425.3608 | 1.2534 | 0.019166 | 5.0772 | 36.7948 | 186.8133 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 47.4105 | 2.6649 | 0.85012 | 110 | 65.76 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.3967 | 54.193
CID=1554713744 | 6 | 40 | 41.5805 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 28291.7152 | 1.333 | 0.021466 | 4.665 | 41.5805 | 193.9749 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 50.0324 | 2.8541 | 0.86312 | 110 | 73.194 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.7901 | 61.371
CID=-1153966635 | 6 | 42.5 | 45.7114 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 28974.4543 | 1.3922 | 0.02363 | 4.3236 | 45.7114 | 197.64 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 52.4816 | 3.0532 | 0.87238 | 110 | 79.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0078 | 66.415
CID=432320282 | 6 | 45 | 50.9295 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 29737.0911 | 1.469 | 0.026352 | 3.9913 | 50.9295 | 203.275 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 55.12 | 3.2625 | 0.88195 | 110 | 87.737 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0513 | 73.8077
CID=533076831 | 6 | 47.5 | 56.1149 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 30444.2827 | 1.538 | 0.029213 | 3.6937 | 56.1148 | 207.2741 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 57.7474 | 3.4825 | 0.88955 | 110 | 95.8434 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5834 | 80.6463
CID=633833380 | 6 | 50 | 60.7942 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 31037.6874 | 1.5963 | 0.032023 | 3.4432 | 60.7942 | 209.326 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 60.2018 | 3.7134 | 0.8951 | 110 | 103.1919 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.1297 | 86.4588
CID=-2074846999 | 6 | 52.5 | 63.0553 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 31376.5629 | 1.6118 | 0.033939 | 3.2581 | 63.0553 | 205.4409 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 62.2012 | 3.9556 | 0.89741 | 110 | 106.7547 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.549 | 86.5615
CID=-488560082 | 6 | 55 | 64.6553 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 31689.0726 | 1.6004 | 0.035678 | 3.0637 | 64.6553 | 198.0814 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 64.4179 | 4.2094 | 0.89891 | 110 | 109.2807 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.4253 | 85.8853
CID=-387803533 | 6 | 57.5 | 67.5307 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 32116.6246 | 1.6141 | 0.038131 | 2.869 | 67.5307 | 193.7458 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 66.8025 | 4.4753 | 0.90136 | 110 | 113.8301 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.4863 | 86.5751
CID=-287046984 | 6 | 60 | 70.372 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 32550.2395 | 1.6244 | 0.040737 | 2.6839 | 70.372 | 188.8708 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 69.2438 | 4.7536 | 0.90351 | 110 | 118.338 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7344 | 86.0097
CID=1453962316 | 6 | 62.5 | 73.8095 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 32997.7492 | 1.6441 | 0.043829 | 2.5053 | 73.8095 | 184.9136 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 71.7791 | 5.0447 | 0.90577 | 110 | 123.808 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.5946 | 87.0244
CID=1554718865 | 6 | 65 | 77.1684 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 33421.8558 | 1.6569 | 0.047114 | 2.3324 | 77.1684 | 179.9885 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 74.4144 | 5.349 | 0.90769 | 109.3262 | 129.1693 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7118 | 67.1624 | 87.1744
CID=-1153961514 | 6 | 67.5 | 81.4893 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 33761.0786 | 1.2926 | 0.048822 | 1.7562 | 77.0983 | 135.3988 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 85.2725 | 5.667 | 0.90765 | 95.9768 | 129.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.7476 | 86.2309
CID=432325403 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533081952 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=633838501 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074841878 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488554961 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387798412 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-287041863 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1453963341 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554719890 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153960489 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432326428 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533082977 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=633839526 | 9 | 22.5 | 12.4807 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 19635.5265 | 0.76938 | 0.0089007 | 10.5902 | 12.4807 | 132.1727 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 31.7403 | 1.5501 | 0.7212 | 110 | 26.2927 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3644 | 17.597
CID=-2074840853 | 9 | 25 | 14.4973 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 20601.6446 | 0.81654 | 0.0096995 | 9.4845 | 14.4973 | 137.4991 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 34.0548 | 1.6731 | 0.73772 | 110 | 29.8575 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5779 | 21.4167
CID=-488553936 | 9 | 27.5 | 17.7615 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 21854.4188 | 0.90673 | 0.010953 | 8.4219 | 17.7615 | 149.5863 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 36.7079 | 1.8033 | 0.76159 | 110 | 35.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3386 | 26.1844
CID=-387797387 | 9 | 30 | 21.2752 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 23025.0261 | 0.996 | 0.012367 | 7.5622 | 21.2752 | 160.888 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 39.2872 | 1.941 | 0.7838 | 110 | 41.2404 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.0478 | 31.5026
CID=-287040838 | 9 | 32.5 | 25.1653 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 24128.7187 | 1.0887 | 0.013988 | 6.8385 | 25.1653 | 172.0935 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 41.8467 | 2.0864 | 0.80478 | 110 | 47.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9917 | 37.3388
CID=1453960270 | 9 | 35 | 28.5075 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 24984.7554 | 1.1539 | 0.015498 | 6.2573 | 28.5075 | 178.3815 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 44.2378 | 2.24 | 0.8202 | 110 | 52.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.0271 | 41.988
CID=1554716819 | 9 | 37.5 | 33.1232 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 25980.5509 | 1.2492 | 0.017554 | 5.6977 | 33.1232 | 188.7264 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 46.8543 | 2.4019 | 0.83817 | 110 | 60.0421 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4302 | 48.8161
CID=-1153963560 | 9 | 40 | 37.8665 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 26936.4277 | 1.3368 | 0.019764 | 5.209 | 37.8665 | 197.2447 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 49.4691 | 2.5724 | 0.85327 | 110 | 67.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.739 | 55.9939
CID=432323357 | 9 | 42.5 | 43.3335 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 27891.1052 | 1.4336 | 0.022372 | 4.7639 | 43.3335 | 206.4353 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 52.1722 | 2.7519 | 0.86725 | 110 | 75.9166 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9419 | 63.7251
CID=533079906 | 9 | 45 | 47.3153 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 28521.979 | 1.491 | 0.024528 | 4.4246 | 47.3153 | 209.3533 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 54.5287 | 2.9406 | 0.87555 | 110 | 82.1064 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6277 | 69.0029
CID=633836455 | 9 | 47.5 | 52.7778 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 29286.9903 | 1.5751 | 0.027411 | 4.0827 | 52.7778 | 215.4784 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 57.1385 | 3.1388 | 0.88485 | 110 | 90.6223 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.871 | 76.6845
CID=-2074843924 | 9 | 50 | 58.4356 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 30023.1758 | 1.6521 | 0.03054 | 3.7649 | 58.4356 | 220.0044 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 59.8322 | 3.3469 | 0.89244 | 110 | 99.4837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.4252 | 84.4459
CID=-488557007 | 9 | 52.5 | 63.185 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 30601.8388 | 1.7133 | 0.033461 | 3.5115 | 63.185 | 221.8762 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 62.2411 | 3.5652 | 0.89753 | 110 | 106.9594 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2376 | 90.1325
CID=-387800458 | 9 | 55 | 65.288 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 30921.6187 | 1.7196 | 0.035382 | 3.3136 | 65.288 | 216.3369 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 64.3161 | 3.794 | 0.89948 | 110 | 110.2806 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.4435 | 90.1325
CID=-287043909 | 9 | 57.5 | 67.6521 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 31255.6477 | 1.7283 | 0.03755 | 3.1187 | 67.6521 | 210.9859 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 66.4975 | 4.0336 | 0.90146 | 110 | 114.0225 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.1717 | 90.1326
CID=1453961295 | 9 | 60 | 69.7051 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 31587.4553 | 1.7212 | 0.039719 | 2.9214 | 69.7051 | 203.6379 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 68.8459 | 4.2845 | 0.90303 | 110 | 117.2789 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2777 | 90.1326
CID=1554717844 | 9 | 62.5 | 72.616 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 32015.508 | 1.7315 | 0.042464 | 2.7305 | 72.616 | 198.2747 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 71.293 | 4.5468 | 0.90502 | 110 | 121.9068 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.0994 | 90.1325
CID=-1153962535 | 9 | 65 | 75.8421 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 32457.0325 | 1.7448 | 0.045573 | 2.546 | 75.8421 | 193.0957 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 73.8333 | 4.8211 | 0.90696 | 110 | 127.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5516 | 90.1325
CID=432324382 | 9 | 67.5 | 78.9707 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 32870.4675 | 1.7523 | 0.048874 | 2.3696 | 78.9707 | 187.1303 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 76.4441 | 5.1077 | 0.9086 | 109.2655 | 132.0525 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.8089 | 90.1325
CID=533080931 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=633837480 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074842899 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488555982 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387799433 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-287042884 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1453950016 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554706565 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153973814 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432313103 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533069652 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=633826201 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074854178 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488567261 | 12 | 25 | 11.1742 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 18522.6761 | 0.7525 | 0.0085885 | 11.4764 | 11.1742 | 128.2395 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 33.2537 | 1.5117 | 0.70972 | 109.8308 | 23.9215 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1013 | 7.9035 | 14.4449
CID=-387810712 | 12 | 27.5 | 14.8327 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 20180.9085 | 0.87177 | 0.0098859 | 9.8152 | 14.8327 | 145.5858 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 36.2948 | 1.6293 | 0.74033 | 110 | 30.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.806 | 21.8594
CID=-287054163 | 12 | 30 | 18.2206 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 21434.0667 | 0.96649 | 0.011199 | 8.6759 | 18.2206 | 158.0792 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 38.9582 | 1.7537 | 0.76468 | 110 | 36.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6007 | 26.8405
CID=1453951041 | 12 | 32.5 | 21.8991 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 22591.1716 | 1.0626 | 0.012691 | 7.7686 | 21.8991 | 170.1255 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 41.535 | 1.8852 | 0.78741 | 110 | 42.2555 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4509 | 32.3474
CID=1554707590 | 12 | 35 | 25.8039 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 23667.0866 | 1.1572 | 0.014343 | 7.0235 | 25.8039 | 181.2327 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 44.047 | 2.0239 | 0.8079 | 110 | 48.5269 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2216 | 38.3861
CID=-1153972789 | 12 | 37.5 | 29.1444 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 24500.0253 | 1.2249 | 0.015878 | 6.4352 | 29.1444 | 187.5495 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 46.3698 | 2.1702 | 0.8229 | 110 | 53.8101 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1077 | 43.1811
CID=432314128 | 12 | 40 | 33.9058 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 25500.4753 | 1.325 | 0.018021 | 5.8453 | 33.9058 | 198.1907 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 48.9911 | 2.3243 | 0.84088 | 110 | 61.2628 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6528 | 50.1588
CID=533070677 | 12 | 42.5 | 39.2545 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 26505.2248 | 1.4307 | 0.020502 | 5.3219 | 39.2545 | 208.9098 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 51.6645 | 2.4864 | 0.85713 | 110 | 69.5819 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6832 | 57.8258
CID=633827226 | 12 | 45 | 44.5246 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 27396.6263 | 1.5264 | 0.023084 | 4.8832 | 44.5246 | 217.4246 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 54.2389 | 2.6569 | 0.86988 | 110 | 77.7671 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3728 | 65.6764
CID=-2074853153 | 12 | 47.5 | 50.0522 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 28223.0156 | 1.6185 | 0.025911 | 4.4893 | 50.0522 | 224.6975 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 56.844 | 2.836 | 0.88048 | 110 | 86.3689 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.1625 | 73.9419
CID=-488566236 | 12 | 50 | 54.667 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 28854.4077 | 1.6845 | 0.02852 | 4.1659 | 54.667 | 227.7361 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 59.2627 | 3.0241 | 0.8876 | 110 | 93.5762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.7952 | 79.5389
CID=-387809687 | 12 | 52.5 | 60.5158 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 29566.5095 | 1.7719 | 0.031808 | 3.8511 | 60.5158 | 233.0536 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 61.8499 | 3.2213 | 0.8948 | 110 | 102.7537 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.0954 | 87.9361
CID=-287053138 | 12 | 55 | 63.7286 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 30008.7504 | 1.798 | 0.034137 | 3.6065 | 63.7286 | 229.8381 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 64.1061 | 3.428 | 0.89805 | 110 | 107.8173 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3247 | 90.1325
CID=-1599722741 | 12 | 57.5 | 65.6206 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 30309.4971 | 1.7991 | 0.036019 | 3.4024 | 65.6206 | 223.2707 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 66.1773 | 3.6445 | 0.89977 | 110 | 110.8065 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.1087 | 90.1325
CID=-295760826 | 12 | 60 | 68.0357 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 30654.8685 | 1.8029 | 0.038272 | 3.1887 | 68.0357 | 216.9474 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 68.47 | 3.8712 | 0.90176 | 110 | 114.6305 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.939 | 90.1325
CID=-477329279 | 12 | 62.5 | 70.491 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 31003.0067 | 1.8017 | 0.040702 | 2.9785 | 70.491 | 209.9578 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 70.8873 | 4.1083 | 0.90359 | 110 | 118.5271 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8496 | 90.1325
CID=826632636 | 12 | 65 | 72.903 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 31343.4347 | 1.801 | 0.04329 | 2.784 | 72.903 | 202.9627 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 73.3078 | 4.3561 | 0.90521 | 110 | 122.3638 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.6734 | 90.1325
CID=-678842377 | 12 | 67.5 | 76.1654 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 31819.1781 | 1.8132 | 0.046517 | 2.5904 | 76.1655 | 197.2981 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 75.8871 | 4.615 | 0.90714 | 110 | 127.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.1983 | 90.1326
CID=625119538 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443551085 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747513000 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853483827 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137521554 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599721716 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295759801 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477328254 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826633661 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678841352 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625120563 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443552110 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747514025 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853484852 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137520529 | 15 | 27.5 | 9.569 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18440.5609 | 0.70677 | 0.0082065 | 12.4831 | 9.569 | 119.4511 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 34.7836 | 1.4757 | 0.69469 | 77.8765 | 20.9282 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=-1599724787 | 15 | 30 | 15.43 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 19856.3173 | 0.94242 | 0.010162 | 10.1126 | 15.43 | 156.0369 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 38.6385 | 1.5883 | 0.74488 | 110 | 31.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.6958 | 22.1642
CID=-295762872 | 15 | 32.5 | 18.7072 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 21027.3882 | 1.0324 | 0.011461 | 8.9466 | 18.7072 | 167.3652 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 41.2149 | 1.7074 | 0.7679 | 110 | 37.0135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9438 | 27.4707
CID=-477331325 | 15 | 35 | 22.4964 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 22161.7563 | 1.134 | 0.013015 | 7.9959 | 22.4964 | 179.8795 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 43.7694 | 1.833 | 0.79077 | 110 | 43.2234 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8586 | 33.1342
CID=826630590 | 15 | 37.5 | 26.6408 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 23257.8289 | 1.237 | 0.01478 | 7.2025 | 26.6408 | 191.8793 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 46.3056 | 1.9655 | 0.81186 | 110 | 49.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9017 | 39.38
CID=-678844423 | 15 | 40 | 30.643 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 24190.3094 | 1.3259 | 0.016586 | 6.5593 | 30.643 | 200.9975 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 48.7276 | 2.1051 | 0.82896 | 110 | 56.1634 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8898 | 45.3962
CID=625117492 | 15 | 42.5 | 34.8902 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 25065.4838 | 1.4118 | 0.01858 | 5.99 | 34.8902 | 208.9904 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 51.1859 | 2.2519 | 0.84416 | 110 | 62.7965 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2373 | 51.5431
CID=443549039 | 15 | 45 | 40.2419 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 26006.7312 | 1.5225 | 0.021106 | 5.4651 | 40.2419 | 219.9253 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 53.766 | 2.4063 | 0.85975 | 110 | 71.1153 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.0094 | 59.4744
CID=1747510954 | 15 | 47.5 | 45.7316 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 26915.2576 | 1.6237 | 0.023825 | 5.0006 | 45.7316 | 228.6834 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 56.3662 | 2.5686 | 0.87242 | 110 | 79.6431 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.7775 | 67.6857
CID=853481781 | 15 | 50 | 51.9924 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 27818.8481 | 1.7349 | 0.02701 | 4.5783 | 51.9924 | 238.0391 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 59.0395 | 2.7389 | 0.88365 | 110 | 89.3957 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.453 | 76.5318
CID=-2137523600 | 15 | 52.5 | 56.4816 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 28411.7607 | 1.7994 | 0.029635 | 4.2544 | 56.4816 | 240.2976 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 61.3966 | 2.9175 | 0.89003 | 110 | 96.4181 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.551 | 82.4122
CID=-1599723762 | 15 | 55 | 62.0519 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 29077.0396 | 1.8824 | 0.032884 | 3.9389 | 62.0519 | 244.4191 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 63.9088 | 3.1047 | 0.89641 | 110 | 105.1727 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.9713 | 90.1325
CID=-295761847 | 15 | 57.5 | 64.2335 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 29413.8587 | 1.8877 | 0.034827 | 3.7062 | 64.2335 | 238.0635 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 66.0159 | 3.3008 | 0.89852 | 110 | 108.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3346 | 90.1325
CID=-477330300 | 15 | 60 | 66.1644 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 29731.6135 | 1.8853 | 0.036784 | 3.4862 | 66.1644 | 230.664 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 68.1616 | 3.5061 | 0.90024 | 110 | 111.6668 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.1963 | 90.1325
CID=826631615 | 15 | 62.5 | 68.4134 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 30062.4861 | 1.881 | 0.039028 | 3.2594 | 68.4134 | 222.986 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 70.505 | 3.7208 | 0.90206 | 110 | 115.2293 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.6943 | 90.1325
CID=-678843398 | 15 | 65 | 71.0312 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 30431.4418 | 1.8816 | 0.041615 | 3.0385 | 71.0312 | 215.8265 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 72.9599 | 3.9453 | 0.90397 | 110 | 119.3857 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.93 | 90.1325
CID=625118517 | 15 | 67.5 | 73.3249 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 30786.4934 | 1.8692 | 0.044234 | 2.8252 | 73.3249 | 207.1581 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 75.5102 | 4.1798 | 0.90547 | 109.9993 | 123.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0034 | 56.5173 | 90.1325
CID=443550064 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747511979 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853482806 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137522575 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599718641 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295756726 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477325179 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826636736 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678838277 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625123638 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443555185 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747517100 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853487927 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137517454 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599717616 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295755701 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477324154 | 18 | 32.5 | 16.2321 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 19596.1348 | 1.0231 | 0.010512 | 10.3436 | 16.2321 | 167.8973 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 41.1055 | 1.5499 | 0.75082 | 110 | 32.8469 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4876 | 22.9766
CID=826637761 | 18 | 35 | 18.8589 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 20534.9398 | 1.0869 | 0.011619 | 9.257 | 18.8589 | 174.5769 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 43.4279 | 1.664 | 0.76889 | 110 | 37.2657 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6985 | 28.0193
CID=-678837252 | 18 | 37.5 | 22.876 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 21704.788 | 1.1977 | 0.013272 | 8.2261 | 22.876 | 188.18 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 46.0274 | 1.7842 | 0.79286 | 110 | 43.8368 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8592 | 33.8929
CID=625124663 | 18 | 40 | 27.151 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 22792.8225 | 1.308 | 0.015111 | 7.3989 | 27.151 | 200.8885 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 48.5456 | 1.9109 | 0.81421 | 110 | 50.6646 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.906 | 40.396
CID=443556210 | 18 | 42.5 | 31.7646 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 23814.4137 | 1.4195 | 0.017174 | 6.7046 | 31.7646 | 212.9707 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 51.0361 | 2.0442 | 0.83325 | 110 | 57.9197 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0656 | 47.4637
CID=1747518125 | 18 | 45 | 35.7042 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 24603.1582 | 1.4981 | 0.01909 | 6.1447 | 35.7042 | 219.3918 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 53.3837 | 2.1844 | 0.84677 | 110 | 64.0636 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.496 | 52.9123
CID=853488952 | 18 | 47.5 | 41.2746 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 25551.9388 | 1.6154 | 0.021748 | 5.5903 | 41.2746 | 230.7393 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 55.9861 | 2.3317 | 0.86236 | 110 | 72.719 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.5596 | 60.9897
CID=-2137516429 | 18 | 50 | 47.2574 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 26485.8503 | 1.7316 | 0.024719 | 5.1006 | 47.2574 | 241.0405 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 58.6184 | 2.4862 | 0.87544 | 110 | 82.0162 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7665 | 69.7483
CID=-1599720687 | 18 | 52.5 | 53.2834 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 27327.8554 | 1.8417 | 0.027877 | 4.6848 | 53.2834 | 249.62 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 61.179 | 2.6484 | 0.88561 | 110 | 91.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8781 | 78.6886
CID=-295758772 | 18 | 55 | 59.5996 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 28115.6664 | 1.9473 | 0.031344 | 4.3076 | 59.5995 | 256.732 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 63.784 | 2.8184 | 0.89379 | 110 | 101.3126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.0948 | 88.1043
CID=-477327225 | 18 | 57.5 | 62.5696 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 28510.8144 | 1.9736 | 0.033556 | 4.0409 | 62.5696 | 252.8365 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 65.9287 | 2.9964 | 0.89693 | 110 | 105.9887 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0067 | 90.1325
CID=826634690 | 18 | 60 | 64.5759 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 28836.0893 | 1.9732 | 0.035477 | 3.7995 | 64.5759 | 245.3535 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 68.0468 | 3.1827 | 0.89884 | 110 | 109.1553 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.0194 | 90.1325
CID=-678840323 | 18 | 62.5 | 66.7055 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 29158.4448 | 1.9717 | 0.037587 | 3.5629 | 66.7055 | 237.6629 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 70.2679 | 3.3776 | 0.90069 | 110 | 112.5231 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.2784 | 90.1325
CID=625121592 | 18 | 65 | 69.0992 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 29505.5641 | 1.9738 | 0.039975 | 3.3336 | 69.0992 | 230.3479 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 72.5794 | 3.5814 | 0.90258 | 110 | 116.3171 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0659 | 90.1326
CID=443553139 | 18 | 67.5 | 71.5757 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 29865.4607 | 1.9599 | 0.042582 | 3.0892 | 71.5757 | 221.1128 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 75.1715 | 3.7943 | 0.90434 | 110 | 120.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.0188 | 90.1325
CID=1747515054 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853485881 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137519500 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599719662 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295757747 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477326200 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826635715 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678839298 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625122617 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443554164 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747516079 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853486906 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137518475 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599730941 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295769026 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477337479 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826624436 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678850577 | 21 | 35 | 15.4446 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 18830.6413 | 1.0416 | 0.010352 | 10.9656 | 15.4446 | 169.3591 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 43.0281 | 1.5138 | 0.74499 | 110 | 31.4979 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9152 | 20.974
CID=625111338 | 21 | 37.5 | 19.1794 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 20107.3204 | 1.1527 | 0.01184 | 9.5617 | 19.1794 | 183.3878 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 45.7002 | 1.6232 | 0.77096 | 110 | 37.7972 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.8342 | 28.5245
CID=443542885 | 21 | 40 | 23.4214 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 21298.199 | 1.2738 | 0.013597 | 8.4601 | 23.4214 | 198.1486 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 48.3179 | 1.7385 | 0.79581 | 110 | 44.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2151 | 34.6277
CID=1747504800 | 21 | 42.5 | 27.9332 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 22382.574 | 1.3938 | 0.015552 | 7.5845 | 27.9332 | 211.8599 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 50.852 | 1.8598 | 0.81771 | 110 | 51.9012 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.5417 | 41.3248
CID=853475627 | 21 | 45 | 32.6769 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 23392.8844 | 1.5106 | 0.017701 | 6.8614 | 32.6769 | 224.2108 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 53.3367 | 1.9873 | 0.83658 | 110 | 59.3454 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.752 | 48.6019
CID=-2137529754 | 21 | 47.5 | 36.6556 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 24172.1119 | 1.5928 | 0.019671 | 6.2926 | 36.6556 | 230.6611 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 55.6451 | 2.1213 | 0.8497 | 110 | 65.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0805 | 54.2307
CID=-1599729916 | 21 | 50 | 42.2061 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 25099.8983 | 1.7107 | 0.022372 | 5.7222 | 42.2061 | 241.5126 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 58.2191 | 2.2619 | 0.86463 | 110 | 74.1655 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9077 | 62.5046
CID=-295768001 | 21 | 52.5 | 48.4257 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 26001.793 | 1.8402 | 0.025498 | 5.2255 | 48.4257 | 253.0467 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 60.7985 | 2.4094 | 0.87762 | 110 | 83.8349 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.2501 | 71.6014
CID=-477336454 | 21 | 55 | 54.6412 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 26854.4792 | 1.9548 | 0.028804 | 4.7873 | 54.6412 | 261.5861 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 63.3843 | 2.564 | 0.88756 | 110 | 93.5359 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.3799 | 80.9026
CID=826625461 | 21 | 57.5 | 61.3275 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 27672.0329 | 2.0722 | 0.032511 | 4.3955 | 61.3274 | 269.5641 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 65.9946 | 2.726 | 0.89567 | 110 | 104.0314 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.5224 | 90.1325
CID=-678849552 | 21 | 60 | 63.0917 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 27969.9074 | 2.0686 | 0.034263 | 4.1417 | 63.0917 | 261.3043 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 68.0215 | 2.8955 | 0.89744 | 110 | 106.8121 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.0509 | 90.1326
CID=625112363 | 21 | 62.5 | 64.9688 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 28270.0819 | 2.0618 | 0.036185 | 3.888 | 64.9688 | 252.6019 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 70.1738 | 3.0728 | 0.89919 | 110 | 109.7761 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.8051 | 90.1326
CID=443543910 | 21 | 65 | 67.259 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 28603.4214 | 2.0613 | 0.038439 | 3.6371 | 67.259 | 244.6277 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 72.4489 | 3.2582 | 0.90114 | 110 | 113.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3855 | 90.1326
CID=1747505825 | 21 | 67.5 | 69.6876 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 28956.7473 | 2.0538 | 0.040925 | 3.3832 | 69.6876 | 235.7695 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 74.8954 | 3.4519 | 0.90301 | 110 | 117.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2427 | 90.1326
CID=853476652 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137528729 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=370937382 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471693931 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493330844 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215349535 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291817746 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392574295 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880756088 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294469171 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470823346 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1370066797 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=370938407 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471694956 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493331869 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215348510 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291818771 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392575320 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880755063 | 24 | 37.5 | 13.2257 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18331.0051 | 0.98367 | 0.0097311 | 11.9783 | 13.2257 | 158.4213 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 44.5825 | 1.4799 | 0.72747 | 89.3426 | 27.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=-294468146 | 24 | 40 | 19.8786 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 19785.9037 | 1.2411 | 0.012199 | 9.835 | 19.8786 | 195.5063 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 48.0659 | 1.5849 | 0.77537 | 110 | 38.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.888 | 28.8692
CID=-1470822321 | 24 | 42.5 | 23.9643 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 20897.0398 | 1.3547 | 0.013932 | 8.7036 | 23.9643 | 208.5751 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 50.6241 | 1.6955 | 0.79867 | 110 | 45.588 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5977 | 35.3309
CID=-1370065772 | 24 | 45 | 28.5197 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 21948.9308 | 1.478 | 0.015936 | 7.7934 | 28.5197 | 222.2659 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 53.1345 | 1.8118 | 0.82026 | 110 | 52.8263 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8492 | 42.1901
CID=370935336 | 24 | 47.5 | 33.4913 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 22975.8046 | 1.6035 | 0.018208 | 7.0273 | 33.4913 | 235.3535 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 55.6424 | 1.9339 | 0.83945 | 110 | 60.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2586 | 49.7239
CID=471691885 | 24 | 50 | 38.8569 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 23934.807 | 1.7311 | 0.02076 | 6.377 | 38.8569 | 247.7902 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 58.139 | 2.0621 | 0.85605 | 110 | 68.9643 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8019 | 57.9119
CID=1493328798 | 24 | 52.5 | 43.3118 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 24668.2929 | 1.8178 | 0.023089 | 5.8538 | 43.3118 | 253.5387 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 60.4935 | 2.1966 | 0.8672 | 110 | 75.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5727 | 64.0509
CID=-1215351581 | 24 | 55 | 49.6713 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 25556.133 | 1.952 | 0.026338 | 5.3357 | 49.6713 | 265.0288 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 63.0804 | 2.3376 | 0.87983 | 110 | 85.7752 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0461 | 73.2965
CID=1291815700 | 24 | 57.5 | 56.2779 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 26423.6135 | 2.078 | 0.029885 | 4.8756 | 56.2779 | 274.386 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 65.696 | 2.4852 | 0.88977 | 110 | 96.0988 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.3599 | 83.1958
CID=1392572249 | 24 | 60 | 61.528 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 27076.2062 | 2.1643 | 0.033056 | 4.5124 | 61.528 | 277.636 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 68.0948 | 2.6398 | 0.89588 | 110 | 104.3473 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.9235 | 90.1325
CID=-1880758134 | 24 | 62.5 | 63.3637 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 27413.1765 | 2.1603 | 0.034893 | 4.2438 | 63.3637 | 268.9021 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 70.1665 | 2.8015 | 0.89771 | 110 | 107.2413 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5949 | 90.1326
CID=-294471217 | 24 | 65 | 65.4457 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 27724.3768 | 2.1549 | 0.036971 | 3.9721 | 65.4457 | 259.9591 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 72.3854 | 2.9705 | 0.89962 | 110 | 110.53 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7589 | 90.1326
CID=-1470825392 | 24 | 67.5 | 67.8323 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 28063.9317 | 2.1511 | 0.039347 | 3.7026 | 67.8323 | 251.1538 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 74.737 | 3.147 | 0.9016 | 110 | 114.308 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.532 | 90.1326
CID=-1370068843 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=370936361 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471692910 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493329823 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215350556 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291816725 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392573274 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880757109 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294470192 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470824367 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1370067818 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=370941482 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471698031 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493334944 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215345435 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291821846 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392578395 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880751988 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294465071 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470819246 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1370062697 | 27 | 42.5 | 20.702 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 19492.235 | 1.3347 | 0.012613 | 10.0518 | 20.702 | 208.0917 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 50.5315 | 1.5489 | 0.7804 | 110 | 40.3041 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.0582 | 29.3459
CID=370942507 | 27 | 45 | 24.1129 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 20418.4761 | 1.422 | 0.014136 | 8.9831 | 24.1129 | 216.609 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 52.8948 | 1.6551 | 0.79945 | 110 | 45.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2922 | 35.9335
CID=471699056 | 27 | 47.5 | 28.9433 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 21506.9401 | 1.5562 | 0.016273 | 7.9962 | 28.9433 | 231.4355 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 55.4598 | 1.7667 | 0.82206 | 110 | 53.4936 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8597 | 43.0269
CID=1493335969 | 27 | 50 | 34.1315 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 22530.9263 | 1.6932 | 0.018667 | 7.1969 | 34.1315 | 245.6399 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 57.9677 | 1.8839 | 0.84164 | 110 | 61.6147 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4382 | 50.8249
CID=-1215344410 | 27 | 52.5 | 39.6042 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 23483.1935 | 1.8277 | 0.021308 | 6.5259 | 39.6042 | 258.455 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 60.4493 | 2.0067 | 0.85807 | 110 | 70.1251 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9821 | 59.2263
CID=1291822871 | 27 | 55 | 44.0988 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 24203.5194 | 1.9194 | 0.023704 | 5.9941 | 44.0988 | 264.3314 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 62.774 | 2.1355 | 0.86896 | 110 | 77.1054 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.6823 | 65.5153
CID=1392579420 | 27 | 57.5 | 50.4994 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 25086.3436 | 2.0558 | 0.027036 | 5.4544 | 50.4994 | 275.4448 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 65.3635 | 2.2704 | 0.88124 | 110 | 87.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0535 | 74.9452
CID=-1880750963 | 27 | 60 | 57.6784 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 25956.977 | 2.2061 | 0.030906 | 4.9805 | 57.6784 | 287.2664 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 67.969 | 2.4116 | 0.89153 | 110 | 98.2951 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1043 | 85.2525
CID=-294464046 | 27 | 62.5 | 61.8425 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 26504.8326 | 2.2631 | 0.033683 | 4.6262 | 61.8425 | 286.0962 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 70.2704 | 2.5593 | 0.8962 | 110 | 104.8427 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.5524 | 90.1325
CID=-1470818221 | 27 | 65 | 64.144 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 26872.0192 | 2.2649 | 0.035791 | 4.3281 | 64.144 | 277.6244 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 72.4584 | 2.7136 | 0.89844 | 110 | 108.4731 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.1555 | 90.1326
CID=-1370061672 | 27 | 67.5 | 66.0368 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 27202.2738 | 2.253 | 0.037855 | 4.0497 | 66.0368 | 267.4267 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 74.6829 | 2.875 | 0.90013 | 110 | 111.4649 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9411 | 90.1326
CID=370939436 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471695985 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493332898 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215347481 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291819800 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392576349 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880754034 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294467117 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470821292 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1370064743 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=370940461 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471697010 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493333923 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215346456 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291820825 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392577374 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880753009 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294466092 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470820267 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1370063718 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=370929182 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471685731 | 30 | 45 | 21.1094 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 19104.7813 | 1.4178 | 0.012893 | 10.3591 | 21.1094 | 218.6745 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 52.8871 | 1.515 | 0.78283 | 110 | 40.97 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2153 | 30.0035
CID=1493322644 | 30 | 47.5 | 24.5579 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 20018.6071 | 1.5069 | 0.014457 | 9.2428 | 24.5579 | 226.985 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 55.2397 | 1.6171 | 0.80173 | 110 | 46.5392 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.6305 | 36.4854
CID=-1215357735 | 30 | 50 | 29.5619 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 21108.6292 | 1.6507 | 0.016696 | 8.2082 | 29.5619 | 242.6498 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 57.8017 | 1.7244 | 0.82463 | 110 | 54.4666 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2979 | 43.826
CID=1291809546 | 30 | 52.5 | 34.9922 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 22125.7595 | 1.7987 | 0.019229 | 7.3674 | 34.9922 | 257.802 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 60.3236 | 1.8368 | 0.84449 | 110 | 62.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.16 | 51.8244
CID=1392566095 | 30 | 55 | 40.6575 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 23077.6501 | 1.9411 | 0.022001 | 6.6663 | 40.6575 | 271.0346 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 62.8167 | 1.9547 | 0.86081 | 110 | 71.7607 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8596 | 60.4554
CID=-1880764288 | 30 | 57.5 | 46.1073 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 23899.2805 | 2.0646 | 0.024846 | 6.0852 | 46.1073 | 280.5716 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 65.2435 | 2.0782 | 0.87318 | 110 | 80.2273 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.677 | 68.5376
CID=-294477371 | 30 | 60 | 51.7728 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 24664.2071 | 2.1816 | 0.027954 | 5.5679 | 51.7728 | 288.2683 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 67.7045 | 2.2074 | 0.8833 | 110 | 89.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.9058 | 76.6398
CID=-1470831546 | 30 | 62.5 | 58.9921 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 25501.9869 | 2.3354 | 0.031934 | 5.0805 | 58.9921 | 299.7087 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 70.2987 | 2.3426 | 0.8931 | 110 | 100.3579 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.8512 | 87.1331
CID=-1370074997 | 30 | 65 | 62.301 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 25962.2706 | 2.3634 | 0.034409 | 4.7226 | 62.301 | 294.2254 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 72.5737 | 2.4839 | 0.89666 | 110 | 105.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4695 | 90.1325
CID=370930207 | 30 | 67.5 | 64.3219 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 26304.9618 | 2.3589 | 0.036456 | 4.4232 | 64.3219 | 284.5119 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 74.7392 | 2.6315 | 0.89861 | 110 | 108.754 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.5113 | 90.1325
CID=471686756 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493323669 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215356710 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291810571 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392567120 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880763263 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294476346 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470830521 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1370073972 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968454081 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022551300 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639469749 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664492166 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405632851 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101670936 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281410615 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585372530 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126693353 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1430655268 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968455106 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022550275 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639468724 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664493191 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405631826 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101669911 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281411640 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585373555 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126694378 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1430656293 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968452035 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022553346 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639471795 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664490120 | -15 | -5 | 4.2026 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18380.5718 | 0.24776 | 0.0067309 | 11.2107 | 4.2026 | 47.1137 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 4.169 | 1.4946 | 0.63621 | 82.7673 | 10.0362 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=-1405634897 | -15 | -2.5 | 7.4734 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 21182.3966 | 0.37686 | 0.0068999 | 9.4915 | 7.4734 | 70.9335 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 9.8717 | 1.6437 | 0.67344 | 110 | 16.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3.8092 | 8.6947
CID=-101672982 | -15 | 0 | 9.3823 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 22728.4211 | 0.4276 | 0.0074514 | 8.4309 | 9.3823 | 79.1021 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 12.948 | 1.804 | 0.69287 | 110 | 20.5737 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.4307 | 11.0329
CID=281408569 | -15 | 2.5 | 11.6004 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 24194.7355 | 0.48257 | 0.0081693 | 7.5606 | 11.6004 | 87.7061 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 15.9174 | 1.9762 | 0.71354 | 110 | 24.7009 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.2867 | 13.7049
CID=1585370484 | -15 | 5 | 13.6923 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 25387.9267 | 0.52536 | 0.0089157 | 6.8484 | 13.6923 | 93.7709 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 18.6883 | 2.1607 | 0.7313 | 110 | 28.4471 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1823 | 16.1956
CID=126691307 | -15 | 7.5 | 16.339 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 26652.2803 | 0.57751 | 0.0098781 | 6.193 | 16.339 | 101.187 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 21.6622 | 2.3583 | 0.7516 | 110 | 33.0291 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2299 | 19.3754
CID=1430653222 | -15 | 10 | 19.4583 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 27896.987 | 0.63367 | 0.011044 | 5.5988 | 19.4582 | 108.942 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 24.7917 | 2.5693 | 0.77273 | 110 | 38.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5747 | 23.0861
CID=1968453060 | -15 | 12.5 | 22.8281 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 29084.5765 | 0.6851 | 0.012352 | 5.0603 | 22.8281 | 115.5177 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 28.0696 | 2.7945 | 0.7926 | 110 | 43.7594 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0921 | 27.0734
CID=-1022552321 | -15 | 15 | 25.4653 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 29895.3962 | 0.72071 | 0.013478 | 4.678 | 25.4653 | 119.1255 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 30.705 | 3.0345 | 0.80626 | 110 | 47.9878 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.5676 | 30.0979
CID=-639470770 | -15 | 17.5 | 29.0469 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 30827.9814 | 0.76997 | 0.014979 | 4.2928 | 29.0469 | 124.6932 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 33.7217 | 3.2899 | 0.82249 | 110 | 53.6566 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.3575 | 34.2767
CID=664491145 | -15 | 20 | 32.5164 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 31736.6625 | 0.81395 | 0.01651 | 3.9697 | 32.5164 | 129.0806 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 36.5549 | 3.5612 | 0.83601 | 110 | 59.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3391 | 38.2422
CID=-1405633872 | -15 | 22.5 | 34.3572 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 32261.5741 | 0.83472 | 0.01753 | 3.7708 | 34.3572 | 129.5536 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 38.3968 | 3.8493 | 0.8424 | 110 | 61.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6718 | 39.9189
CID=-101671957 | -15 | 25 | 35.0842 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 32522.9587 | 0.83503 | 0.018189 | 3.6131 | 35.0842 | 126.7645 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 39.8976 | 4.1546 | 0.84479 | 110 | 63.0987 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9411 | 40.1319
CID=281409594 | -15 | 27.5 | 35.7924 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 32787.5397 | 0.83075 | 0.018874 | 3.4441 | 35.7924 | 123.2732 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 41.6157 | 4.4779 | 0.84704 | 110 | 64.2009 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9327 | 40.079
CID=1585371509 | -15 | 30 | 36.7072 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 33123.159 | 0.82389 | 0.019673 | 3.2534 | 36.7072 | 119.4217 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 43.7164 | 4.8198 | 0.84986 | 110 | 65.6238 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.5427 | 40.0954
CID=126692332 | -15 | 32.5 | 37.8542 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 33479.986 | 0.82295 | 0.020607 | 3.0759 | 37.8542 | 116.4366 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 45.8199 | 5.1811 | 0.85323 | 110 | 67.4067 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1228 | 40.4314
CID=1430654247 | -15 | 35 | 38.8614 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33589.2282 | 0.60011 | 0.020316 | 2.3103 | 35.8474 | 82.8181 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 58.2873 | 5.5624 | 0.84722 | 95.8907 | 64.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.7098 | 39.9119
CID=1968458181 | -15 | 37.5 | 38.9981 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022547200 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639465649 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664496266 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405628751 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101666836 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281414715 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585376630 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126697453 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1430659368 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968459206 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022546175 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639464624 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664497291 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405627726 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101665811 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281415740 | -12 | 0 | 7.701 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 20715.4366 | 0.40832 | 0.0069873 | 9.92 | 7.701 | 76.3935 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 11.9386 | 1.5931 | 0.67585 | 110 | 17.3123 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.1993 | 8.8682
CID=1585377655 | -12 | 2.5 | 9.7111 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 22244.7644 | 0.4619 | 0.0075799 | 8.7444 | 9.7111 | 84.9186 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 15.0352 | 1.7452 | 0.69606 | 110 | 21.1972 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.6238 | 11.4069
CID=126698478 | -12 | 5 | 12.0267 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 23708.5713 | 0.52142 | 0.00834 | 7.8294 | 12.0267 | 94.1621 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 17.9309 | 1.9081 | 0.71729 | 110 | 25.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4802 | 14.2089
CID=1430660393 | -12 | 7.5 | 14.6269 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 25068.8053 | 0.57932 | 0.0092499 | 7.0228 | 14.6269 | 102.7209 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 20.8954 | 2.0826 | 0.73873 | 110 | 30.083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.3445 | 17.3877
CID=1968456135 | -12 | 10 | 16.9981 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 26151.718 | 0.62485 | 0.010148 | 6.397 | 16.9981 | 108.7363 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 23.5544 | 2.269 | 0.7563 | 110 | 34.1477 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5663 | 20.1421
CID=-1022549246 | -12 | 12.5 | 20.2748 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 27400.0527 | 0.6866 | 0.011382 | 5.7812 | 20.2748 | 117.2123 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 26.5958 | 2.4678 | 0.77781 | 110 | 39.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9351 | 24.0547
CID=-639467695 | -12 | 15 | 23.764 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 28550.4046 | 0.74381 | 0.012749 | 5.2393 | 23.764 | 124.506 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 29.6889 | 2.6798 | 0.79762 | 110 | 45.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.4239 | 28.2107
CID=664494220 | -12 | 17.5 | 27.1723 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 29547.2404 | 0.7936 | 0.014154 | 4.7911 | 27.1723 | 130.1863 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 32.622 | 2.9053 | 0.81431 | 110 | 50.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.959 | 32.2434
CID=-1405630797 | -12 | 20 | 30.4595 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 30386.8294 | 0.83617 | 0.015584 | 4.4111 | 30.4595 | 134.3612 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 35.433 | 3.1449 | 0.82824 | 110 | 55.8757 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.8048 | 36.0111
CID=-101668882 | -12 | 22.5 | 34.3307 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 31227.5627 | 0.88869 | 0.017286 | 4.0721 | 34.3307 | 139.7969 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 38.264 | 3.3993 | 0.84231 | 110 | 61.925 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8745 | 40.4827
CID=281412669 | -12 | 25 | 38.1806 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 32148.4469 | 0.9374 | 0.019062 | 3.7787 | 38.1806 | 144.273 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 40.9855 | 3.6689 | 0.85416 | 110 | 67.9138 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0705 | 44.884
CID=1585374584 | -12 | 27.5 | 39.0561 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 32417.5233 | 0.94127 | 0.01982 | 3.6268 | 39.0561 | 141.6499 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 42.4261 | 3.9544 | 0.8566 | 110 | 69.2738 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8318 | 45.1309
CID=126695407 | -12 | 30 | 39.5623 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 32628.0675 | 0.93577 | 0.020475 | 3.4782 | 39.5623 | 137.6038 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 43.9061 | 4.2564 | 0.85796 | 110 | 70.0599 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.4146 | 44.9448
CID=1430657322 | -12 | 32.5 | 40.4644 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 32908.3939 | 0.93099 | 0.02132 | 3.3036 | 40.4644 | 133.6787 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 45.7781 | 4.5754 | 0.86032 | 110 | 71.4609 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.064 | 44.9312
CID=1968457160 | -12 | 35 | 41.5738 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 33254.4539 | 0.92498 | 0.022292 | 3.1172 | 41.5738 | 129.5939 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 47.9337 | 4.9121 | 0.8631 | 110 | 73.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.8778 | 45.1391
CID=-1022548221 | -12 | 37.5 | 42.8527 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 33599.9651 | 0.92443 | 0.023387 | 2.9467 | 42.8527 | 126.2741 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 50.0501 | 5.2671 | 0.86615 | 110 | 75.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0704 | 45.4468
CID=-639466670 | -12 | 40 | 44.2699 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 33790.8619 | 0.67548 | 0.023397 | 2.1712 | 41.3982 | 89.8843 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 63.413 | 5.6411 | 0.86267 | 95.3718 | 72.911 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.392 | 45.2292
CID=664495245 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405629772 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101667857 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281413694 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585375609 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126696432 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1430658347 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968445881 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022559500 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639477949 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664483966 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405641051 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101679136 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281402415 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585364330 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126685153 | -9 | 2.5 | 7.8231 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 20177.6892 | 0.4376 | 0.0070559 | 10.4009 | 7.8231 | 81.3679 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 13.9492 | 1.5462 | 0.67712 | 110 | 17.5537 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.3612 | 8.9771
CID=1430647068 | -9 | 5 | 9.958 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 21747.4205 | 0.4965 | 0.0076913 | 9.1085 | 9.958 | 90.7022 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 17.0505 | 1.6906 | 0.69843 | 110 | 21.6624 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5803 | 11.7505
CID=1968446906 | -9 | 7.5 | 12.4228 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 23219.8298 | 0.56099 | 0.0085066 | 8.1017 | 12.4228 | 100.646 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 19.9847 | 1.8452 | 0.72071 | 110 | 26.1888 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6398 | 14.6838
CID=-1022558475 | -9 | 10 | 15.1867 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 24587.9447 | 0.62622 | 0.0094801 | 7.2621 | 15.1867 | 110.2874 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 22.8747 | 2.0103 | 0.74304 | 110 | 31.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.707 | 18.0132
CID=-639476924 | -9 | 12.5 | 17.5982 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 25644.1333 | 0.6734 | 0.010406 | 6.6126 | 17.5982 | 116.3693 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 25.4593 | 2.1865 | 0.76047 | 110 | 35.1593 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7039 | 20.8962
CID=664484991 | -9 | 15 | 21.0119 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 26895.5717 | 0.73979 | 0.011702 | 5.9672 | 21.0119 | 125.3818 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 28.4459 | 2.3743 | 0.78225 | 110 | 40.8107 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2107 | 24.9456
CID=-1405640026 | -9 | 17.5 | 24.7375 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 28049.8218 | 0.80557 | 0.013167 | 5.4104 | 24.7375 | 133.8386 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 31.4389 | 2.5741 | 0.80264 | 110 | 46.8263 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7125 | 29.4124
CID=-101678111 | -9 | 20 | 28.8055 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 29174.1063 | 0.86709 | 0.01482 | 4.8999 | 28.8055 | 141.1445 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 34.6031 | 2.7864 | 0.82148 | 110 | 53.2766 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5811 | 34.2136
CID=281403440 | -9 | 22.5 | 31.8904 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 29926.8379 | 0.90834 | 0.016208 | 4.5402 | 31.8904 | 144.7898 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 37.1335 | 3.0118 | 0.83371 | 110 | 58.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.2865 | 37.7584
CID=1585365355 | -9 | 25 | 36.1313 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 30810.717 | 0.96608 | 0.018074 | 4.1712 | 36.1313 | 150.7108 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 40.0596 | 3.2507 | 0.8481 | 110 | 64.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.365 | 42.7201
CID=126686178 | -9 | 27.5 | 40.2923 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 31644.3662 | 1.0196 | 0.02 | 3.8612 | 40.2923 | 155.5752 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 42.8117 | 3.5036 | 0.85988 | 110 | 71.1937 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.8057 | 47.4545
CID=1430648093 | -9 | 30 | 43.3519 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 32312.5712 | 1.0571 | 0.021607 | 3.6366 | 43.3519 | 157.6551 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 44.9783 | 3.7712 | 0.86729 | 110 | 75.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4049 | 50.6676
CID=-355853092 | -9 | 32.5 | 44.4202 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 32595.7056 | 1.0608 | 0.02253 | 3.4791 | 44.4202 | 154.541 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 46.5612 | 4.0538 | 0.86966 | 110 | 77.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.4891 | 51.064
CID=-255096543 | -9 | 35 | 44.9157 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 32790.2012 | 1.0517 | 0.023277 | 3.3297 | 44.9157 | 149.5558 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 48.1355 | 4.3522 | 0.87072 | 110 | 78.3749 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.363 | 50.7666
CID=1331190374 | -9 | 37.5 | 45.5448 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 33014.5745 | 1.039 | 0.024119 | 3.1638 | 45.5448 | 144.0945 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 50.0003 | 4.6667 | 0.87203 | 110 | 79.3528 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5427 | 50.2122
CID=-1377490005 | -9 | 40 | 47.1722 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 33399.1761 | 1.0409 | 0.025423 | 2.9826 | 47.1722 | 140.6959 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 52.206 | 4.9981 | 0.87527 | 110 | 81.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.6622 | 51.0088
CID=565027272 | -9 | 42.5 | 48.3461 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 33710.052 | 1.0346 | 0.026609 | 2.8164 | 48.3461 | 136.1608 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 54.3648 | 5.3467 | 0.87748 | 110 | 83.7108 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6387 | 50.9152
CID=665783821 | -9 | 45 | 49.49 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 34047.1169 | 1.0218 | 0.027853 | 2.6433 | 49.49 | 130.8159 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.785 | 5.7134 | 0.87952 | 109.1639 | 85.4926 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=-2042896558 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-456609641 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2097353476 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2096857271 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-355852067 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-255095518 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1331191399 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1377488980 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=565028297 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=665784846 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2042895533 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-456608616 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2097354501 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2096856246 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-355855138 | -6 | 5 | 6.0522 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18703.4035 | 0.38526 | 0.0067989 | 11.7618 | 6.0522 | 71.1848 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 14.1407 | 1.5026 | 0.65791 | 88.6098 | 13.9767 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=-255098589 | -6 | 7.5 | 10.24 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 21279.2915 | 0.53535 | 0.0078151 | 9.4885 | 10.24 | 97.1629 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 19.1078 | 1.64 | 0.7011 | 110 | 22.191 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.779 | 12.0604
CID=1331188328 | -6 | 10 | 12.7978 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 22729.9546 | 0.60229 | 0.0086713 | 8.3866 | 12.7978 | 107.3297 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 22.0571 | 1.7868 | 0.7239 | 110 | 26.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7257 | 15.1552
CID=-1377492051 | -6 | 12.5 | 15.6879 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 24095.8392 | 0.67392 | 0.0096979 | 7.5132 | 15.6879 | 117.8655 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 24.8703 | 1.9434 | 0.74681 | 110 | 31.9159 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8046 | 18.649
CID=565025226 | -6 | 15 | 18.9479 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 25396.05 | 0.74389 | 0.010905 | 6.7358 | 18.9479 | 127.6291 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 27.8012 | 2.1103 | 0.76947 | 110 | 37.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.1409 | 22.5502
CID=665781775 | -6 | 17.5 | 21.7476 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 26385.9009 | 0.79603 | 0.012028 | 6.1577 | 21.7476 | 133.9143 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 30.3426 | 2.2879 | 0.78654 | 110 | 42.0094 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4617 | 25.8429
CID=-2042898604 | -6 | 20 | 25.7426 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 27568.206 | 0.87049 | 0.013605 | 5.575 | 25.7426 | 143.5161 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 33.2948 | 2.4766 | 0.80761 | 110 | 48.4294 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.2332 | 30.5791
CID=-456611687 | -6 | 22.5 | 29.897 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 28649.5381 | 0.93722 | 0.015313 | 5.0624 | 29.897 | 151.3509 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 36.2894 | 2.6769 | 0.82599 | 110 | 54.9929 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9502 | 35.5459
CID=2097351430 | -6 | 25 | 34.0645 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 29613.6918 | 0.99779 | 0.017107 | 4.6306 | 34.0646 | 157.741 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 39.1825 | 2.8892 | 0.84142 | 110 | 61.5103 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7519 | 40.5021
CID=-2096859317 | -6 | 27.5 | 37.7753 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 30374.0748 | 1.0453 | 0.018822 | 4.2799 | 37.7753 | 161.6734 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 41.8328 | 3.1141 | 0.85301 | 110 | 67.284 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9384 | 44.721
CID=-355854113 | -6 | 30 | 42.4629 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 31190.6291 | 1.1088 | 0.02098 | 3.9488 | 42.4629 | 167.6793 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 44.6419 | 3.3519 | 0.86524 | 110 | 74.5644 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.4722 | 50.1265
CID=-255097564 | -6 | 32.5 | 46.9819 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 32045.6078 | 1.1646 | 0.023181 | 3.6631 | 46.9819 | 172.0972 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 47.3369 | 3.6031 | 0.87491 | 110 | 81.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.148 | 55.2599
CID=1331189353 | -6 | 35 | 48.7475 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 32416.0117 | 1.1817 | 0.024426 | 3.4978 | 48.7475 | 170.5096 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 48.996 | 3.8682 | 0.8782 | 110 | 84.336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0822 | 56.636
CID=-1377491026 | -6 | 37.5 | 49.7248 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 32659.8547 | 1.1826 | 0.025423 | 3.3482 | 49.7248 | 166.4877 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 50.5729 | 4.1478 | 0.87992 | 110 | 85.8587 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0639 | 56.9451
CID=565026251 | -6 | 40 | 50.5173 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 32882.4376 | 1.1758 | 0.0264 | 3.1945 | 50.5173 | 161.3773 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 52.2833 | 4.4423 | 0.88127 | 110 | 87.0941 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.7052 | 56.788
CID=665782800 | -6 | 42.5 | 51.5341 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 33161.5762 | 1.1646 | 0.027528 | 3.0212 | 51.5341 | 155.6962 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 54.3391 | 4.7522 | 0.88292 | 110 | 88.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.4168 | 56.5732
CID=-2042897579 | -6 | 45 | 52.8949 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 33476.9526 | 1.1602 | 0.028872 | 2.8539 | 52.8949 | 150.9565 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 56.4678 | 5.0781 | 0.88503 | 110 | 90.8053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.914 | 56.8886
CID=-456610662 | -6 | 47.5 | 54.6677 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 33839.4673 | 1.161 | 0.03048 | 2.6867 | 54.6677 | 146.8748 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 58.7523 | 5.4204 | 0.8876 | 110 | 93.5773 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8283 | 57.2808
CID=2097352455 | -6 | 50 | 55.7391 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34051.8889 | 0.88287 | 0.030801 | 2.0316 | 53.3935 | 108.4754 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 70.5466 | 5.7798 | 0.88577 | 95.3498 | 91.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=-2096858292 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-355848992 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-255092443 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1331194474 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1377485905 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=565031372 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=665787921 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2042892458 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-456605541 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2097357576 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2096853171 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-355847967 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-255091418 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1331195499 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1377484880 | -3 | 10 | 10.5436 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 20838.3868 | 0.57681 | 0.0079482 | 9.8628 | 10.5436 | 103.9892 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 21.239 | 1.5929 | 0.70394 | 110 | 22.7567 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.3391 | 12.2784
CID=565032397 | -3 | 12.5 | 13.2067 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 22265.1522 | 0.6465 | 0.00885 | 8.6633 | 13.2067 | 114.4142 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 24.2021 | 1.7325 | 0.72732 | 110 | 27.5885 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9798 | 15.6157
CID=665788946 | -3 | 15 | 16.2312 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 23640.3778 | 0.72386 | 0.0099338 | 7.7442 | 16.2313 | 125.6981 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 26.9795 | 1.8813 | 0.75081 | 110 | 32.8455 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.1813 | 19.2479
CID=-2042891433 | -3 | 17.5 | 19.5726 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 24907.9116 | 0.79909 | 0.011185 | 6.9532 | 19.5726 | 136.0924 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 29.7919 | 2.0396 | 0.77346 | 110 | 38.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3228 | 23.3226
CID=-456604516 | -3 | 20 | 22.4706 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 25891.1537 | 0.85474 | 0.012357 | 6.3504 | 22.4706 | 142.6975 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 32.2918 | 2.2079 | 0.79063 | 110 | 43.1817 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6291 | 26.7511
CID=2097358601 | -3 | 22.5 | 26.6362 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 27083.9791 | 0.93412 | 0.014015 | 5.7363 | 26.6362 | 152.7926 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 35.224 | 2.3864 | 0.81184 | 110 | 49.849 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.6237 | 31.6404
CID=-2096852146 | -3 | 25 | 31.0222 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 28156.6956 | 1.0104 | 0.015829 | 5.217 | 31.0222 | 161.8414 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 38.1002 | 2.5757 | 0.83043 | 110 | 56.7576 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2655 | 36.9411
CID=-355851038 | -3 | 27.5 | 35.8632 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 29221.6047 | 1.0832 | 0.017892 | 4.7345 | 35.8632 | 169.7938 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 41.1659 | 2.7762 | 0.84726 | 110 | 64.3111 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.5311 | 42.6405
CID=-255094489 | -3 | 30 | 39.4247 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 29920.5157 | 1.1307 | 0.019589 | 4.397 | 39.4247 | 173.3524 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 43.607 | 2.9882 | 0.85759 | 110 | 69.8463 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4826 | 46.7387
CID=1331192428 | -3 | 32.5 | 44.4246 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 30766.2985 | 1.1981 | 0.021905 | 4.0414 | 44.4246 | 179.538 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 46.4791 | 3.2122 | 0.86967 | 110 | 77.6117 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0462 | 52.5507
CID=-1377487951 | -3 | 35 | 49.3111 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 31521.9852 | 1.262 | 0.024294 | 3.746 | 49.3112 | 184.7177 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 49.1505 | 3.4485 | 0.8792 | 110 | 85.214 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9114 | 58.111
CID=565029326 | -3 | 37.5 | 53.9013 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 32315.7596 | 1.3191 | 0.02669 | 3.4961 | 53.9014 | 188.446 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 51.6389 | 3.6978 | 0.88651 | 110 | 92.3785 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.5999 | 63.3351
CID=665785875 | -3 | 40 | 54.8898 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 32541.0924 | 1.3212 | 0.027764 | 3.3537 | 54.8898 | 184.0819 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 53.1423 | 3.9603 | 0.88791 | 110 | 93.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1961 | 63.4544
CID=-2042894504 | -3 | 42.5 | 55.3851 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 32710.519 | 1.3122 | 0.028695 | 3.2169 | 55.3851 | 178.1672 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 54.6574 | 4.2366 | 0.88858 | 110 | 94.7003 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.3922 | 63.0494
CID=-456607587 | -3 | 45 | 56.4758 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 32955.5804 | 1.3058 | 0.029935 | 3.0565 | 56.4758 | 172.6167 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 56.5366 | 4.5271 | 0.89002 | 110 | 96.409 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.8219 | 63.027
CID=2097355530 | -3 | 47.5 | 58.0581 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 33286.149 | 1.3014 | 0.031465 | 2.8824 | 58.0581 | 167.3444 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 58.713 | 4.8323 | 0.89199 | 110 | 98.891 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.7507 | 63.4939
CID=-2096855217 | -3 | 50 | 59.5065 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 33581.5079 | 1.2974 | 0.03303 | 2.7241 | 59.5065 | 162.0997 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 60.8281 | 5.1527 | 0.89368 | 110 | 101.1664 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.6377 | 63.7961
CID=-355850013 | -3 | 52.5 | 61.0989 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 33903.6877 | 1.2898 | 0.034765 | 2.5601 | 61.0989 | 156.421 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 63.1691 | 5.4887 | 0.89543 | 109.9613 | 103.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3223 | 53.5574 | 63.6127
CID=-255093464 | -3 | 55 | 61.0621 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34145.4634 | 0.99406 | 0.035397 | 1.9438 | 60.1317 | 116.8839 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 74.5757 | 5.841 | 0.89438 | 97.0873 | 102.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=1331193453 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1377486926 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=565030351 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=665786900 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2042893479 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-456606562 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2097356555 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2096854192 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-355861292 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-255104743 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1331182174 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1377498205 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=565019072 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=665775621 | 0 | 12.5 | 11.3081 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 20643.1038 | 0.6365 | 0.0082115 | 10.078 | 11.3081 | 113.9629 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 23.7403 | 1.5491 | 0.71092 | 110 | 24.167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6702 | 13.1874
CID=-2042904758 | 0 | 15 | 13.4943 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 21783.1423 | 0.69095 | 0.0089976 | 8.9976 | 13.4943 | 121.4159 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 26.2613 | 1.6821 | 0.72968 | 110 | 28.0977 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.883 | 16.0314
CID=-456617841 | 0 | 17.5 | 16.6788 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 23153.955 | 0.77372 | 0.010146 | 7.9966 | 16.6788 | 133.3733 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 29.0711 | 1.8236 | 0.75404 | 110 | 33.6069 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2692 | 19.8154
CID=2097345276 | 0 | 20 | 20.2365 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 24441.0191 | 0.85881 | 0.011484 | 7.173 | 20.2365 | 145.1552 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 31.8324 | 1.9741 | 0.77758 | 110 | 39.5408 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.7353 | 24.0702
CID=-2096865471 | 0 | 22.5 | 23.604 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 25511.8818 | 0.9267 | 0.01283 | 6.5031 | 23.604 | 153.4985 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 34.4589 | 2.1337 | 0.79678 | 110 | 45.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1199 | 28.0987
CID=-355860267 | 0 | 25 | 27.4447 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 26568.6025 | 1.0006 | 0.014405 | 5.9149 | 27.4447 | 162.3318 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 37.1326 | 2.303 | 0.81554 | 110 | 51.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7385 | 32.6801
CID=-255103718 | 0 | 27.5 | 32.2352 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 27688.5975 | 1.089 | 0.016387 | 5.3654 | 32.2352 | 172.9556 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 40.0108 | 2.4822 | 0.83498 | 110 | 58.6553 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9765 | 38.3214
CID=1331183199 | 0 | 30 | 37.1146 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 28704.81 | 1.1662 | 0.018498 | 4.8822 | 37.1146 | 181.2016 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 42.9195 | 2.6717 | 0.85108 | 110 | 66.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9309 | 44.1758
CID=-1377497180 | 0 | 32.5 | 42.1719 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 29642.7079 | 1.2396 | 0.020778 | 4.4654 | 42.1719 | 188.3151 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 45.7919 | 2.872 | 0.86455 | 110 | 74.1124 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0018 | 50.2286
CID=565020097 | 0 | 35 | 46.2957 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 30329.0293 | 1.2915 | 0.022819 | 4.141 | 46.2957 | 191.7098 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 48.3154 | 3.0833 | 0.87356 | 110 | 80.5203 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6907 | 54.8307
CID=665776646 | 0 | 37.5 | 51.853 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 31118.3882 | 1.3669 | 0.025517 | 3.8206 | 51.853 | 198.1105 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 51.092 | 3.3062 | 0.88343 | 110 | 89.1781 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6252 | 61.2623
CID=-2042903733 | 0 | 40 | 57.0049 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 31889.185 | 1.4302 | 0.028195 | 3.5476 | 57.0049 | 202.229 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 53.7204 | 3.5409 | 0.8907 | 110 | 97.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4682 | 67.1838
CID=-456616816 | 0 | 42.5 | 60.3229 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 32409.3369 | 1.4697 | 0.030272 | 3.3584 | 60.3229 | 202.5865 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 55.7083 | 3.7879 | 0.89459 | 110 | 102.4503 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9202 | 70.4572
CID=2097346301 | 0 | 45 | 61.7107 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 32669.9893 | 1.4747 | 0.031659 | 3.2085 | 61.7106 | 197.9987 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 57.3781 | 4.0477 | 0.89606 | 110 | 104.635 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7902 | 71.0175
CID=-2096864446 | 0 | 47.5 | 62.2717 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 32840.4216 | 1.4624 | 0.032774 | 3.0683 | 62.2717 | 191.0697 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 59.0221 | 4.3205 | 0.89663 | 110 | 105.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3283 | 70.5862
CID=885433247 | 0 | 50 | 63.3166 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 33058.1879 | 1.4531 | 0.034174 | 2.915 | 63.3166 | 184.5705 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 60.918 | 4.607 | 0.89766 | 110 | 107.167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.4342 | 70.2774
CID=-2105572134 | 0 | 52.5 | 65.1198 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 33387.0153 | 1.4501 | 0.03601 | 2.7467 | 65.1198 | 178.8663 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 63.1304 | 4.9075 | 0.89933 | 110 | 110.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.5636 | 70.9719
CID=2007826709 | 0 | 55 | 66.6548 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 33665.9949 | 1.4457 | 0.037842 | 2.5953 | 66.6549 | 172.9883 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 65.2566 | 5.2224 | 0.90065 | 110 | 112.443 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.837 | 71.2608
CID=-983178672 | 0 | 57.5 | 68.4949 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 33985.0598 | 1.4395 | 0.03995 | 2.4363 | 68.4949 | 166.8726 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 67.6341 | 5.5522 | 0.90212 | 110 | 115.3585 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.8149 | 71.0549
CID=-35447117 | 0 | 60 | 68.182 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34214.8219 | 1.1117 | 0.040731 | 1.8506 | 67.3745 | 124.6825 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 78.7718 | 5.8975 | 0.90124 | 97.0873 | 113.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=1268514798 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1086946345 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1904059036 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1567773321 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263811406 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=885434272 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2105571109 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2007827734 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-983177647 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-35446092 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1268515823 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1086947370 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1904058011 | 3 | 15 | 8.8339 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 19057.796 | 0.57216 | 0.0076159 | 11.5149 | 8.8339 | 101.7214 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 24.0783 | 1.5081 | 0.68745 | 88.8812 | 19.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=-1567772296 | 3 | 17.5 | 13.8351 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 21329.0157 | 0.74068 | 0.0091649 | 9.339 | 13.8351 | 129.2054 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 28.3711 | 1.635 | 0.73245 | 110 | 28.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1159 | 16.4081
CID=-263810381 | 3 | 20 | 17.1492 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 22687.5078 | 0.82688 | 0.01037 | 8.249 | 17.1492 | 141.4639 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 31.2118 | 1.7699 | 0.75736 | 110 | 34.4031 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.4444 | 20.3842
CID=885431201 | 3 | 22.5 | 20.8372 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 23969.6181 | 0.91855 | 0.011769 | 7.3926 | 20.8372 | 154.0419 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 33.9201 | 1.9131 | 0.78121 | 110 | 40.5253 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.8813 | 24.8225
CID=-2105574180 | 3 | 25 | 24.8769 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 25168.7891 | 1.0064 | 0.013361 | 6.6469 | 24.8769 | 165.3542 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 36.6904 | 2.0648 | 0.80334 | 110 | 47.0491 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.3039 | 29.7346
CID=2007824663 | 3 | 27.5 | 28.3522 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 26094.3029 | 1.0719 | 0.014838 | 6.0824 | 28.3522 | 172.449 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 39.1495 | 2.2255 | 0.81954 | 110 | 52.5623 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.151 | 33.7526
CID=-983180718 | 3 | 30 | 33.2529 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 27207.5321 | 1.1639 | 0.01689 | 5.5109 | 33.2529 | 183.2534 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 41.9876 | 2.3954 | 0.83862 | 110 | 60.2445 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.3139 | 39.5659
CID=-35449163 | 3 | 32.5 | 38.3953 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 28218.395 | 1.2522 | 0.01913 | 5.0219 | 38.3953 | 192.8186 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 44.7917 | 2.575 | 0.85477 | 110 | 68.2474 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.265 | 45.7721
CID=1268512752 | 3 | 35 | 44.0814 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 29227.7992 | 1.3374 | 0.021683 | 4.566 | 44.0814 | 201.2774 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 47.7757 | 2.7645 | 0.86892 | 110 | 77.0784 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.9753 | 52.4501
CID=1086944299 | 3 | 37.5 | 48.167 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 29879.5655 | 1.3923 | 0.023755 | 4.2489 | 48.167 | 204.6574 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 50.1501 | 2.9643 | 0.87715 | 110 | 83.4321 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.2782 | 57.13
CID=-1904061082 | 3 | 40 | 53.9611 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 30686.9711 | 1.4693 | 0.026601 | 3.9064 | 53.9611 | 210.7953 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 52.9804 | 3.1747 | 0.8866 | 110 | 92.4719 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.2945 | 63.85
CID=-1567775367 | 3 | 42.5 | 59.6599 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 31393.7527 | 1.5447 | 0.02956 | 3.6224 | 59.6599 | 216.1096 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 55.6112 | 3.3962 | 0.89386 | 110 | 101.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2941 | 70.4485
CID=-263813452 | 3 | 45 | 65.4125 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 32192.3415 | 1.6157 | 0.032703 | 3.3672 | 65.4125 | 220.2556 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 58.2176 | 3.6291 | 0.89959 | 110 | 110.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.628 | 77.0074
CID=885432226 | 3 | 47.5 | 67.1342 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 32471.0731 | 1.6289 | 0.03432 | 3.2201 | 67.1342 | 216.1817 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 59.8577 | 3.8738 | 0.90104 | 110 | 113.202 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4646 | 78.0241
CID=-2105573155 | 3 | 50 | 68.3759 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 32695.1299 | 1.63 | 0.035827 | 3.0772 | 68.3759 | 210.4037 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 61.5371 | 4.1306 | 0.90203 | 110 | 115.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3198 | 78.3946
CID=2007825688 | 3 | 52.5 | 69.3359 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 32896.0826 | 1.6212 | 0.037304 | 2.9324 | 69.3359 | 203.3176 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 63.3253 | 4.4 | 0.90276 | 110 | 116.6927 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.5765 | 78.2557
CID=-983179693 | 3 | 55 | 70.1775 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 33096.1432 | 1.6022 | 0.038825 | 2.7788 | 70.1775 | 195.0125 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 65.3191 | 4.6823 | 0.90337 | 110 | 118.029 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3691 | 77.4469
CID=-35448138 | 3 | 57.5 | 72.2799 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 33425.5677 | 1.6024 | 0.041053 | 2.6157 | 72.2799 | 189.0594 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 67.5712 | 4.9781 | 0.90481 | 110 | 121.3718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.8459 | 78.4246
CID=1268513777 | 3 | 60 | 73.8919 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 33693.6014 | 1.5964 | 0.043198 | 2.4677 | 73.8919 | 182.3428 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 69.7504 | 5.2877 | 0.90582 | 110 | 123.9393 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59.7005 | 78.6223
CID=1086945324 | 3 | 62.5 | 75.5033 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 33681.8935 | 1.1962 | 0.042237 | 1.9122 | 69.075 | 132.0841 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 79.5947 | 5.6115 | 0.90256 | 98.2763 | 116.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.5754 | 77.8125
CID=-1904060057 | 3 | 65 | 75.8225 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34259.8998 | 1.2377 | 0.04694 | 1.7561 | 75.117 | 131.9149 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 83.0361 | 5.95 | 0.90655 | 97.0873 | 125.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=-1567774342 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263812427 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=885437347 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2105568034 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2007830809 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-983174572 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-35443017 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1268518898 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1086950445 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1904054936 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1567769221 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263807306 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=885438372 | 6 | 20 | 14.2128 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 20904.8947 | 0.7939 | 0.009348 | 9.6708 | 14.2128 | 137.4499 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 30.5524 | 1.5911 | 0.73547 | 110 | 29.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8403 | 16.6703
CID=-2105567009 | 6 | 22.5 | 17.635 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 22237.1197 | 0.88274 | 0.010605 | 8.4972 | 17.635 | 149.8482 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 33.4047 | 1.7198 | 0.76072 | 110 | 35.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7456 | 20.9315
CID=2007831834 | 6 | 25 | 21.4742 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 23527.5659 | 0.98113 | 0.012074 | 7.6006 | 21.4742 | 163.2155 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 36.086 | 1.8563 | 0.78496 | 110 | 41.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3478 | 25.5163
CID=-983173547 | 6 | 27.5 | 25.6719 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 24710.3417 | 1.0775 | 0.013742 | 6.8387 | 25.6719 | 175.5619 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 38.7774 | 2.0007 | 0.80726 | 110 | 48.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.8391 | 30.6162
CID=-35441992 | 6 | 30 | 29.1972 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 25615.6849 | 1.1452 | 0.015261 | 6.2557 | 29.1972 | 182.6492 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 41.193 | 2.1535 | 0.82312 | 110 | 53.8932 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4236 | 34.7884
CID=1268519923 | 6 | 32.5 | 34.171 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 26701.4317 | 1.2425 | 0.01737 | 5.6735 | 34.171 | 193.8707 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 43.9397 | 2.3149 | 0.84177 | 110 | 61.6762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.4257 | 40.7528
CID=1086951470 | 6 | 35 | 39.8048 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 27757.3308 | 1.3453 | 0.019826 | 5.1558 | 39.8048 | 205.225 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 46.7576 | 2.4852 | 0.8586 | 110 | 70.4365 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.097 | 47.374
CID=-1904053911 | 6 | 37.5 | 45.4939 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 28717.2088 | 1.4347 | 0.022425 | 4.7001 | 45.4939 | 213.8276 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 49.5983 | 2.6649 | 0.87193 | 110 | 79.2736 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.3967 | 54.193
CID=-1567768196 | 6 | 40 | 51.4757 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 29619.7271 | 1.5214 | 0.02527 | 4.3009 | 51.4757 | 221.3907 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 52.4376 | 2.8541 | 0.88283 | 110 | 88.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.7901 | 61.371
CID=-263806281 | 6 | 42.5 | 56.0632 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 30247.2866 | 1.5788 | 0.027713 | 3.9976 | 56.0632 | 224.1193 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 54.8805 | 3.0532 | 0.88948 | 110 | 95.7624 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0078 | 66.415
CID=885435301 | 6 | 45 | 62.3686 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 30990.1996 | 1.6639 | 0.030984 | 3.6917 | 62.3686 | 230.2436 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 57.5996 | 3.2625 | 0.89673 | 110 | 105.6718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0513 | 73.8077
CID=-2105570080 | 6 | 47.5 | 68.3806 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 31693.7585 | 1.7397 | 0.034317 | 3.4287 | 68.3806 | 234.4581 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 60.1946 | 3.4825 | 0.90203 | 110 | 115.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5834 | 80.6463
CID=2007828763 | 6 | 50 | 73.6265 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 32352.5464 | 1.8046 | 0.037513 | 3.2141 | 73.6265 | 236.6424 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 62.5237 | 3.7134 | 0.90566 | 110 | 123.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.1297 | 86.4588
CID=-983176618 | 6 | 52.5 | 74.8084 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 32552.1114 | 1.8058 | 0.039113 | 3.0768 | 74.8084 | 230.1691 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 64.1479 | 3.9556 | 0.90637 | 110 | 125.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.549 | 86.5615
CID=-35445063 | 6 | 55 | 75.2703 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 32688.3766 | 1.7925 | 0.040491 | 2.9474 | 75.2703 | 221.8539 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 65.7597 | 4.2094 | 0.90664 | 110 | 126.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.4253 | 85.8853
CID=1268516852 | 6 | 57.5 | 77.0529 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 32947.7231 | 1.7936 | 0.042583 | 2.7941 | 77.0529 | 215.2912 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 67.7449 | 4.4753 | 0.90763 | 110 | 128.9847 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.4863 | 86.5751
CID=1086948399 | 6 | 60 | 78.1908 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 33172.1815 | 1.7746 | 0.044512 | 2.6389 | 78.1908 | 206.3354 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 69.8635 | 4.7536 | 0.90822 | 110 | 130.8045 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7344 | 86.0097
CID=-1904056982 | 6 | 62.5 | 80.4169 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 33481.6403 | 1.7755 | 0.047127 | 2.4831 | 80.4169 | 199.6865 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 72.1234 | 5.0447 | 0.90929 | 110 | 134.3693 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.5946 | 87.0244
CID=-1567771267 | 6 | 65 | 82.1714 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 33740.3826 | 1.7698 | 0.0497 | 2.3397 | 82.1714 | 192.2554 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 74.3404 | 5.349 | 0.91007 | 110 | 137.1834 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.1624 | 87.1744
CID=-263809352 | 6 | 67.5 | 83.8601 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 33761.0786 | 1.2926 | 0.048822 | 1.7562 | 77.0983 | 135.3988 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 85.2725 | 5.667 | 0.90765 | 95.9768 | 129.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.7476 | 86.2309
CID=885436326 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2105569055 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2007829788 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-983175593 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-35444038 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1268517877 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1086949424 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1904055957 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1567770242 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263808327 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=885425047 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2105580334 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2007818509 | 9 | 22.5 | 15.0388 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 20655.936 | 0.86532 | 0.0096733 | 9.8847 | 15.0388 | 148.6547 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 32.9943 | 1.5501 | 0.74191 | 110 | 30.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3644 | 17.597
CID=-983186872 | 9 | 25 | 17.957 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 21767.5577 | 0.93881 | 0.010793 | 8.8037 | 17.957 | 158.0884 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 35.5107 | 1.6731 | 0.76291 | 110 | 35.7613 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5779 | 21.4167
CID=-35455317 | 9 | 27.5 | 21.9729 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 23047.6549 | 1.0431 | 0.01234 | 7.8314 | 21.9729 | 172.0778 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 38.2279 | 1.8033 | 0.78783 | 110 | 42.3753 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3386 | 26.1844
CID=1268506598 | 9 | 30 | 26.3889 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 24244.5321 | 1.1502 | 0.014106 | 7.0408 | 26.3889 | 185.798 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 40.8765 | 1.941 | 0.81069 | 110 | 49.4566 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.0478 | 31.5026
CID=1086938145 | 9 | 32.5 | 31.252 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 25386.0166 | 1.2535 | 0.01612 | 6.34 | 31.252 | 198.1365 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 43.6197 | 2.0864 | 0.83131 | 110 | 57.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9917 | 37.3388
CID=-1904067236 | 9 | 35 | 35.2477 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 26236.46 | 1.3272 | 0.01792 | 5.8209 | 35.2477 | 205.1724 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 46.014 | 2.24 | 0.84531 | 110 | 63.3533 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.0271 | 41.988
CID=-1567781521 | 9 | 37.5 | 40.9696 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 27281.6098 | 1.4338 | 0.020449 | 5.2874 | 40.9696 | 216.6241 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 48.7828 | 2.4019 | 0.8616 | 110 | 72.2454 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4302 | 48.8161
CID=-263819606 | 9 | 40 | 46.9302 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 28235.826 | 1.535 | 0.023196 | 4.8262 | 46.9302 | 226.4965 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 51.5339 | 2.5724 | 0.87481 | 110 | 81.5072 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.739 | 55.9939
CID=885426072 | 9 | 42.5 | 53.5293 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 29193.1204 | 1.6338 | 0.026334 | 4.395 | 53.5293 | 235.261 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 54.4536 | 2.7519 | 0.88597 | 110 | 91.7968 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9419 | 63.7251
CID=-2105579309 | 9 | 45 | 58.1591 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 29800.7778 | 1.6967 | 0.028854 | 4.0963 | 58.1591 | 238.2374 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 56.7822 | 2.9406 | 0.89211 | 110 | 99.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6277 | 69.0029
CID=2007819534 | 9 | 47.5 | 64.7312 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 30566.7142 | 1.7825 | 0.032309 | 3.7672 | 64.7312 | 243.8563 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 59.5774 | 3.1388 | 0.89898 | 110 | 109.4006 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.871 | 76.6845
CID=-983185847 | 9 | 50 | 71.4407 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 31247.618 | 1.8728 | 0.036018 | 3.491 | 71.4407 | 249.4023 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 62.2081 | 3.3469 | 0.90425 | 110 | 120.0368 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.4252 | 84.4459
CID=-35454292 | 9 | 52.5 | 76.6587 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 31852.9155 | 1.9329 | 0.039299 | 3.2654 | 76.6587 | 250.3189 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 64.5816 | 3.5652 | 0.90741 | 110 | 128.3548 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2376 | 90.1325
CID=1268507623 | 9 | 55 | 77.7102 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 32042.2375 | 1.9345 | 0.040924 | 3.1317 | 77.7102 | 243.3638 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 66.153 | 3.794 | 0.90797 | 110 | 130.0356 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.4435 | 90.1325
CID=1086939170 | 9 | 57.5 | 78.8923 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 32249.431 | 1.9309 | 0.042718 | 2.9878 | 78.8923 | 235.7158 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 67.9103 | 4.0336 | 0.90857 | 110 | 131.9271 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.1717 | 90.1326
CID=-1904066211 | 9 | 60 | 79.9188 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 32452.7516 | 1.9201 | 0.044565 | 2.8425 | 79.9188 | 227.1655 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 69.7738 | 4.2845 | 0.90906 | 110 | 133.5711 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2777 | 90.1326
CID=-1567780496 | 9 | 62.5 | 81.3743 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 32686.9898 | 1.9062 | 0.046758 | 2.6824 | 81.3742 | 218.2779 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 71.912 | 4.5468 | 0.90972 | 110 | 135.9043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.0994 | 90.1325
CID=-263818581 | 9 | 65 | 82.9873 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 32957.4615 | 1.8889 | 0.049198 | 2.519 | 82.9873 | 209.0424 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 74.2197 | 4.8211 | 0.91041 | 110 | 138.4935 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5516 | 90.1325
CID=-1438873926 | 9 | 67.5 | 84.5516 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 33215.2524 | 1.8714 | 0.051809 | 2.3636 | 84.5516 | 199.8443 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 76.5594 | 5.1077 | 0.91104 | 110 | 141.0075 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.8089 | 90.1325
CID=-1338117377 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-316480464 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269806453 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1935213006 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035969555 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1237360828 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=348926089 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=402886802 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503643351 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1438872901 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1338116352 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-316479439 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269807478 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1935214031 | 12 | 25 | 12.8096 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 19237.8902 | 0.82475 | 0.0090709 | 10.9725 | 12.8096 | 140.5528 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 34.0189 | 1.5117 | 0.724 | 110 | 26.8816 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.9035 | 14.4449
CID=2035970580 | 12 | 27.5 | 18.3461 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 21322.2773 | 1.0012 | 0.011009 | 9.1137 | 18.3461 | 167.1999 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 37.6658 | 1.6293 | 0.76552 | 110 | 36.4118 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.806 | 21.8594
CID=-1237359803 | 12 | 30 | 22.5305 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 22595.3707 | 1.1102 | 0.012633 | 8.0593 | 22.5305 | 181.5802 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 40.4205 | 1.7537 | 0.79096 | 110 | 43.2786 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6007 | 26.8405
CID=348927114 | 12 | 32.5 | 27.1233 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 23798.284 | 1.2253 | 0.014486 | 7.2326 | 27.1233 | 196.171 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 43.0488 | 1.8852 | 0.81408 | 110 | 50.6208 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4509 | 32.3474
CID=402887827 | 12 | 35 | 32.095 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 24918.8171 | 1.3353 | 0.016569 | 6.516 | 32.095 | 209.1317 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 45.7229 | 2.0239 | 0.83447 | 110 | 58.4362 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2216 | 38.3861
CID=503644376 | 12 | 37.5 | 36.1628 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 25756.2475 | 1.4125 | 0.018427 | 5.9803 | 36.1628 | 216.2653 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 48.0842 | 2.1702 | 0.8482 | 110 | 64.7771 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1077 | 43.1811
CID=-1438875972 | 12 | 40 | 42.0323 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 26790.2358 | 1.5264 | 0.021051 | 5.4318 | 42.0323 | 228.312 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 50.7985 | 2.3243 | 0.86421 | 110 | 73.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6528 | 50.1588
CID=-1338119423 | 12 | 42.5 | 48.5401 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 27779.6981 | 1.6444 | 0.024056 | 4.9468 | 48.5401 | 240.1172 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 53.5571 | 2.4864 | 0.87783 | 110 | 84.013 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6832 | 57.8258
CID=-316482510 | 12 | 45 | 55.1005 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 28687.357 | 1.747 | 0.02724 | 4.5161 | 55.1005 | 248.8419 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 56.3491 | 2.6569 | 0.88819 | 110 | 94.2547 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3728 | 65.6764
CID=1269804407 | 12 | 47.5 | 61.997 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 29545.4772 | 1.8471 | 0.030733 | 4.1363 | 61.997 | 256.4363 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 59.1477 | 2.836 | 0.89636 | 110 | 105.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.1625 | 73.9419
CID=1935210960 | 12 | 50 | 67.1029 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 30126.1325 | 1.9108 | 0.033678 | 3.8498 | 67.1029 | 258.3322 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 61.5496 | 3.0241 | 0.90102 | 110 | 113.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.7952 | 79.5389
CID=2035967509 | 12 | 52.5 | 74.2259 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 30830.3475 | 2.0066 | 0.037656 | 3.5557 | 74.2259 | 263.9269 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 64.2417 | 3.2213 | 0.90603 | 110 | 124.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.0954 | 87.9361
CID=-1237362874 | 12 | 55 | 76.9306 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 31124.8271 | 2.0309 | 0.039933 | 3.3746 | 76.9306 | 259.6086 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 66.1329 | 3.428 | 0.90756 | 110 | 128.7892 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3247 | 90.1325
CID=348924043 | 12 | 57.5 | 77.8765 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 31294.0342 | 2.0235 | 0.041561 | 3.2246 | 77.8765 | 251.1191 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 67.83 | 3.6445 | 0.90806 | 110 | 130.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.1087 | 90.1325
CID=402884756 | 12 | 60 | 79.0841 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 31506.9413 | 2.0207 | 0.043425 | 3.0747 | 79.0841 | 243.1605 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 69.613 | 3.8712 | 0.90866 | 110 | 132.2342 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.939 | 90.1325
CID=503641305 | 12 | 62.5 | 80.3117 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 31738.7367 | 2.0071 | 0.045433 | 2.9123 | 80.3118 | 233.895 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 71.6154 | 4.1083 | 0.90924 | 110 | 134.2007 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8496 | 90.1325
CID=-1438874947 | 12 | 65 | 81.5178 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 31978.5853 | 1.9826 | 0.047582 | 2.7409 | 81.5178 | 223.4285 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 73.8278 | 4.3561 | 0.90979 | 110 | 136.1346 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.6734 | 90.1325
CID=-1338118398 | 12 | 67.5 | 83.149 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 32257.4611 | 1.9647 | 0.05012 | 2.5711 | 83.149 | 213.7811 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 76.1539 | 4.615 | 0.91048 | 110 | 138.7532 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.1983 | 90.1326
CID=-316481485 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269805432 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1935211985 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035968534 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1237361849 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=348925068 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=402885781 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503642330 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1438869826 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1338113277 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-316476364 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269810553 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1935217106 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035973655 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1237356728 | 15 | 27.5 | 10.0573 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18440.7373 | 0.73518 | 0.0083411 | 12.3545 | 10.0573 | 124.2532 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 34.9722 | 1.4757 | 0.69937 | 84.7006 | 21.8489 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=348930189 | 15 | 30 | 18.7971 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 20910.6206 | 1.0683 | 0.011251 | 9.4101 | 18.7971 | 176.8833 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 39.8919 | 1.5883 | 0.76849 | 110 | 37.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.6958 | 22.1642
CID=402890902 | 15 | 32.5 | 23.089 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 22156.7025 | 1.1799 | 0.012935 | 8.2839 | 23.089 | 191.2662 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 42.6568 | 1.7074 | 0.79402 | 110 | 44.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9438 | 27.4707
CID=503647451 | 15 | 35 | 27.8153 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 23356.2646 | 1.3017 | 0.014862 | 7.4237 | 27.8153 | 206.4912 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 45.2586 | 1.833 | 0.81719 | 110 | 51.715 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8586 | 33.1342
CID=-1438868801 | 15 | 37.5 | 33.0104 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 24473.2543 | 1.4241 | 0.017056 | 6.6921 | 33.0104 | 220.9103 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 47.8709 | 1.9655 | 0.83777 | 110 | 59.8661 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9017 | 39.38
CID=-1338112252 | 15 | 40 | 38.0196 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 25434.9473 | 1.5257 | 0.019294 | 6.083 | 38.0196 | 231.2735 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 50.4146 | 2.1051 | 0.85371 | 110 | 67.6636 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8898 | 45.3962
CID=-316475339 | 15 | 42.5 | 43.2166 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 26322.5417 | 1.6248 | 0.021718 | 5.5655 | 43.2166 | 240.5217 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 52.9119 | 2.2519 | 0.86698 | 110 | 75.735 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2373 | 51.5431
CID=1269811578 | 15 | 45 | 49.8581 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 27308.6057 | 1.7483 | 0.024828 | 5.0653 | 49.8581 | 252.5451 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 55.636 | 2.4063 | 0.88015 | 110 | 86.0664 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.0094 | 59.4744
CID=1935218131 | 15 | 47.5 | 56.7086 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 28211.1434 | 1.8637 | 0.028189 | 4.6287 | 56.7086 | 262.4888 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 58.3559 | 2.5686 | 0.89032 | 110 | 96.774 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.7775 | 67.6857
CID=2035974680 | 15 | 50 | 64.2621 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 29117.6667 | 1.9768 | 0.032023 | 4.2207 | 64.2621 | 271.2298 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 61.2261 | 2.7389 | 0.89855 | 110 | 108.6595 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.453 | 76.5318
CID=-1237355703 | 15 | 52.5 | 69.4469 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 29683.7637 | 2.0482 | 0.03508 | 3.9384 | 69.4469 | 273.5098 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 63.5308 | 2.9175 | 0.90284 | 110 | 116.8689 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.551 | 82.4122
CID=348931214 | 15 | 55 | 76.0922 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 30343.0653 | 2.1329 | 0.038952 | 3.6395 | 76.0922 | 276.934 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 66.1629 | 3.1047 | 0.9071 | 110 | 127.4498 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.9713 | 90.1325
CID=402891927 | 15 | 57.5 | 77.183 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 30503.1538 | 2.1283 | 0.04059 | 3.4775 | 77.183 | 268.4015 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 67.851 | 3.3008 | 0.90769 | 110 | 129.1927 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3346 | 90.1325
CID=503648476 | 15 | 60 | 78.1485 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 30670.0498 | 2.1189 | 0.042282 | 3.3173 | 78.1485 | 259.2429 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 69.6087 | 3.5061 | 0.90819 | 110 | 130.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.1963 | 90.1325
CID=-1438871872 | 15 | 62.5 | 79.273 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 30865.6593 | 2.1069 | 0.04417 | 3.1506 | 79.273 | 249.7604 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 71.5151 | 3.7208 | 0.90875 | 110 | 132.5365 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.6943 | 90.1325
CID=-1338115323 | 15 | 65 | 80.5819 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 31079.8166 | 2.0933 | 0.046289 | 2.9797 | 80.5819 | 240.113 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 73.5628 | 3.9453 | 0.90937 | 110 | 134.6337 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.93 | 90.1325
CID=-316478410 | 15 | 67.5 | 81.7287 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 31298.2083 | 2.0638 | 0.048491 | 2.7985 | 81.7287 | 228.7218 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 75.8258 | 4.1798 | 0.90988 | 110 | 136.473 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5173 | 90.1325
CID=1269808507 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1935215060 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035971609 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1237358774 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=348928143 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=402888856 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503645405 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1438870847 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1338114298 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-316477385 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269809532 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1935216085 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035972634 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1237357749 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=348929168 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=402889881 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503646430 | 18 | 32.5 | 19.6043 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 20604.7709 | 1.1511 | 0.011618 | 9.6356 | 19.6043 | 188.8989 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 42.2783 | 1.5499 | 0.77366 | 110 | 38.4999 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4876 | 22.9766
CID=-1438882126 | 18 | 35 | 23.4391 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 21697.3703 | 1.2495 | 0.013175 | 8.5625 | 23.4391 | 200.6978 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 44.8148 | 1.664 | 0.7959 | 110 | 44.7442 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6985 | 28.0193
CID=-1338125577 | 18 | 37.5 | 28.3845 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 22891.8912 | 1.3788 | 0.015206 | 7.6321 | 28.3845 | 216.634 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 47.4583 | 1.7842 | 0.81968 | 110 | 52.6132 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8592 | 33.8929
CID=-316488664 | 18 | 40 | 33.7735 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 24010.919 | 1.5118 | 0.017503 | 6.8749 | 33.7735 | 232.1897 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 50.0374 | 1.9109 | 0.84043 | 110 | 61.0565 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.906 | 40.396
CID=1269798253 | 18 | 42.5 | 39.6142 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 25072.0035 | 1.6382 | 0.020088 | 6.2044 | 39.6142 | 245.7829 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 52.695 | 2.0442 | 0.8581 | 110 | 70.1405 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0656 | 47.4637
CID=1935204806 | 18 | 45 | 44.3082 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 25856.0552 | 1.7261 | 0.02237 | 5.705 | 44.3083 | 252.7769 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 55.0441 | 2.1844 | 0.86941 | 110 | 77.4309 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.496 | 52.9123
CID=2035961355 | 18 | 47.5 | 51.1321 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 26838.0994 | 1.8573 | 0.025608 | 5.1884 | 51.1322 | 265.2947 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 57.7388 | 2.3317 | 0.88228 | 110 | 88.0531 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.5596 | 60.9897
CID=-1237369028 | 18 | 50 | 58.5028 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 27758.1044 | 1.9905 | 0.029244 | 4.7362 | 58.5028 | 277.0824 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 60.4429 | 2.4862 | 0.89252 | 110 | 99.5894 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7665 | 69.7483
CID=348917889 | 18 | 52.5 | 65.986 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 28615.5303 | 2.1077 | 0.033131 | 4.3292 | 65.986 | 285.6643 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 63.2002 | 2.6484 | 0.90008 | 110 | 111.3845 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8781 | 78.6886
CID=402878602 | 18 | 55 | 73.8519 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 29431.1675 | 2.2222 | 0.037408 | 3.967 | 73.8519 | 292.9686 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 65.9748 | 2.8184 | 0.9058 | 110 | 123.8756 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.0948 | 88.1043
CID=503635151 | 18 | 57.5 | 76.351 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 29706.2252 | 2.2437 | 0.039593 | 3.7646 | 76.351 | 287.4347 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 67.8389 | 2.9964 | 0.90725 | 110 | 127.8632 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0067 | 90.1325
CID=-1438881101 | 18 | 60 | 77.3542 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 29864.1974 | 2.2337 | 0.041245 | 3.5905 | 77.3542 | 277.7431 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 69.5892 | 3.1827 | 0.90778 | 110 | 129.4664 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.0194 | 90.1325
CID=-1338124552 | 18 | 62.5 | 78.419 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 30058.1066 | 2.2166 | 0.043041 | 3.4072 | 78.419 | 267.1877 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 71.5021 | 3.3776 | 0.90833 | 110 | 131.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.2784 | 90.1325
CID=-316487639 | 18 | 65 | 79.6159 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 30260.7785 | 2.2042 | 0.045033 | 3.231 | 79.6159 | 257.2364 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 73.4587 | 3.5814 | 0.90892 | 110 | 133.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0659 | 90.1326
CID=1269799278 | 18 | 67.5 | 80.8541 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 30482.282 | 2.1803 | 0.047198 | 3.0422 | 80.8541 | 245.9764 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 75.6278 | 3.7943 | 0.90949 | 110 | 135.0702 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.0188 | 90.1325
CID=1935205831 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035962380 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1237368003 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=348918914 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=402879627 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503636176 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210266138 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514228053 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332659600 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658345781 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710614226 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593347689 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411779236 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715741151 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631494590 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327532675 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210260889 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514222804 | 21 | 35 | 18.2093 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 19689.1398 | 1.1573 | 0.011262 | 10.3344 | 18.2093 | 188.1832 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 43.9404 | 1.5138 | 0.76461 | 110 | 36.1835 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9152 | 20.974
CID=1332654351 | 21 | 37.5 | 23.8519 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 21255.4748 | 1.3264 | 0.013444 | 8.8469 | 23.8519 | 211.0159 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 47.0096 | 1.6232 | 0.79809 | 110 | 45.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.8342 | 28.5245
CID=-1658351030 | 21 | 40 | 29.0246 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 22450.8809 | 1.4622 | 0.015585 | 7.8369 | 29.0246 | 227.4623 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 49.704 | 1.7385 | 0.8224 | 110 | 53.6215 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2151 | 34.6277
CID=-710619475 | 21 | 42.5 | 34.629 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 23581.1286 | 1.6043 | 0.017998 | 7.042 | 34.629 | 243.8589 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 52.2854 | 1.8598 | 0.8433 | 110 | 62.3898 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.5417 | 41.3248
CID=593342440 | 21 | 45 | 40.6394 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 24626.4339 | 1.741 | 0.020691 | 6.3587 | 40.6394 | 258.4127 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 54.8896 | 1.9873 | 0.86077 | 110 | 71.7326 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.752 | 48.6019
CID=411773987 | 21 | 47.5 | 45.4432 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 25402.1869 | 1.833 | 0.02306 | 5.8415 | 45.4432 | 265.4547 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 57.2296 | 2.1213 | 0.87182 | 110 | 79.1948 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0805 | 54.2307
CID=1715735902 | 21 | 50 | 52.3554 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 26360.046 | 1.9703 | 0.026394 | 5.313 | 52.3553 | 278.1625 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 59.8802 | 2.2619 | 0.88421 | 110 | 89.9625 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9077 | 62.5046
CID=-1631499839 | 21 | 52.5 | 60.0136 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 27293.0898 | 2.113 | 0.030219 | 4.8416 | 60.0136 | 290.5587 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 62.5839 | 2.4094 | 0.89425 | 110 | 101.9636 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.2501 | 71.6014
CID=-327537924 | 21 | 55 | 67.7719 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 28143.6625 | 2.2428 | 0.034306 | 4.4283 | 67.7719 | 300.1151 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 65.285 | 2.564 | 0.90156 | 110 | 114.2123 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.3799 | 80.9026
CID=210259736 | 21 | 57.5 | 75.73 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 28950.0235 | 2.3611 | 0.038723 | 4.0558 | 75.73 | 307.1444 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 68.0296 | 2.726 | 0.9069 | 110 | 126.8714 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.5224 | 90.1325
CID=1514221651 | 21 | 60 | 76.6121 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 29090.5959 | 2.3545 | 0.040269 | 3.8821 | 76.6121 | 297.4169 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 69.6729 | 2.8955 | 0.90739 | 110 | 128.2804 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.0509 | 90.1326
CID=1332653198 | 21 | 62.5 | 77.5507 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 29240.5579 | 2.3424 | 0.041949 | 3.7007 | 77.5507 | 286.9908 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 71.4502 | 3.0728 | 0.90789 | 110 | 129.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.8051 | 90.1326
CID=-1658352183 | 21 | 65 | 78.6958 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 29444.9779 | 2.3227 | 0.043847 | 3.5028 | 78.6958 | 275.6586 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 73.4358 | 3.2582 | 0.90847 | 110 | 131.6125 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3855 | 90.1326
CID=-710620628 | 21 | 67.5 | 79.9101 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 29671.8231 | 2.3009 | 0.045923 | 3.3055 | 79.9101 | 264.1442 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 75.5248 | 3.4519 | 0.90906 | 110 | 133.5571 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2427 | 90.1326
CID=593341287 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411772834 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715734749 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631500992 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327539077 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210262935 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514224850 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332656397 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658348984 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710617429 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593344486 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411776033 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715737948 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631497793 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327535878 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210270238 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514232153 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332663700 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658341681 | 24 | 37.5 | 14.4727 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18606.1379 | 1.0487 | 0.010134 | 11.6698 | 14.4727 | 168.8935 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 44.9605 | 1.4799 | 0.73752 | 88.6538 | 29.8146 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=-710610126 | 24 | 40 | 24.3739 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 20853.6342 | 1.41 | 0.013761 | 9.1123 | 24.3739 | 222.1028 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 49.2796 | 1.5849 | 0.80079 | 110 | 46.2446 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.888 | 28.8692
CID=593351789 | 24 | 42.5 | 29.6476 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 22020.3619 | 1.5481 | 0.015971 | 8.0395 | 29.6476 | 238.351 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 51.9856 | 1.6955 | 0.82498 | 110 | 54.6012 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5977 | 35.3309
CID=411783336 | 24 | 45 | 35.3549 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 23136.83 | 1.6972 | 0.018461 | 7.2192 | 35.3549 | 255.2338 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 54.5374 | 1.8118 | 0.84566 | 110 | 63.52 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8492 | 42.1901
CID=1715745251 | 24 | 47.5 | 41.6076 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 24182.2852 | 1.848 | 0.021292 | 6.5192 | 41.6076 | 271.2472 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 57.1017 | 1.9339 | 0.86318 | 110 | 73.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2586 | 49.7239
CID=-1631490490 | 24 | 50 | 48.3844 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 25182.7485 | 1.9927 | 0.02448 | 5.8952 | 48.3844 | 285.2373 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 59.746 | 2.0621 | 0.87755 | 110 | 83.7705 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8019 | 57.9119
CID=-327528575 | 24 | 52.5 | 53.6814 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 25908.2445 | 2.0908 | 0.02725 | 5.4321 | 53.6814 | 291.6037 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 62.086 | 2.1966 | 0.88619 | 110 | 92.0345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5727 | 64.0509
CID=210264989 | 24 | 55 | 61.4839 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 26836.9044 | 2.2395 | 0.031213 | 4.9456 | 61.4839 | 304.0719 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 64.7723 | 2.3376 | 0.89583 | 110 | 104.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0461 | 73.2965
CID=1514226904 | 24 | 57.5 | 69.7369 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 27691.2064 | 2.389 | 0.035601 | 4.5234 | 69.7369 | 315.4468 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 67.4395 | 2.4852 | 0.90305 | 110 | 117.3293 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.3599 | 83.1958
CID=1332658451 | 24 | 60 | 75.8303 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 28306.3329 | 2.4792 | 0.039312 | 4.194 | 75.8302 | 318.0326 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 69.8434 | 2.6398 | 0.90696 | 110 | 127.0315 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.9235 | 90.1325
CID=-1658346930 | 24 | 62.5 | 76.7481 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 28466.7641 | 2.4654 | 0.040926 | 3.9986 | 76.7481 | 306.8839 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 71.6019 | 2.8015 | 0.90746 | 110 | 128.4976 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5949 | 90.1326
CID=-710615375 | 24 | 65 | 77.7891 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 28648.4739 | 2.4472 | 0.042713 | 3.7951 | 77.7891 | 295.219 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 73.5002 | 2.9705 | 0.90801 | 110 | 130.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7589 | 90.1326
CID=593346540 | 24 | 67.5 | 78.9824 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 28866.2781 | 2.4263 | 0.044707 | 3.5867 | 78.9824 | 283.2859 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 75.5307 | 3.147 | 0.90861 | 110 | 132.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.532 | 90.1326
CID=411778087 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715740002 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631495739 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327533824 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210263836 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514225751 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332657298 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658348083 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710616528 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593345387 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411776934 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715738849 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631496892 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327534977 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210267035 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514228950 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332660497 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658344884 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710613329 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593348586 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411780133 | 27 | 42.5 | 25.024 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 20483.7818 | 1.5021 | 0.014133 | 9.3584 | 25.024 | 234.1831 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 51.6134 | 1.5489 | 0.80408 | 110 | 47.2839 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.0582 | 29.3459
CID=1715742048 | 27 | 45 | 30.0232 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 21570.4802 | 1.634 | 0.01628 | 8.2899 | 30.0232 | 248.8891 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 54.2017 | 1.6551 | 0.8265 | 110 | 55.1911 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2922 | 35.9335
CID=-1631493693 | 27 | 47.5 | 35.9851 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 22684.3125 | 1.7921 | 0.018905 | 7.4063 | 35.9851 | 266.5183 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 56.7971 | 1.7667 | 0.84764 | 110 | 64.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8597 | 43.0269
CID=-327531778 | 27 | 50 | 42.4782 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 23736.1246 | 1.9554 | 0.021876 | 6.6784 | 42.4782 | 283.6849 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 59.3525 | 1.8839 | 0.86527 | 110 | 74.5881 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4382 | 50.8249
CID=210257938 | 27 | 52.5 | 49.4153 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 24726.5395 | 2.1094 | 0.025187 | 6.0365 | 49.4153 | 298.2941 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 61.9684 | 2.0067 | 0.87939 | 110 | 85.3762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9821 | 59.2263
CID=1514219853 | 27 | 55 | 54.807 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 25442.4403 | 2.212 | 0.028056 | 5.558 | 54.807 | 304.6189 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 64.3031 | 2.1355 | 0.88779 | 110 | 93.7953 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.6823 | 65.5153
CID=1332651400 | 27 | 57.5 | 62.7223 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 26350.3945 | 2.3693 | 0.032149 | 5.0612 | 62.7223 | 317.4503 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 66.9495 | 2.2704 | 0.89708 | 110 | 106.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0535 | 74.9452
CID=-1658353981 | 27 | 60 | 71.4654 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 27232.5364 | 2.5331 | 0.036845 | 4.6156 | 71.4654 | 329.8556 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 69.6485 | 2.4116 | 0.90426 | 110 | 120.076 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1043 | 85.2525
CID=-710622426 | 27 | 62.5 | 75.9875 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 27702.5868 | 2.5976 | 0.039961 | 4.3215 | 75.9875 | 328.3789 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 71.8081 | 2.5593 | 0.90704 | 110 | 127.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.5524 | 90.1325
CID=593339489 | 27 | 65 | 77.1383 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 27899.9367 | 2.581 | 0.04174 | 4.1013 | 77.1383 | 316.3706 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 73.688 | 2.7136 | 0.90767 | 110 | 129.1212 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.1555 | 90.1326
CID=411771036 | 27 | 67.5 | 78.0847 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 28081.4439 | 2.5572 | 0.043552 | 3.8871 | 78.0847 | 303.5262 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 75.6312 | 2.875 | 0.90816 | 110 | 130.6346 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9411 | 90.1326
CID=1715732951 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631502790 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327540875 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=210252689 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1514214604 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1332646151 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1658359230 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-710627675 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=593334240 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=411765787 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1715727702 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1631508039 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-327546124 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114041035 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013284486 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991647573 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594639344 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1260045897 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360802446 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912527937 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326241020 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=339165533 | 30 | 45 | 25.5564 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 20095.0896 | 1.594 | 0.014476 | 9.62 | 25.5564 | 245.8542 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 53.9469 | 1.515 | 0.8067 | 110 | 48.133 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2153 | 30.0035
CID=439922082 | 30 | 47.5 | 30.5217 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 21144.7299 | 1.7302 | 0.016647 | 8.5389 | 30.5217 | 260.6207 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 56.4619 | 1.6171 | 0.82848 | 110 | 55.9731 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.6305 | 36.4854
CID=-2114046284 | 30 | 50 | 36.694 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 22250.9332 | 1.8945 | 0.019394 | 7.5894 | 36.694 | 278.484 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 59.0989 | 1.7244 | 0.84982 | 110 | 65.6032 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2979 | 43.826
CID=-2013289735 | 30 | 52.5 | 43.4083 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 23311.8664 | 2.0677 | 0.022506 | 6.8274 | 43.4083 | 296.3656 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 61.6625 | 1.8368 | 0.86742 | 110 | 76.0327 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.16 | 51.8244
CID=-991652822 | 30 | 55 | 50.5564 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 24289.43 | 2.2357 | 0.025966 | 6.1746 | 50.5564 | 312.1647 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 64.2373 | 1.9547 | 0.88133 | 110 | 87.1551 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8596 | 60.4554
CID=594634095 | 30 | 57.5 | 57.3224 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 25129.484 | 2.3751 | 0.029467 | 5.6309 | 57.3224 | 322.7786 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 66.7449 | 2.0782 | 0.89109 | 110 | 97.7366 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.677 | 68.5376
CID=1260040648 | 30 | 60 | 64.2063 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 25900.7554 | 2.509 | 0.033228 | 5.1634 | 64.2063 | 331.5224 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 69.2227 | 2.2074 | 0.8985 | 110 | 108.5714 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.9058 | 76.6398
CID=1360797197 | 30 | 62.5 | 73.0626 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 26779.4355 | 2.678 | 0.038085 | 4.7038 | 73.0626 | 343.6743 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 71.9123 | 2.3426 | 0.90531 | 110 | 122.618 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.8512 | 87.1331
CID=-1912533186 | 30 | 65 | 76.2168 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 27119.5936 | 2.7164 | 0.040681 | 4.4371 | 76.2168 | 338.1786 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 73.9062 | 2.4839 | 0.90717 | 110 | 127.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4695 | 90.1325
CID=-326246269 | 30 | 67.5 | 77.2272 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 27316.1842 | 2.6956 | 0.04246 | 4.21 | 77.2272 | 325.1248 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 75.8057 | 2.6315 | 0.90772 | 110 | 129.2633 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.5113 | 90.1325
CID=339160284 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439916833 | -18 | -5 | 0 | 4 | -11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114047437 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013290888 | -18 | 0 | 0 | 4 | -6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991653975 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594632942 | -18 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1260039495 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360796044 | -18 | 10 | 0 | 4 | 4 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912534339 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326247422 | -18 | 15 | 0 | 4 | 9 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=339159131 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439915680 | -18 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114044238 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013287689 | -18 | 25 | 0 | 4 | 19 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991650776 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594636141 | -18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1260042694 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360799243 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912531140 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326244223 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=339162330 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439918879 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114036935 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013280386 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991643473 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594643444 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1260049997 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360806546 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912523837 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326236920 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=339169633 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439926182 | -18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114042184 | -15 | -5 | 4.3277 | 4 | -10 | 0 | 0.78091 | 139.7222 | 6.5785 | 11.4385 | 209.0164 | 201.5939 | 18389.6498 | 0.25583 | 0.0066832 | 11.2409 | 4.3277 | 48.6475 | -15 | -5 | 4 | -10 | 120.0066 | 179.3581 | 4.3525 | 1.4946 | 0.63773 | 87.9109 | 10.3104 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 3.8194 | 4.3303
CID=-2013285635 | -15 | -2.5 | 8.6703 | 4 | -8.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 13.3704 | 210.798 | 201.5939 | 22080.5296 | 0.41361 | 0.0071558 | 8.9791 | 8.6703 | 77.8513 | -15 | -2.5 | 4 | -8.5 | 120.0066 | 197.2508 | 11.3538 | 1.6437 | 0.68581 | 110 | 19.2081 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 3.8092 | 8.6947
CID=-991648722 | -15 | 0 | 10.9999 | 4 | -6 | 0 | 0.78091 | 139.7222 | 6.5785 | 16.6013 | 212.5504 | 201.5939 | 23712.7729 | 0.47462 | 0.0078656 | 7.982 | 10.9999 | 87.8006 | -15 | 0 | 4 | -6 | 120.0066 | 216.4944 | 14.4943 | 1.804 | 0.70813 | 110 | 23.6009 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.4307 | 11.0329
CID=594638195 | -15 | 2.5 | 13.6629 | 4 | -3.5 | 0 | 0.78091 | 139.7222 | 6.5785 | 19.8464 | 214.2738 | 201.5939 | 25214.0353 | 0.53449 | 0.0087474 | 7.1099 | 13.6629 | 97.1421 | -15 | 2.5 | 4 | -3.5 | 120.0066 | 237.1558 | 17.6998 | 1.9762 | 0.73106 | 110 | 28.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.2867 | 13.7049
CID=1260044748 | -15 | 5 | 16.1456 | 4 | -1 | 0 | 0.78091 | 139.7222 | 6.5785 | 23.1064 | 215.9685 | 201.5939 | 26415.5142 | 0.58213 | 0.0096391 | 6.4354 | 16.1456 | 103.9026 | -15 | 5 | 4 | -1 | 120.0066 | 259.303 | 20.5818 | 2.1607 | 0.75019 | 110 | 32.6993 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1823 | 16.1956
CID=1360801297 | -15 | 7.5 | 19.3146 | 4 | 1.5 | 0.3 | 0.78091 | 139.7222 | 6.5785 | 26.3817 | 217.6348 | 201.5939 | 27724.0951 | 0.63728 | 0.010792 | 5.7811 | 19.3147 | 111.6596 | -15 | 7.5 | 4 | 1.5 | 120.0066 | 283.0058 | 23.8512 | 2.3583 | 0.77182 | 110 | 38.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2299 | 19.3754
CID=-1912529086 | -15 | 10 | 23.0135 | 4 | 4 | 0.8 | 0.78091 | 139.7222 | 6.5785 | 29.6729 | 219.2728 | 201.5939 | 29040.2824 | 0.69367 | 0.012173 | 5.182 | 23.0135 | 119.2571 | -15 | 10 | 4 | 4 | 120.0066 | 308.3347 | 27.3768 | 2.5693 | 0.79361 | 110 | 44.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5747 | 23.0861
CID=-326242169 | -15 | 12.5 | 26.9885 | 4 | 6.5 | 1.3 | 0.78091 | 139.7222 | 6.5785 | 32.9806 | 220.8828 | 201.5939 | 30203.4184 | 0.7489 | 0.013711 | 4.6788 | 26.9885 | 126.2747 | -15 | 12.5 | 4 | 6.5 | 120.0066 | 335.3618 | 30.8542 | 2.7945 | 0.81347 | 110 | 50.4074 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0921 | 27.0734
CID=339164384 | -15 | 15 | 30.0052 | 4 | 9 | 1.8 | 0.78091 | 139.7222 | 6.5785 | 36.3054 | 222.465 | 201.5939 | 30975.5077 | 0.78957 | 0.014997 | 4.3495 | 30.0052 | 130.5064 | -15 | 15 | 4 | 9 | 120.0066 | 364.1604 | 33.4105 | 3.0345 | 0.82643 | 110 | 55.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.5676 | 30.0979
CID=439920933 | -15 | 17.5 | 34.1721 | 4 | 11.5 | 2.3 | 0.78091 | 139.7222 | 6.5785 | 39.6477 | 224.0197 | 201.5939 | 32030.2394 | 0.84271 | 0.016736 | 3.9937 | 34.1721 | 136.4737 | -15 | 17.5 | 4 | 11.5 | 120.0066 | 394.805 | 36.5381 | 3.2899 | 0.84178 | 110 | 61.6779 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.3575 | 34.2767
CID=-2114043337 | -15 | 20 | 38.1277 | 4 | 14 | 2.8 | 0.78091 | 139.7222 | 6.5785 | 43.0083 | 225.547 | 201.5939 | 32970.6187 | 0.89467 | 0.018481 | 3.7212 | 38.1276 | 141.882 | -15 | 20 | 4 | 14 | 120.0066 | 427.3713 | 39.1904 | 3.5612 | 0.85401 | 110 | 67.8315 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3391 | 38.2422
CID=-2013286788 | -15 | 22.5 | 39.8077 | 4 | 16.5 | 3.3 | 0.78091 | 139.7222 | 6.5785 | 46.3877 | 227.0473 | 201.5939 | 33397.7863 | 0.91648 | 0.019487 | 3.5733 | 39.8077 | 142.2431 | -15 | 22.5 | 4 | 16.5 | 120.0066 | 461.9363 | 40.6357 | 3.8493 | 0.85861 | 110 | 70.4411 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6718 | 39.9189
CID=-991649875 | -15 | 25 | 40.031 | 4 | 19 | 3.8 | 0.78091 | 139.7222 | 6.5785 | 49.7865 | 228.5206 | 201.5939 | 33498.7853 | 0.91482 | 0.020006 | 3.4692 | 40.031 | 138.8761 | -15 | 25 | 4 | 19 | 120.0066 | 498.5781 | 41.619 | 4.1546 | 0.8592 | 110 | 70.7878 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8885 | 19.9411 | 40.1319
CID=594637042 | -15 | 27.5 | 39.9932 | 4 | 21.5 | 4.3 | 0.78091 | 139.7222 | 6.5785 | 53.2055 | 229.9673 | 201.5939 | 33554.5109 | 0.90183 | 0.020453 | 3.3461 | 39.9932 | 133.8207 | -15 | 27.5 | 4 | 21.5 | 120.0066 | 537.3762 | 42.8689 | 4.4779 | 0.8591 | 110 | 70.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9327 | 40.079
CID=1260043595 | -15 | 30 | 40.0276 | 4 | 24 | 4.8 | 0.78091 | 139.7222 | 6.5785 | 56.6452 | 231.3875 | 201.5939 | 33675.5963 | 0.88771 | 0.020951 | 3.2146 | 40.0276 | 128.6724 | -15 | 30 | 4 | 24 | 120.0066 | 578.4112 | 44.2911 | 4.8198 | 0.85919 | 110 | 70.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.5427 | 40.0954
CID=1360800144 | -15 | 32.5 | 40.3798 | 4 | 26.5 | 5.3 | 0.78091 | 139.7222 | 6.5785 | 60.1065 | 232.7814 | 201.5939 | 33871.072 | 0.87355 | 0.021603 | 3.0608 | 40.3798 | 123.5963 | -15 | 32.5 | 4 | 26.5 | 120.0066 | 621.7653 | 46.0935 | 5.1811 | 0.8601 | 110 | 71.3295 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1228 | 40.4314
CID=-1912530239 | -15 | 35 | 39.8909 | 4 | 29 | 5.8 | 0.78091 | 139.7222 | 6.5785 | 63.59 | 234.1492 | 201.5939 | 33589.2282 | 0.60011 | 0.020316 | 2.3103 | 35.8474 | 82.8181 | -15 | 35 | 4 | 29 | 120.0066 | 667.522 | 58.2873 | 5.5624 | 0.84722 | 95.8907 | 64.2864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.7098 | 39.9119
CID=-326243322 | -15 | 37.5 | 38.5956 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=339163231 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439919780 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114040138 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013283589 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991646676 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594640241 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1260046794 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1360803343 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1912527040 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-326240123 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=339166430 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=439922979 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2114049235 | -15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2013292686 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-991655773 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=594631144 | -12 | 0 | 8.8449 | 4 | -6 | 0 | 0.78025 | 139.9678 | 7.3973 | 16.6013 | 212.3651 | 203.6939 | 21532.7341 | 0.44448 | 0.0072395 | 9.402 | 8.8449 | 83.1594 | -12 | 0 | 4 | -6 | 135.8928 | 216.4944 | 13.2656 | 1.5931 | 0.68756 | 110 | 19.545 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.1993 | 8.8682
CID=1260037697 | -12 | 2.5 | 11.373 | 4 | -3.5 | 0 | 0.78025 | 139.9678 | 7.3973 | 19.8464 | 214.0869 | 203.6939 | 23214.3866 | 0.51166 | 0.0080146 | 8.2711 | 11.373 | 94.0672 | -12 | 2.5 | 4 | -3.5 | 135.8928 | 237.1558 | 16.5114 | 1.7452 | 0.71151 | 110 | 24.2858 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.6238 | 11.4069
CID=1360794246 | -12 | 5 | 14.1652 | 4 | -1 | 0 | 0.78025 | 139.9678 | 7.3973 | 23.1064 | 215.7799 | 203.6939 | 24717.385 | 0.57775 | 0.0089483 | 7.3655 | 14.1652 | 104.3344 | -12 | 5 | 4 | -1 | 135.8928 | 259.303 | 19.6103 | 1.9081 | 0.7351 | 110 | 29.2776 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4802 | 14.2089
CID=-1912536137 | -12 | 7.5 | 17.3324 | 4 | 1.5 | 0.3 | 0.78025 | 139.9678 | 7.3973 | 26.3817 | 217.4445 | 203.6939 | 26125.0327 | 0.64248 | 0.010061 | 6.5726 | 17.3324 | 113.9192 | -12 | 7.5 | 4 | 1.5 | 135.8928 | 283.0058 | 22.8117 | 2.0826 | 0.75864 | 110 | 34.7121 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.3445 | 17.3877
CID=-326249220 | -12 | 10 | 20.0792 | 4 | 4 | 0.8 | 0.78025 | 139.9678 | 7.3973 | 29.6729 | 219.0809 | 203.6939 | 27207.7646 | 0.69073 | 0.011105 | 5.9864 | 20.0792 | 120.202 | -12 | 10 | 4 | 4 | 135.8928 | 308.3347 | 25.5669 | 2.269 | 0.77661 | 110 | 39.2823 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5663 | 20.1421
CID=339157333 | -12 | 12.5 | 23.9791 | 4 | 6.5 | 1.3 | 0.78025 | 139.9678 | 7.3973 | 32.9806 | 220.6893 | 203.6939 | 28509.1075 | 0.75303 | 0.01257 | 5.361 | 23.9791 | 128.5514 | -12 | 12.5 | 4 | 6.5 | 135.8928 | 335.3618 | 29.0009 | 2.4678 | 0.79875 | 110 | 45.6118 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9351 | 24.0547
CID=439913882 | -12 | 15 | 28.1218 | 4 | 9 | 1.8 | 0.78025 | 139.9678 | 7.3973 | 36.3054 | 222.2699 | 203.6939 | 29690.248 | 0.81396 | 0.014185 | 4.8449 | 28.1218 | 136.2483 | -12 | 15 | 4 | 9 | 135.8928 | 364.1604 | 32.3313 | 2.6798 | 0.81854 | 110 | 52.1989 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.4239 | 28.2107
CID=-2114054484 | -12 | 17.5 | 32.142 | 4 | 11.5 | 2.3 | 0.78025 | 139.9678 | 7.3973 | 39.6477 | 223.823 | 203.6939 | 30666.341 | 0.86785 | 0.015834 | 4.4293 | 32.142 | 142.3672 | -12 | 17.5 | 4 | 11.5 | 135.8928 | 394.805 | 35.4157 | 2.9053 | 0.83464 | 110 | 58.5097 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.959 | 32.2434
CID=-2013297935 | -12 | 20 | 35.9 | 4 | 14 | 2.8 | 0.78025 | 139.9678 | 7.3973 | 43.0083 | 225.3488 | 203.6939 | 31478.4394 | 0.91698 | 0.017467 | 4.1043 | 35.9 | 147.346 | -12 | 20 | 4 | 14 | 135.8928 | 427.3713 | 38.1237 | 3.1449 | 0.84738 | 110 | 64.3684 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.8048 | 36.0111
CID=-991661022 | -12 | 22.5 | 40.3597 | 4 | 16.5 | 3.3 | 0.78025 | 139.9678 | 7.3973 | 46.3877 | 226.8474 | 203.6939 | 32506.7136 | 0.9741 | 0.019423 | 3.7967 | 40.3597 | 153.2319 | -12 | 22.5 | 4 | 16.5 | 135.8928 | 461.9363 | 40.9929 | 3.3993 | 0.86005 | 110 | 71.2983 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8745 | 40.4827
CID=594625895 | -12 | 25 | 44.7499 | 4 | 19 | 3.8 | 0.78025 | 139.9678 | 7.3973 | 49.7865 | 228.3192 | 203.6939 | 33385.303 | 1.0305 | 0.021446 | 3.544 | 44.7499 | 158.595 | -12 | 25 | 4 | 19 | 135.8928 | 498.5781 | 43.5845 | 3.6689 | 0.87036 | 110 | 78.1172 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0705 | 44.884
CID=1260032448 | -12 | 27.5 | 45.0094 | 4 | 21.5 | 4.3 | 0.78025 | 139.9678 | 7.3973 | 53.2055 | 229.7643 | 203.6939 | 33499.3791 | 1.0322 | 0.02203 | 3.451 | 45.0094 | 155.3293 | -12 | 27.5 | 4 | 21.5 | 135.8928 | 537.3762 | 44.4609 | 3.9544 | 0.87092 | 110 | 78.5205 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8318 | 45.1309
CID=1360788997 | -12 | 30 | 44.8372 | 4 | 24 | 4.8 | 0.78025 | 139.9678 | 7.3973 | 56.6452 | 231.183 | 203.6939 | 33535.9338 | 1.0165 | 0.022479 | 3.3337 | 44.8372 | 149.4725 | -12 | 30 | 4 | 24 | 135.8928 | 578.4112 | 45.6554 | 4.2564 | 0.87055 | 110 | 78.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.4146 | 44.9448
CID=-1912541386 | -12 | 32.5 | 44.8419 | 4 | 26.5 | 5.3 | 0.78025 | 139.9678 | 7.3973 | 60.1065 | 232.5753 | 203.6939 | 33587.6007 | 1.0147 | 0.023023 | 3.249 | 44.8419 | 145.6919 | -12 | 32.5 | 4 | 26.5 | 135.8928 | 621.7653 | 46.5218 | 4.5754 | 0.87056 | 110 | 78.2601 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8698 | 27.064 | 44.9312
CID=-326254469 | -12 | 35 | 45.0678 | 4 | 29 | 5.8 | 0.78025 | 139.9678 | 7.3973 | 63.59 | 233.9416 | 203.6939 | 33751.0885 | 0.99881 | 0.023686 | 3.105 | 45.0678 | 139.9374 | -12 | 35 | 4 | 29 | 135.8928 | 667.522 | 48.1688 | 4.9121 | 0.87104 | 110 | 78.6113 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8438 | 30.8778 | 45.1391
CID=339152084 | -12 | 37.5 | 45.3949 | 4 | 31.5 | 6.3 | 0.78025 | 139.9678 | 7.3973 | 67.0967 | 235.282 | 203.6939 | 33934.5442 | 0.98289 | 0.024428 | 2.9576 | 45.3949 | 134.2604 | -12 | 37.5 | 4 | 31.5 | 135.8928 | 715.7661 | 49.9638 | 5.2671 | 0.87172 | 110 | 79.1197 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8079 | 35.0704 | 45.4468
CID=439908633 | -12 | 40 | 45.21 | 4 | 34 | 6.8 | 0.78025 | 139.9678 | 7.3973 | 70.6273 | 236.5967 | 203.6939 | 33790.8619 | 0.67548 | 0.023397 | 2.1712 | 41.3982 | 89.8843 | -12 | 40 | 4 | 34 | 135.8928 | 766.5841 | 63.413 | 5.6411 | 0.86267 | 95.3718 | 72.911 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.392 | 45.2292
CID=-516524336 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787437579 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170519130 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820486251 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437404700 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133442785 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249638766 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553600681 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936682232 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054323149 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516529585 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787432330 | -12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170513881 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820491500 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437409949 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133448034 | -9 | 2.5 | 8.9541 | 4 | -3.5 | 0 | 0.77973 | 140.1723 | 8.294 | 19.8464 | 213.9436 | 205.7883 | 20969.6705 | 0.47616 | 0.0073101 | 9.888 | 8.9541 | 88.538 | -9 | 2.5 | 4 | -3.5 | 153.3765 | 237.1558 | 15.1312 | 1.5462 | 0.68865 | 110 | 19.7549 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.3612 | 8.9771
CID=249633517 | -9 | 5 | 11.7147 | 4 | -1 | 0 | 0.77973 | 140.1723 | 8.294 | 23.1064 | 215.6354 | 205.7883 | 22712.52 | 0.54985 | 0.0081587 | 8.5746 | 11.7147 | 100.4485 | -9 | 5 | 4 | -1 | 153.3765 | 259.303 | 18.5433 | 1.6906 | 0.71455 | 110 | 24.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5803 | 11.7505
CID=1553595432 | -9 | 7.5 | 14.6386 | 4 | 1.5 | 0.3 | 0.77973 | 140.1723 | 8.294 | 26.3817 | 217.2988 | 205.7883 | 24215.7811 | 0.62255 | 0.0091454 | 7.6297 | 14.6386 | 111.6889 | -9 | 7.5 | 4 | 1.5 | 153.3765 | 283.0058 | 21.5544 | 1.8452 | 0.73882 | 110 | 30.1035 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6398 | 14.6838
CID=1936676983 | -9 | 10 | 17.9567 | 4 | 4 | 0.8 | 0.77973 | 140.1723 | 8.294 | 29.6729 | 218.9339 | 205.7883 | 25616.7173 | 0.69382 | 0.01032 | 6.8048 | 17.9567 | 122.1923 | -9 | 10 | 4 | 4 | 153.3765 | 308.3347 | 24.6612 | 2.0103 | 0.76291 | 110 | 35.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.707 | 18.0132
CID=-1054328398 | -9 | 12.5 | 20.8303 | 4 | 6.5 | 1.3 | 0.77973 | 140.1723 | 8.294 | 32.9806 | 220.541 | 205.7883 | 26686.773 | 0.74651 | 0.011419 | 6.193 | 20.8303 | 129.0026 | -9 | 12.5 | 4 | 6.5 | 153.3765 | 335.3618 | 27.354 | 2.1865 | 0.78117 | 110 | 40.514 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7039 | 20.8962
CID=-516530738 | -9 | 15 | 24.8669 | 4 | 9 | 1.8 | 0.77973 | 140.1723 | 8.294 | 36.3054 | 222.1204 | 205.7883 | 27968.2147 | 0.8151 | 0.01295 | 5.5554 | 24.8669 | 138.1449 | -9 | 15 | 4 | 9 | 153.3765 | 364.1604 | 30.6247 | 2.3743 | 0.80329 | 110 | 47.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2107 | 24.9456
CID=787431177 | -9 | 17.5 | 29.3189 | 4 | 11.5 | 2.3 | 0.77973 | 140.1723 | 8.294 | 39.6477 | 223.6723 | 205.7883 | 29195.884 | 0.88213 | 0.014691 | 4.9987 | 29.3189 | 146.5575 | -9 | 17.5 | 4 | 11.5 | 153.3765 | 394.805 | 33.9836 | 2.5741 | 0.82363 | 110 | 54.0846 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7125 | 29.4124
CID=1170512728 | -9 | 20 | 34.1055 | 4 | 14 | 2.8 | 0.77973 | 140.1723 | 8.294 | 43.0083 | 225.1969 | 205.7883 | 30297.4151 | 0.94774 | 0.016628 | 4.5234 | 34.1055 | 154.2738 | -9 | 20 | 4 | 14 | 153.3765 | 427.3713 | 37.3341 | 2.7864 | 0.84155 | 110 | 61.5741 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5811 | 34.2136
CID=-1820492653 | -9 | 22.5 | 37.641 | 4 | 16.5 | 3.3 | 0.77973 | 140.1723 | 8.294 | 46.3877 | 226.6943 | 205.7883 | 31015.6124 | 0.995 | 0.018216 | 4.2136 | 37.641 | 158.6042 | -9 | 22.5 | 4 | 16.5 | 153.3765 | 461.9363 | 39.792 | 3.0118 | 0.85262 | 110 | 67.0753 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.2865 | 37.7584
CID=-1437411102 | -9 | 25 | 42.5883 | 4 | 19 | 3.8 | 0.77973 | 140.1723 | 8.294 | 49.7865 | 228.1649 | 205.7883 | 31997.579 | 1.0581 | 0.020383 | 3.8758 | 42.5883 | 165.0618 | -9 | 25 | 4 | 19 | 153.3765 | 498.5781 | 42.8026 | 3.2507 | 0.86553 | 110 | 74.7591 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.365 | 42.7201
CID=-133449187 | -9 | 27.5 | 47.3113 | 4 | 21.5 | 4.3 | 0.77973 | 140.1723 | 8.294 | 53.2055 | 229.6088 | 205.7883 | 32905.594 | 1.1197 | 0.022571 | 3.611 | 47.3113 | 170.8431 | -9 | 27.5 | 4 | 21.5 | 153.3765 | 537.3762 | 45.4172 | 3.5036 | 0.87554 | 110 | 82.1001 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.8057 | 47.4545
CID=249632364 | -9 | 30 | 50.5212 | 4 | 24 | 4.8 | 0.77973 | 140.1723 | 8.294 | 56.6452 | 231.0262 | 205.7883 | 33508.3267 | 1.1595 | 0.024296 | 3.4231 | 50.5212 | 172.9379 | -9 | 30 | 4 | 24 | 153.3765 | 578.4112 | 47.3891 | 3.7712 | 0.88127 | 110 | 87.1002 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4049 | 50.6676
CID=1553594279 | -9 | 32.5 | 50.9311 | 4 | 26.5 | 5.3 | 0.77973 | 140.1723 | 8.294 | 60.1065 | 232.4174 | 205.7883 | 33633.4152 | 1.1587 | 0.025031 | 3.3144 | 50.9311 | 168.8066 | -9 | 32.5 | 4 | 26.5 | 153.3765 | 621.7653 | 48.5115 | 4.0538 | 0.88195 | 110 | 87.7394 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.4891 | 51.064
CID=1936675830 | -9 | 35 | 50.6496 | 4 | 29 | 5.8 | 0.77973 | 140.1723 | 8.294 | 63.59 | 233.7825 | 205.7883 | 33632.5355 | 1.1413 | 0.025533 | 3.2041 | 50.6496 | 162.2859 | -9 | 35 | 4 | 29 | 153.3765 | 667.522 | 49.6977 | 4.3522 | 0.88149 | 110 | 87.3004 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.363 | 50.7666
CID=-1054329551 | -9 | 37.5 | 50.1189 | 4 | 31.5 | 6.3 | 0.77973 | 140.1723 | 8.294 | 67.0967 | 235.1217 | 205.7883 | 33639.2101 | 1.1232 | 0.025965 | 3.1082 | 50.1189 | 155.7801 | -9 | 37.5 | 4 | 31.5 | 153.3765 | 715.7661 | 50.7594 | 4.6667 | 0.8806 | 110 | 86.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5427 | 50.2122
CID=-516527539 | -9 | 40 | 50.9321 | 4 | 34 | 6.8 | 0.77973 | 140.1723 | 8.294 | 70.6273 | 236.4353 | 205.7883 | 33864.9732 | 1.1212 | 0.02698 | 2.9754 | 50.9321 | 151.5451 | -9 | 40 | 4 | 34 | 153.3765 | 766.5841 | 52.3674 | 4.9981 | 0.88195 | 110 | 87.7411 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8382 | 35.6622 | 51.0088
CID=787434376 | -9 | 42.5 | 50.8638 | 4 | 36.5 | 7.3 | 0.77973 | 140.1723 | 8.294 | 74.1828 | 237.7233 | 205.7883 | 34007.7106 | 1.0874 | 0.02768 | 2.8134 | 50.8638 | 143.1014 | -9 | 42.5 | 4 | 36.5 | 153.3765 | 820.0642 | 54.4524 | 5.3467 | 0.88184 | 110 | 87.6345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6387 | 50.9152
CID=1170515927 | -9 | 45 | 50.2517 | 4 | 39 | 7.8 | 0.77973 | 140.1723 | 8.294 | 77.7643 | 238.9859 | 205.7883 | 34116.0687 | 1.0513 | 0.028186 | 2.6782 | 50.2517 | 134.586 | -9 | 45 | 4 | 39 | 153.3765 | 876.2965 | 56.2785 | 5.7134 | 0.88082 | 110 | 86.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1582 | 50.2672
CID=-1820489454 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437407903 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133445988 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249635563 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553597478 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936679029 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054326352 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516520236 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787441679 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170523230 | -9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820482151 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437400600 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133438685 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249642866 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553604781 | -6 | 5 | 6.47 | 4 | -1 | 0 | 0.77937 | 140.3347 | 9.2739 | 23.1064 | 215.5319 | 207.8761 | 18944.9897 | 0.40631 | 0.006853 | 11.6033 | 6.47 | 75.0735 | -6 | 5 | 4 | -1 | 172.5645 | 259.303 | 14.5401 | 1.5026 | 0.66257 | 87.9173 | 14.8364 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.7732 | 6.4786
CID=1936686332 | -6 | 7.5 | 12.024 | 4 | 1.5 | 0.3 | 0.77937 | 140.3347 | 9.2739 | 26.3817 | 217.1944 | 207.8761 | 22210.0437 | 0.5891 | 0.0082976 | 8.892 | 12.024 | 106.9175 | -6 | 7.5 | 4 | 1.5 | 172.5645 | 283.0058 | 20.5949 | 1.64 | 0.71726 | 110 | 25.4698 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.779 | 12.0604
CID=-1054319049 | -6 | 10 | 15.108 | 4 | 4 | 0.8 | 0.77937 | 140.3347 | 9.2739 | 29.6729 | 218.8286 | 207.8761 | 23727.1313 | 0.66885 | 0.0093458 | 7.8893 | 15.108 | 119.1917 | -6 | 10 | 4 | 4 | 172.5645 | 308.3347 | 23.571 | 1.7868 | 0.74244 | 110 | 30.9173 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7257 | 15.1552
CID=-516525485 | -6 | 12.5 | 18.5897 | 4 | 6.5 | 1.3 | 0.77937 | 140.3347 | 9.2739 | 32.9806 | 220.4349 | 207.8761 | 25130.3199 | 0.74707 | 0.010587 | 7.0286 | 18.5897 | 130.659 | -6 | 12.5 | 4 | 6.5 | 172.5645 | 335.3618 | 26.6068 | 1.9434 | 0.76713 | 110 | 36.818 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8046 | 18.649
CID=787436430 | -6 | 15 | 22.4782 | 4 | 9 | 1.8 | 0.77937 | 140.3347 | 9.2739 | 36.3054 | 222.0134 | 207.8761 | 26446.8579 | 0.82379 | 0.012027 | 6.2878 | 22.4782 | 141.3375 | -6 | 15 | 4 | 9 | 172.5645 | 364.1604 | 29.7072 | 2.1103 | 0.79067 | 110 | 43.1939 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.1409 | 22.5502
CID=1170517981 | -6 | 17.5 | 25.761 | 4 | 11.5 | 2.3 | 0.77937 | 140.3347 | 9.2739 | 39.6477 | 223.5644 | 207.8761 | 27452.0577 | 0.87977 | 0.013339 | 5.7452 | 25.761 | 148.0025 | -6 | 17.5 | 4 | 11.5 | 172.5645 | 394.805 | 32.3587 | 2.2879 | 0.80769 | 110 | 48.4586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4617 | 25.8429
CID=-1820487400 | -6 | 20 | 30.4823 | 4 | 14 | 2.8 | 0.77937 | 140.3347 | 9.2739 | 43.0083 | 225.0881 | 207.8761 | 28686.2643 | 0.95346 | 0.015196 | 5.1569 | 30.4823 | 157.1942 | -6 | 20 | 4 | 14 | 172.5645 | 427.3713 | 35.686 | 2.4766 | 0.82833 | 110 | 55.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.2332 | 30.5791
CID=-1437405849 | -6 | 22.5 | 35.4329 | 4 | 16.5 | 3.3 | 0.77937 | 140.3347 | 9.2739 | 46.3877 | 226.5847 | 207.8761 | 29795.3999 | 1.0255 | 0.017219 | 4.6737 | 35.433 | 165.6042 | -6 | 22.5 | 4 | 16.5 | 172.5645 | 461.9363 | 38.8862 | 2.6769 | 0.84591 | 110 | 63.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9502 | 35.5459
CID=-133443934 | -6 | 25 | 40.3733 | 4 | 19 | 3.8 | 0.77937 | 140.3347 | 9.2739 | 49.7865 | 228.0544 | 207.8761 | 30742.9709 | 1.0914 | 0.019332 | 4.2737 | 40.3733 | 172.5442 | -6 | 25 | 4 | 19 | 172.5645 | 498.5781 | 41.9295 | 2.8892 | 0.86009 | 110 | 71.3194 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7519 | 40.5021
CID=249637617 | -6 | 27.5 | 44.5821 | 4 | 21.5 | 4.3 | 0.77937 | 140.3347 | 9.2739 | 53.2055 | 229.4974 | 207.8761 | 31460.2238 | 1.146 | 0.021279 | 3.9759 | 44.5821 | 177.253 | -6 | 27.5 | 4 | 21.5 | 172.5645 | 537.3762 | 44.4658 | 3.1141 | 0.87001 | 110 | 77.8563 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9384 | 44.721
CID=1553599532 | -6 | 30 | 49.9732 | 4 | 24 | 4.8 | 0.77937 | 140.3347 | 9.2739 | 56.6452 | 230.914 | 207.8761 | 32444.7124 | 1.2133 | 0.023758 | 3.6718 | 49.9732 | 183.4936 | -6 | 30 | 4 | 24 | 172.5645 | 578.4112 | 47.3535 | 3.3519 | 0.88035 | 110 | 86.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.4722 | 50.1265
CID=1936681083 | -6 | 32.5 | 55.0943 | 4 | 26.5 | 5.3 | 0.77937 | 140.3347 | 9.2739 | 60.1065 | 232.3043 | 207.8761 | 33275.1984 | 1.2798 | 0.026255 | 3.4326 | 55.0943 | 189.1183 | -6 | 32.5 | 4 | 26.5 | 172.5645 | 621.7653 | 49.8536 | 3.6031 | 0.88819 | 110 | 94.2451 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.148 | 55.2599
CID=-1054324298 | -6 | 35 | 56.4782 | 4 | 29 | 5.8 | 0.77937 | 140.3347 | 9.2739 | 63.59 | 233.6686 | 207.8761 | 33543.0167 | 1.2978 | 0.027427 | 3.3154 | 56.4782 | 187.2495 | -6 | 35 | 4 | 29 | 172.5645 | 667.522 | 51.092 | 3.8682 | 0.89002 | 110 | 96.4128 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0822 | 56.636
CID=-516526638 | -6 | 37.5 | 56.8007 | 4 | 31.5 | 6.3 | 0.77937 | 140.3347 | 9.2739 | 67.0967 | 235.007 | 207.8761 | 33642.3882 | 1.2954 | 0.028238 | 3.2106 | 56.8007 | 182.3664 | -6 | 37.5 | 4 | 31.5 | 172.5645 | 715.7661 | 52.2305 | 4.1478 | 0.89044 | 110 | 96.9184 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8884 | 28.0639 | 56.9451
CID=787435277 | -6 | 40 | 56.6626 | 4 | 34 | 6.8 | 0.77937 | 140.3347 | 9.2739 | 70.6273 | 236.3196 | 207.8761 | 33679.3672 | 1.2769 | 0.028908 | 3.093 | 56.6626 | 175.2555 | -6 | 40 | 4 | 34 | 172.5645 | 766.5841 | 53.5746 | 4.4423 | 0.89026 | 110 | 96.7018 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.7052 | 56.788
CID=1170516828 | -6 | 42.5 | 56.4724 | 4 | 36.5 | 7.3 | 0.77937 | 140.3347 | 9.2739 | 74.1828 | 237.6068 | 207.8761 | 33752.0495 | 1.2569 | 0.029597 | 2.9757 | 56.4724 | 168.0422 | -6 | 42.5 | 4 | 36.5 | 172.5645 | 820.0642 | 54.9811 | 4.7522 | 0.89002 | 110 | 96.4037 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.4168 | 56.5732
CID=-1820488553 | -6 | 45 | 56.8087 | 4 | 39 | 7.8 | 0.77937 | 140.3347 | 9.2739 | 77.7643 | 238.8686 | 207.8761 | 33914.3803 | 1.2368 | 0.030557 | 2.8327 | 56.8087 | 160.9212 | -6 | 45 | 4 | 39 | 172.5645 | 876.2965 | 56.8077 | 5.0781 | 0.89045 | 110 | 96.9309 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.914 | 56.8886
CID=-1437407002 | -6 | 47.5 | 57.2285 | 4 | 41.5 | 8.3 | 0.77937 | 140.3347 | 9.2739 | 81.3729 | 240.1052 | 207.8761 | 34100.3486 | 1.2167 | 0.031615 | 2.6895 | 57.2285 | 153.9137 | -6 | 47.5 | 4 | 41.5 | 172.5645 | 935.3729 | 58.7494 | 5.4204 | 0.89098 | 110 | 97.5893 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8283 | 57.2808
CID=-133445087 | -6 | 50 | 56.5053 | 4 | 44 | 8.8 | 0.77937 | 140.3347 | 9.2739 | 85.0099 | 241.3167 | 207.8761 | 34051.8889 | 0.88287 | 0.030801 | 2.0316 | 53.3935 | 108.4754 | -6 | 50 | 4 | 44 | 172.5645 | 997.3873 | 70.5466 | 5.7798 | 0.88577 | 95.3498 | 91.5844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.3934 | 56.521
CID=249636464 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553598379 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936679930 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054325451 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516523439 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=787438476 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1170520027 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1820485354 | -6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1437403803 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-133441888 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=249639663 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1553601578 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1936683129 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1054322252 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-516532536 | -3 | 10 | 12.2437 | 4 | 4 | 0.8 | 0.77914 | 140.4535 | 10.3426 | 29.6729 | 218.7621 | 209.9563 | 21686.1257 | 0.62944 | 0.0084148 | 9.2682 | 12.2437 | 113.4768 | -3 | 10 | 4 | 4 | 193.5663 | 308.3347 | 22.5743 | 1.5929 | 0.71917 | 110 | 25.8665 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.3391 | 12.2784
CID=787429379 | -3 | 12.5 | 15.5676 | 4 | 6.5 | 1.3 | 0.77914 | 140.4535 | 10.3426 | 32.9806 | 220.3678 | 209.9563 | 23246.712 | 0.71659 | 0.0095479 | 8.1464 | 15.5675 | 126.8196 | -3 | 12.5 | 4 | 6.5 | 193.5663 | 335.3618 | 25.6452 | 1.7325 | 0.74592 | 110 | 31.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9798 | 15.6157
CID=1170510930 | -3 | 15 | 19.1876 | 4 | 9 | 1.8 | 0.77914 | 140.4535 | 10.3426 | 36.3054 | 221.9458 | 209.9563 | 24644.3851 | 0.80234 | 0.01085 | 7.2613 | 19.1876 | 139.3274 | -3 | 15 | 4 | 9 | 193.5663 | 364.1604 | 28.5788 | 1.8813 | 0.77101 | 110 | 37.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.1813 | 19.2479
CID=-1820494451 | -3 | 17.5 | 23.2476 | 4 | 11.5 | 2.3 | 0.77914 | 140.4535 | 10.3426 | 39.6477 | 223.4962 | 209.9563 | 25955.7721 | 0.88627 | 0.012364 | 6.4927 | 23.2476 | 150.9396 | -3 | 17.5 | 4 | 11.5 | 193.5663 | 394.805 | 31.599 | 2.0396 | 0.79488 | 110 | 44.4359 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3228 | 23.3226
CID=-1437412900 | -3 | 20 | 26.6655 | 4 | 14 | 2.8 | 0.77914 | 140.4535 | 10.3426 | 43.0083 | 225.0194 | 209.9563 | 26946.8452 | 0.94716 | 0.013741 | 5.93 | 26.6655 | 158.1263 | -3 | 20 | 4 | 14 | 193.5663 | 427.3713 | 34.1917 | 2.2079 | 0.81198 | 110 | 49.8954 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6291 | 26.7511
CID=-133450985 | -3 | 22.5 | 31.5403 | 4 | 16.5 | 3.3 | 0.77914 | 140.4535 | 10.3426 | 46.3877 | 226.5154 | 209.9563 | 28157.1163 | 1.0279 | 0.015676 | 5.3306 | 31.5403 | 168.1297 | -3 | 22.5 | 4 | 16.5 | 193.5663 | 461.9363 | 37.3764 | 2.3864 | 0.83241 | 110 | 57.5687 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.6237 | 31.6404
CID=249630566 | -3 | 25 | 36.8227 | 4 | 19 | 3.8 | 0.77914 | 140.4535 | 10.3426 | 49.7865 | 227.9846 | 209.9563 | 29303.7435 | 1.1067 | 0.017844 | 4.814 | 36.8228 | 177.265 | -3 | 25 | 4 | 19 | 193.5663 | 498.5781 | 40.5916 | 2.5757 | 0.8502 | 110 | 65.8034 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2655 | 36.9411
CID=1553592481 | -3 | 27.5 | 42.505 | 4 | 21.5 | 4.3 | 0.77914 | 140.4535 | 10.3426 | 53.2055 | 229.4271 | 209.9563 | 30347.4109 | 1.1839 | 0.020256 | 4.3659 | 42.505 | 185.5714 | -3 | 27.5 | 4 | 21.5 | 193.5663 | 537.3762 | 43.8298 | 2.7762 | 0.86533 | 110 | 74.6297 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.5311 | 42.6405
CID=1936674032 | -3 | 30 | 46.5925 | 4 | 24 | 4.8 | 0.77914 | 140.4535 | 10.3426 | 56.6452 | 230.8431 | 209.9563 | 31015.387 | 1.2381 | 0.022201 | 4.074 | 46.5924 | 189.8164 | -3 | 30 | 4 | 24 | 193.5663 | 578.4112 | 46.2115 | 2.9882 | 0.87415 | 110 | 80.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4826 | 46.7387
CID=-1054331349 | -3 | 32.5 | 52.3882 | 4 | 26.5 | 5.3 | 0.77914 | 140.4535 | 10.3426 | 60.1065 | 232.2329 | 209.9563 | 31928.3056 | 1.3122 | 0.024879 | 3.7533 | 52.3882 | 196.6313 | -3 | 32.5 | 4 | 26.5 | 193.5663 | 621.7653 | 49.122 | 3.2122 | 0.88426 | 110 | 90.0138 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0462 | 52.5507
CID=-516537785 | -3 | 35 | 57.9351 | 4 | 29 | 5.8 | 0.77914 | 140.4535 | 10.3426 | 63.59 | 233.5967 | 209.9563 | 32809.0983 | 1.3843 | 0.027595 | 3.4974 | 57.9351 | 202.6205 | -3 | 35 | 4 | 29 | 193.5663 | 667.522 | 51.6988 | 3.4485 | 0.89184 | 110 | 98.6979 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9114 | 58.111
CID=787424130 | -3 | 37.5 | 63.1465 | 4 | 31.5 | 6.3 | 0.77914 | 140.4535 | 10.3426 | 67.0967 | 234.9345 | 209.9563 | 33549.3078 | 1.4488 | 0.030317 | 3.2778 | 63.1465 | 206.9803 | -3 | 37.5 | 4 | 31.5 | 193.5663 | 715.7661 | 54.1061 | 3.6978 | 0.8975 | 110 | 106.8986 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.5999 | 63.3351
CID=1170505681 | -3 | 40 | 63.2831 | 4 | 34 | 6.8 | 0.77914 | 140.4535 | 10.3426 | 70.6273 | 236.2466 | 209.9563 | 33624.0563 | 1.4479 | 0.031141 | 3.1879 | 63.2831 | 201.7383 | -3 | 40 | 4 | 34 | 193.5663 | 766.5841 | 55.0891 | 3.9603 | 0.89763 | 110 | 107.1141 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1961 | 63.4544
CID=-1820499700 | -3 | 42.5 | 62.8961 | 4 | 36.5 | 7.3 | 0.77914 | 140.4535 | 10.3426 | 74.1828 | 237.5332 | 209.9563 | 33638.0307 | 1.4258 | 0.031796 | 3.0779 | 62.8962 | 193.5857 | -3 | 42.5 | 4 | 36.5 | 193.5663 | 820.0642 | 56.3555 | 4.2366 | 0.89725 | 110 | 106.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.3922 | 63.0494
CID=-1437418149 | -3 | 45 | 62.896 | 4 | 39 | 7.8 | 0.77914 | 140.4535 | 10.3426 | 77.7643 | 238.7945 | 209.9563 | 33675.7468 | 1.4232 | 0.032658 | 2.9912 | 62.896 | 188.1342 | -3 | 45 | 4 | 39 | 193.5663 | 876.2965 | 57.3974 | 4.5271 | 0.89725 | 110 | 106.5035 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8726 | 36.8219 | 63.027
CID=-133456234 | -3 | 47.5 | 63.3851 | 4 | 41.5 | 8.3 | 0.77914 | 140.4535 | 10.3426 | 81.3729 | 240.0305 | 209.9563 | 33845.0934 | 1.4023 | 0.033788 | 2.8447 | 63.3851 | 180.3097 | -3 | 47.5 | 4 | 41.5 | 193.5663 | 935.3729 | 59.2596 | 4.8323 | 0.89773 | 110 | 107.2751 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.7507 | 63.4939
CID=249625317 | -3 | 50 | 63.7103 | 4 | 44 | 8.8 | 0.77914 | 140.4535 | 10.3426 | 85.0099 | 241.2416 | 209.9563 | 33997.2329 | 1.3797 | 0.034917 | 2.7059 | 63.7103 | 172.3938 | -3 | 50 | 4 | 44 | 193.5663 | 997.3873 | 61.1251 | 5.1527 | 0.89804 | 110 | 107.7884 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.6377 | 63.7961
CID=1553587232 | -3 | 52.5 | 63.5624 | 4 | 46.5 | 9.3 | 0.77914 | 140.4535 | 10.3426 | 88.6765 | 242.4277 | 209.9563 | 34112.5319 | 1.3559 | 0.035904 | 2.587 | 63.5624 | 164.4373 | -3 | 52.5 | 4 | 46.5 | 193.5663 | 1062.4359 | 62.8053 | 5.4887 | 0.8979 | 110 | 107.5549 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7787 | 53.5574 | 63.6127
CID=1936668783 | -3 | 55 | 61.3661 | 4 | 49 | 9.8 | 0.77914 | 140.4535 | 10.3426 | 92.3743 | 243.5891 | 209.9563 | 34145.4634 | 0.99406 | 0.035397 | 1.9438 | 60.1317 | 116.8839 | -3 | 55 | 4 | 49 | 193.5663 | 1130.6169 | 74.5757 | 5.841 | 0.89438 | 97.0873 | 102.1494 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.1316 | 61.3723
CID=-1054336598 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1454135787 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554892336 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153788043 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432498874 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533255423 | -3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=634011972 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074668407 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488381490 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387624941 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-286868392 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1454130538 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554887087 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153793292 | 0 | 12.5 | 13.1498 | 4 | 6.5 | 1.3 | 0.77903 | 140.5275 | 11.5059 | 32.9806 | 220.3371 | 212.0278 | 21493.5166 | 0.69349 | 0.0087312 | 9.4426 | 13.1498 | 124.1681 | 0 | 12.5 | 4 | 6.5 | 216.4944 | 335.3618 | 25.0674 | 1.5491 | 0.72684 | 110 | 27.4875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.6702 | 13.1874
CID=432493625 | 0 | 15 | 15.9806 | 4 | 9 | 1.8 | 0.77903 | 140.5275 | 11.5059 | 36.3054 | 221.9148 | 212.0278 | 22760.1491 | 0.76568 | 0.0097408 | 8.4194 | 15.9806 | 134.5469 | 0 | 15 | 4 | 9 | 216.4944 | 364.1604 | 27.7257 | 1.6821 | 0.74898 | 110 | 32.4175 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.883 | 16.0314
CID=533250174 | 0 | 17.5 | 19.7527 | 4 | 11.5 | 2.3 | 0.77903 | 140.5275 | 11.5059 | 39.6477 | 223.465 | 212.0278 | 24161.1879 | 0.85932 | 0.011107 | 7.4993 | 19.7527 | 148.1303 | 0 | 17.5 | 4 | 11.5 | 216.4944 | 394.805 | 30.5899 | 1.8236 | 0.77459 | 110 | 38.7446 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2692 | 19.8154
CID=634006723 | 0 | 20 | 23.9935 | 4 | 14 | 2.8 | 0.77903 | 140.5275 | 11.5059 | 43.0083 | 224.9879 | 212.0278 | 25470.3152 | 0.9511 | 0.012701 | 6.6999 | 23.9935 | 160.7539 | 0 | 20 | 4 | 14 | 216.4944 | 427.3713 | 33.543 | 1.9741 | 0.79883 | 110 | 45.6349 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.7353 | 24.0702
CID=-2074673656 | 0 | 22.5 | 28.0088 | 4 | 16.5 | 3.3 | 0.77903 | 140.5275 | 11.5059 | 46.3877 | 226.4837 | 212.0278 | 26554.3776 | 1.0267 | 0.014297 | 6.0716 | 28.0088 | 170.0588 | 0 | 22.5 | 4 | 16.5 | 216.4944 | 461.9363 | 36.2816 | 2.1337 | 0.81804 | 110 | 52.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1199 | 28.0987
CID=-488386739 | 0 | 25 | 32.5753 | 4 | 19 | 3.8 | 0.77903 | 140.5275 | 11.5059 | 49.7865 | 227.9526 | 212.0278 | 27642.8628 | 1.1053 | 0.016159 | 5.5051 | 32.5754 | 179.329 | 0 | 25 | 4 | 19 | 216.4944 | 498.5781 | 39.1429 | 2.303 | 0.83622 | 110 | 59.1868 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7385 | 32.6801
CID=-387630190 | 0 | 27.5 | 38.1997 | 4 | 21.5 | 4.3 | 0.77903 | 140.5275 | 11.5059 | 53.2055 | 229.3949 | 212.0278 | 28812.2403 | 1.1916 | 0.018479 | 4.9541 | 38.1997 | 189.2464 | 0 | 27.5 | 4 | 21.5 | 216.4944 | 537.3762 | 42.369 | 2.4822 | 0.85422 | 110 | 67.9434 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9765 | 38.3214
CID=-286873641 | 0 | 30 | 44.0346 | 4 | 24 | 4.8 | 0.77903 | 140.5275 | 11.5059 | 56.6452 | 230.8107 | 212.0278 | 29854.1359 | 1.2758 | 0.020985 | 4.502 | 44.0346 | 198.2432 | 0 | 30 | 4 | 24 | 216.4944 | 578.4112 | 45.4566 | 2.6717 | 0.86881 | 110 | 77.0057 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9309 | 44.1758
CID=1454129385 | 0 | 32.5 | 50.0674 | 4 | 26.5 | 5.3 | 0.77903 | 140.5275 | 11.5059 | 60.1065 | 232.2002 | 212.0278 | 30781.1478 | 1.3563 | 0.023685 | 4.1154 | 50.0674 | 206.048 | 0 | 32.5 | 4 | 26.5 | 216.4944 | 621.7653 | 48.4814 | 2.872 | 0.88051 | 110 | 86.3926 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.0018 | 50.2286
CID=1554885934 | 0 | 35 | 54.66 | 4 | 29 | 5.8 | 0.77903 | 140.5275 | 11.5059 | 63.59 | 233.5637 | 212.0278 | 31411.9151 | 1.4153 | 0.025973 | 3.8436 | 54.66 | 210.0892 | 0 | 35 | 4 | 29 | 216.4944 | 667.522 | 50.8647 | 3.0833 | 0.88759 | 110 | 93.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6907 | 54.8307
CID=-1153794445 | 0 | 37.5 | 61.0741 | 4 | 31.5 | 6.3 | 0.77903 | 140.5275 | 11.5059 | 67.0967 | 234.9013 | 212.0278 | 32346.4223 | 1.4943 | 0.029082 | 3.5461 | 61.0741 | 216.5772 | 0 | 37.5 | 4 | 31.5 | 216.4944 | 715.7661 | 53.7491 | 3.3062 | 0.8954 | 110 | 103.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6252 | 61.2623
CID=432492472 | 0 | 40 | 66.9802 | 4 | 34 | 6.8 | 0.77903 | 140.5275 | 11.5059 | 70.6273 | 236.2131 | 212.0278 | 33133.6611 | 1.5714 | 0.032151 | 3.3174 | 66.9802 | 222.2012 | 0 | 40 | 4 | 34 | 216.4944 | 766.5841 | 56.1961 | 3.5409 | 0.90092 | 110 | 112.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4682 | 67.1838
CID=533249021 | 0 | 42.5 | 70.2545 | 4 | 36.5 | 7.3 | 0.77903 | 140.5275 | 11.5059 | 74.1828 | 237.4995 | 212.0278 | 33592.4681 | 1.6122 | 0.034313 | 3.1632 | 70.2545 | 222.2269 | 0 | 42.5 | 4 | 36.5 | 216.4944 | 820.0642 | 57.95 | 3.7879 | 0.90342 | 110 | 118.1514 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9202 | 70.4572
CID=634005570 | 0 | 45 | 70.8314 | 4 | 39 | 7.8 | 0.77903 | 140.5275 | 11.5059 | 77.7643 | 238.7605 | 212.0278 | 33713.8909 | 1.6109 | 0.03547 | 3.0535 | 70.8314 | 216.2807 | 0 | 45 | 4 | 39 | 216.4944 | 876.2965 | 59.2406 | 4.0477 | 0.90383 | 110 | 119.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7902 | 71.0175
CID=-2074674809 | 0 | 47.5 | 70.42 | 4 | 41.5 | 8.3 | 0.77903 | 140.5275 | 11.5059 | 81.3729 | 239.9963 | 212.0278 | 33707.8718 | 1.5865 | 0.036273 | 2.9436 | 70.4199 | 207.2848 | 0 | 47.5 | 4 | 41.5 | 216.4944 | 935.3729 | 60.5868 | 4.3205 | 0.90354 | 110 | 118.4142 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3283 | 70.5862
CID=-488387892 | 0 | 50 | 70.1382 | 4 | 44 | 8.8 | 0.77903 | 140.5275 | 11.5059 | 85.0099 | 241.2071 | 212.0278 | 33729.6497 | 1.5833 | 0.037187 | 2.8673 | 70.1382 | 201.1086 | 0 | 50 | 4 | 44 | 216.4944 | 997.3873 | 61.5699 | 4.607 | 0.90334 | 110 | 117.9666 | 0 | 0 | 0 | 0 | 0 | 0 | 4.869 | 42.4342 | 70.2774
CID=-387631343 | 0 | 52.5 | 70.8548 | 4 | 46.5 | 9.3 | 0.77903 | 140.5275 | 11.5059 | 88.6765 | 242.393 | 212.0278 | 33917.6568 | 1.5598 | 0.038618 | 2.7155 | 70.8548 | 192.409 | 0 | 52.5 | 4 | 46.5 | 216.4944 | 1062.4359 | 63.5949 | 4.9075 | 0.90385 | 110 | 119.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.5636 | 70.9719
CID=-286874794 | 0 | 55 | 71.1687 | 4 | 49 | 9.8 | 0.77903 | 140.5275 | 11.5059 | 92.3743 | 243.5541 | 212.0278 | 34061.4709 | 1.5347 | 0.039959 | 2.5802 | 71.1687 | 183.6321 | 0 | 55 | 4 | 49 | 216.4944 | 1130.6169 | 65.5087 | 5.2224 | 0.90406 | 110 | 119.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.837 | 71.2608
CID=1454132584 | 0 | 57.5 | 71.0037 | 4 | 51.5 | 10.3 | 0.77903 | 140.5275 | 11.5059 | 96.1049 | 244.6907 | 212.0278 | 34176.2928 | 1.508 | 0.041165 | 2.462 | 71.0037 | 174.8086 | 0 | 57.5 | 4 | 51.5 | 216.4944 | 1202.031 | 67.273 | 5.5522 | 0.90395 | 110 | 119.3419 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7738 | 60.8149 | 71.0549
CID=1554889133 | 0 | 60 | 68.4457 | 4 | 54 | 10.8 | 0.77903 | 140.5275 | 11.5059 | 99.8699 | 245.8028 | 212.0278 | 34214.8219 | 1.1117 | 0.040731 | 1.8506 | 67.3745 | 124.6825 | 0 | 60 | 4 | 54 | 216.4944 | 1276.7811 | 78.7718 | 5.8975 | 0.90124 | 97.0873 | 113.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.3745 | 68.4511
CID=-1153791246 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432495671 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533252220 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=634008769 | 0 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074671610 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488384693 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387628144 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-286871595 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1454139887 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554896436 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153783943 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432502974 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533259523 | 3 | 15 | 9.7372 | 4 | 9 | 1.8 | 0.77904 | 140.5554 | 12.7698 | 36.3054 | 221.9177 | 214.0896 | 19392.8187 | 0.61222 | 0.0078452 | 11.1781 | 9.7372 | 108.8437 | 3 | 15 | 4 | 9 | 241.4641 | 364.1604 | 24.6652 | 1.5081 | 0.69631 | 87.9223 | 21.2464 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.0686 | 9.7556
CID=634016072 | 3 | 17.5 | 16.3566 | 4 | 11.5 | 2.3 | 0.77904 | 140.5554 | 12.7698 | 39.6477 | 223.4679 | 214.0896 | 22275.2918 | 0.81602 | 0.0099271 | 8.7027 | 16.3566 | 142.3473 | 3 | 17.5 | 4 | 11.5 | 241.4641 | 394.805 | 29.8294 | 1.635 | 0.75172 | 110 | 33.0592 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.1159 | 16.4081
CID=-2074664307 | 3 | 20 | 20.3195 | 4 | 14 | 2.8 | 0.77904 | 140.5554 | 12.7698 | 43.0083 | 224.9908 | 214.0896 | 23687.7896 | 0.9181 | 0.011372 | 7.73 | 20.3195 | 157.07 | 3 | 20 | 4 | 14 | 241.4641 | 427.3713 | 32.6724 | 1.7699 | 0.77809 | 110 | 39.6771 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.4444 | 20.3842
CID=-488377390 | 3 | 22.5 | 24.7428 | 4 | 16.5 | 3.3 | 0.77904 | 140.5554 | 12.7698 | 46.3877 | 226.4866 | 214.0896 | 25000.1539 | 1.0182 | 0.013046 | 6.9009 | 24.7427 | 170.7465 | 3 | 22.5 | 4 | 16.5 | 241.4641 | 461.9363 | 35.5639 | 1.9131 | 0.80267 | 110 | 46.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.8813 | 24.8225
CID=-387620841 | 3 | 25 | 29.6374 | 4 | 19 | 3.8 | 0.77904 | 140.5554 | 12.7698 | 49.7865 | 227.9556 | 214.0896 | 26234.3324 | 1.1162 | 0.014963 | 6.1879 | 29.6374 | 183.3948 | 3 | 25 | 4 | 19 | 241.4641 | 498.5781 | 38.5111 | 2.0648 | 0.82494 | 110 | 54.5853 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.3039 | 29.7346
CID=-286864292 | 3 | 27.5 | 33.6446 | 4 | 21.5 | 4.3 | 0.77904 | 140.5554 | 12.7698 | 53.2055 | 229.3978 | 214.0896 | 27153.2382 | 1.1858 | 0.016664 | 5.6704 | 33.6446 | 190.7776 | 3 | 27.5 | 4 | 21.5 | 241.4641 | 537.3762 | 41.0245 | 2.2255 | 0.83998 | 110 | 60.8555 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.151 | 33.7526
CID=1454134638 | 3 | 30 | 39.4396 | 4 | 24 | 4.8 | 0.77904 | 140.5554 | 12.7698 | 56.6452 | 230.8137 | 214.0896 | 28293.1683 | 1.2799 | 0.01908 | 5.1094 | 39.4396 | 201.5111 | 3 | 30 | 4 | 24 | 241.4641 | 578.4112 | 44.1274 | 2.3954 | 0.85763 | 110 | 69.8694 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.3139 | 39.5659
CID=1554891187 | 3 | 32.5 | 45.6246 | 4 | 26.5 | 5.3 | 0.77904 | 140.5554 | 12.7698 | 60.1065 | 232.2032 | 214.0896 | 29365.2159 | 1.3718 | 0.021753 | 4.6297 | 45.6246 | 211.2283 | 3 | 32.5 | 4 | 26.5 | 241.4641 | 621.7653 | 47.2192 | 2.575 | 0.8722 | 110 | 79.4768 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.265 | 45.7721
CID=-1153789192 | 3 | 35 | 52.2828 | 4 | 29 | 5.8 | 0.77904 | 140.5554 | 12.7698 | 63.59 | 233.5667 | 214.0896 | 30354.3691 | 1.4615 | 0.024733 | 4.2072 | 52.2828 | 219.9619 | 3 | 35 | 4 | 29 | 241.4641 | 667.522 | 50.3605 | 2.7645 | 0.8841 | 110 | 89.8491 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.9753 | 52.4501
CID=432497725 | 3 | 37.5 | 56.9507 | 4 | 31.5 | 6.3 | 0.77904 | 140.5554 | 12.7698 | 67.0967 | 234.9043 | 214.0896 | 30975.441 | 1.5231 | 0.027102 | 3.9313 | 56.9507 | 223.8896 | 3 | 37.5 | 4 | 31.5 | 241.4641 | 715.7661 | 52.6878 | 2.9643 | 0.89063 | 110 | 97.1536 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.2782 | 57.13
CID=533254274 | 3 | 40 | 63.6522 | 4 | 34 | 6.8 | 0.77904 | 140.5554 | 12.7698 | 70.6273 | 236.2162 | 214.0896 | 31822.6263 | 1.6092 | 0.030388 | 3.627 | 63.6522 | 230.865 | 3 | 40 | 4 | 34 | 241.4641 | 766.5841 | 55.5146 | 3.1747 | 0.89798 | 110 | 107.6966 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.2945 | 63.85
CID=634010823 | 3 | 42.5 | 70.2327 | 4 | 36.5 | 7.3 | 0.77904 | 140.5554 | 12.7698 | 74.1828 | 237.5026 | 214.0896 | 32681.0578 | 1.6929 | 0.033799 | 3.3724 | 70.2327 | 236.8494 | 3 | 42.5 | 4 | 36.5 | 241.4641 | 820.0642 | 58.1403 | 3.3962 | 0.90341 | 110 | 118.1166 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2941 | 70.4485
CID=-2074669556 | 3 | 45 | 76.7755 | 4 | 39 | 7.8 | 0.77904 | 140.5554 | 12.7698 | 77.7643 | 238.7637 | 214.0896 | 33429.6554 | 1.7753 | 0.037381 | 3.1524 | 76.7754 | 242.0236 | 3 | 45 | 4 | 39 | 241.4641 | 876.2965 | 60.624 | 3.6291 | 0.90748 | 110 | 128.5413 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.628 | 77.0074
CID=-488382639 | 3 | 47.5 | 77.8063 | 4 | 41.5 | 8.3 | 0.77904 | 140.5554 | 12.7698 | 81.3729 | 239.9995 | 214.0896 | 33595.4353 | 1.7887 | 0.038833 | 3.0511 | 77.8063 | 237.3947 | 3 | 47.5 | 4 | 41.5 | 241.4641 | 935.3729 | 61.8305 | 3.8738 | 0.90802 | 110 | 130.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4646 | 78.0241
CID=-387626090 | 3 | 50 | 78.1942 | 4 | 44 | 8.8 | 0.77904 | 140.5554 | 12.7698 | 85.0099 | 241.2103 | 214.0896 | 33685.7978 | 1.7854 | 0.040096 | 2.9472 | 78.1942 | 230.4566 | 3 | 50 | 4 | 44 | 241.4641 | 997.3873 | 63.1199 | 4.1306 | 0.90822 | 110 | 130.8098 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8883 | 38.3198 | 78.3946
CID=-286869541 | 3 | 52.5 | 78.0773 | 4 | 46.5 | 9.3 | 0.77904 | 140.5554 | 12.7698 | 88.6765 | 242.3962 | 214.0896 | 33723.0549 | 1.7599 | 0.041216 | 2.8269 | 78.0773 | 220.7145 | 3 | 52.5 | 4 | 46.5 | 241.4641 | 1062.4359 | 64.6728 | 4.4 | 0.90816 | 110 | 130.6228 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.5765 | 78.2557
CID=1454133485 | 3 | 55 | 77.3015 | 4 | 49 | 9.8 | 0.77904 | 140.5554 | 12.7698 | 92.3743 | 243.5574 | 214.0896 | 33725.2558 | 1.732 | 0.04211 | 2.7272 | 77.3015 | 210.8152 | 3 | 55 | 4 | 49 | 241.4641 | 1130.6169 | 66.0278 | 4.6823 | 0.90776 | 110 | 129.3822 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3691 | 77.4469
CID=1554890034 | 3 | 57.5 | 78.3017 | 4 | 51.5 | 10.3 | 0.77904 | 140.5554 | 12.7698 | 96.1049 | 244.694 | 214.0896 | 33913.983 | 1.7286 | 0.043918 | 2.6047 | 78.3017 | 203.9541 | 3 | 57.5 | 4 | 51.5 | 241.4641 | 1202.031 | 67.7618 | 4.9781 | 0.90827 | 110 | 130.9818 | 0 | 0 | 0 | 0 | 0 | 0 | 4.842 | 53.8459 | 78.4246
CID=-1153790345 | 3 | 60 | 78.5277 | 4 | 54 | 10.8 | 0.77904 | 140.5554 | 12.7698 | 99.8699 | 245.8061 | 214.0896 | 34043.9956 | 1.7007 | 0.045476 | 2.4737 | 78.5277 | 194.2541 | 3 | 60 | 4 | 54 | 241.4641 | 1276.7811 | 69.6981 | 5.2877 | 0.90839 | 110 | 131.3435 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8111 | 59.7005 | 78.6223
CID=432496572 | 3 | 62.5 | 77.7663 | 4 | 56.5 | 11.3 | 0.77904 | 140.5554 | 12.7698 | 103.6713 | 246.8939 | 214.0896 | 33681.8935 | 1.1962 | 0.042237 | 1.9122 | 69.075 | 132.0841 | 3 | 62.5 | 4 | 56.5 | 241.4641 | 1354.9726 | 79.5947 | 5.6115 | 0.90256 | 98.2763 | 116.2788 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.5754 | 77.8125
CID=533253121 | 3 | 65 | 76.053 | 4 | 59 | 11.8 | 0.77904 | 140.5554 | 12.7698 | 107.511 | 247.9576 | 214.0896 | 34259.8998 | 1.2377 | 0.04694 | 1.7561 | 75.117 | 131.9149 | 3 | 65 | 4 | 59 | 241.4641 | 1436.7133 | 83.0361 | 5.95 | 0.90655 | 97.0873 | 125.8931 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.117 | 76.0577
CID=634009670 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074670709 | 3 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488383792 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387627243 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-286870694 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1454136684 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1554893233 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1153787146 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=432499771 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=533256320 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=634012869 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2074667510 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-488380593 | 6 | 20 | 16.6212 | 4 | 14 | 2.8 | 0.77916 | 140.5359 | 14.1408 | 43.0083 | 225.0254 | 216.1405 | 21771.6415 | 0.86768 | 0.010084 | 9.038 | 16.6212 | 150.2226 | 6 | 20 | 4 | 14 | 268.5935 | 427.3713 | 31.8714 | 1.5911 | 0.75363 | 110 | 33.509 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.8403 | 16.6703
CID=-387624044 | 6 | 22.5 | 20.8656 | 4 | 16.5 | 3.3 | 0.77916 | 140.5359 | 14.1408 | 46.3877 | 226.5215 | 216.1405 | 23222.004 | 0.97852 | 0.011636 | 7.9608 | 20.8656 | 166.1069 | 6 | 22.5 | 4 | 16.5 | 268.5935 | 461.9363 | 34.7984 | 1.7198 | 0.78138 | 110 | 40.5717 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.7456 | 20.9315
CID=-286867495 | 6 | 25 | 25.4354 | 4 | 19 | 3.8 | 0.77916 | 140.5359 | 14.1408 | 49.7865 | 227.9908 | 216.1405 | 24523.8432 | 1.0875 | 0.013381 | 7.1126 | 25.4354 | 180.9128 | 6 | 25 | 4 | 19 | 268.5935 | 498.5781 | 37.5991 | 1.8563 | 0.80611 | 110 | 47.9402 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3478 | 25.5163
CID=1454127587 | 6 | 27.5 | 30.5173 | 4 | 21.5 | 4.3 | 0.77916 | 140.5359 | 14.1408 | 53.2055 | 229.4333 | 216.1405 | 25749.2118 | 1.1942 | 0.015388 | 6.3758 | 30.5173 | 194.5734 | 6 | 27.5 | 4 | 21.5 | 268.5935 | 537.3762 | 40.4774 | 2.0007 | 0.82847 | 110 | 55.9663 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.8391 | 30.6162
CID=1554884136 | 6 | 30 | 34.6766 | 4 | 24 | 4.8 | 0.77916 | 140.5359 | 14.1408 | 56.6452 | 230.8494 | 216.1405 | 26657.2917 | 1.2693 | 0.01717 | 5.8383 | 34.6766 | 202.4515 | 6 | 30 | 4 | 24 | 268.5935 | 578.4112 | 42.9548 | 2.1535 | 0.84346 | 110 | 62.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4236 | 34.7884
CID=-1153796243 | 6 | 32.5 | 40.6212 | 4 | 26.5 | 5.3 | 0.77916 | 140.5359 | 14.1408 | 60.1065 | 232.2392 | 216.1405 | 27781.5012 | 1.3717 | 0.019675 | 5.2689 | 40.6212 | 214.0289 | 6 | 32.5 | 4 | 26.5 | 268.5935 | 621.7653 | 45.9357 | 2.3149 | 0.86072 | 110 | 71.7043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.4257 | 40.7528
CID=432490674 | 6 | 35 | 47.2226 | 4 | 29 | 5.8 | 0.77916 | 140.5359 | 14.1408 | 63.59 | 233.603 | 216.1405 | 28888.1584 | 1.4717 | 0.022543 | 4.7542 | 47.2226 | 224.5073 | 6 | 35 | 4 | 29 | 268.5935 | 667.522 | 49.0674 | 2.4852 | 0.87537 | 110 | 81.9621 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.097 | 47.374
CID=533247223 | 6 | 37.5 | 54.019 | 4 | 31.5 | 6.3 | 0.77916 | 140.5359 | 14.1408 | 67.0967 | 234.9409 | 216.1405 | 29867.8253 | 1.5694 | 0.025627 | 4.3302 | 54.019 | 233.9133 | 6 | 37.5 | 4 | 31.5 | 268.5935 | 715.7661 | 52.0632 | 2.6649 | 0.88668 | 110 | 92.5625 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.3967 | 54.193
CID=634003772 | 6 | 40 | 61.1731 | 4 | 34 | 6.8 | 0.77916 | 140.5359 | 14.1408 | 70.6273 | 236.2531 | 216.1405 | 30761.1713 | 1.6646 | 0.029004 | 3.9596 | 61.1731 | 242.222 | 6 | 40 | 4 | 34 | 268.5935 | 766.5841 | 55.0506 | 2.8541 | 0.8955 | 110 | 103.7883 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.7901 | 61.371
CID=-2074676607 | 6 | 42.5 | 66.2079 | 4 | 36.5 | 7.3 | 0.77916 | 140.5359 | 14.1408 | 74.1828 | 237.5397 | 216.1405 | 31325.8563 | 1.7293 | 0.03172 | 3.7078 | 66.2079 | 245.4834 | 6 | 42.5 | 4 | 36.5 | 268.5935 | 820.0642 | 57.3381 | 3.0532 | 0.90027 | 110 | 111.7356 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0078 | 66.415
CID=-488389690 | 6 | 45 | 73.5789 | 4 | 39 | 7.8 | 0.77916 | 140.5359 | 14.1408 | 77.7643 | 238.801 | 216.1405 | 32197.7587 | 1.8206 | 0.03553 | 3.4239 | 73.5789 | 251.9284 | 6 | 45 | 4 | 39 | 268.5935 | 876.2965 | 60.1549 | 3.2625 | 0.90563 | 110 | 123.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0513 | 73.8077
CID=-387633141 | 6 | 47.5 | 80.401 | 4 | 41.5 | 8.3 | 0.77916 | 140.5359 | 14.1408 | 81.3729 | 240.0371 | 216.1405 | 32963.0851 | 1.9096 | 0.039323 | 3.2009 | 80.401 | 257.3521 | 6 | 47.5 | 4 | 41.5 | 268.5935 | 935.3729 | 62.6029 | 3.4825 | 0.90928 | 110 | 134.3437 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.5834 | 80.6463
CID=-286876592 | 6 | 50 | 86.2021 | 4 | 44 | 8.8 | 0.77916 | 140.5359 | 14.1408 | 85.0099 | 241.2482 | 216.1405 | 33578.8658 | 1.9807 | 0.042898 | 3.013 | 86.2021 | 259.725 | 6 | 50 | 4 | 44 | 268.5935 | 997.3873 | 64.8344 | 3.7134 | 0.91165 | 110 | 143.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.1297 | 86.4588
CID=1454122338 | 6 | 52.5 | 86.3264 | 4 | 46.5 | 9.3 | 0.77916 | 140.5359 | 14.1408 | 88.6765 | 242.4344 | 216.1405 | 33637.8385 | 1.9792 | 0.044187 | 2.9224 | 86.3264 | 252.2799 | 6 | 52.5 | 4 | 46.5 | 268.5935 | 1062.4359 | 65.9849 | 3.9556 | 0.91169 | 110 | 143.8633 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.549 | 86.5615
CID=1554878887 | 6 | 55 | 85.673 | 4 | 49 | 9.8 | 0.77916 | 140.5359 | 14.1408 | 92.3743 | 243.5958 | 216.1405 | 33638.3199 | 1.9487 | 0.04521 | 2.8152 | 85.673 | 241.1879 | 6 | 55 | 4 | 49 | 268.5935 | 1130.6169 | 67.3891 | 4.2094 | 0.91146 | 110 | 142.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.4253 | 85.8853
CID=-1153801492 | 6 | 57.5 | 86.3846 | 4 | 51.5 | 10.3 | 0.77916 | 140.5359 | 14.1408 | 96.1049 | 244.7327 | 216.1405 | 33735.973 | 1.947 | 0.046949 | 2.7055 | 86.3846 | 233.7144 | 6 | 57.5 | 4 | 51.5 | 268.5935 | 1202.031 | 68.8976 | 4.4753 | 0.91172 | 110 | 143.9571 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.4863 | 86.5751
CID=432485425 | 6 | 60 | 85.8533 | 4 | 54 | 10.8 | 0.77916 | 140.5359 | 14.1408 | 99.8699 | 245.8451 | 216.1405 | 33775.5629 | 1.9162 | 0.048212 | 2.5951 | 85.8533 | 222.8001 | 6 | 60 | 4 | 54 | 268.5935 | 1276.7811 | 70.4775 | 4.7536 | 0.91152 | 110 | 143.1016 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7344 | 86.0097
CID=533241974 | 6 | 62.5 | 86.8922 | 4 | 56.5 | 11.3 | 0.77916 | 140.5359 | 14.1408 | 103.6713 | 246.9332 | 216.1405 | 33950.0413 | 1.9123 | 0.05036 | 2.4752 | 86.8922 | 215.0775 | 6 | 62.5 | 4 | 56.5 | 268.5935 | 1354.9726 | 72.2693 | 5.0447 | 0.91189 | 110 | 144.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8385 | 60.5946 | 87.0244
CID=633998523 | 6 | 65 | 87.0743 | 4 | 59 | 11.8 | 0.77916 | 140.5359 | 14.1408 | 107.511 | 247.9972 | 216.1405 | 34075.076 | 1.8812 | 0.052235 | 2.3469 | 87.0743 | 204.3539 | 6 | 65 | 4 | 59 | 268.5935 | 1436.7133 | 74.2637 | 5.349 | 0.91196 | 110 | 145.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8076 | 67.1624 | 87.1744
CID=-2074681856 | 6 | 67.5 | 86.1835 | 4 | 61.5 | 12.3 | 0.77916 | 140.5359 | 14.1408 | 111.3912 | 249.0371 | 216.1405 | 33761.0786 | 1.2926 | 0.048822 | 1.7562 | 77.0983 | 135.3988 | 6 | 67.5 | 4 | 61.5 | 268.5935 | 1522.1141 | 85.2725 | 5.667 | 0.90765 | 95.9768 | 129.0573 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.7476 | 86.2309
CID=-488394939 | 6 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-387638390 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-286881841 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599545170 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295583255 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477151708 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826810207 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678664806 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625297109 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443728656 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747690571 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853661398 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137343983 | 9 | 22.5 | 17.5458 | 4 | 16.5 | 3.3 | 0.77937 | 140.4677 | 15.6257 | 46.3877 | 226.5858 | 218.1794 | 21503.5638 | 0.94281 | 0.010451 | 9.2311 | 17.5458 | 161.9677 | 9 | 22.5 | 4 | 16.5 | 298.0034 | 461.9363 | 34.2662 | 1.5501 | 0.76011 | 110 | 35.0713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3644 | 17.597
CID=-1599550419 | 9 | 25 | 21.3475 | 4 | 19 | 3.8 | 0.77937 | 140.4677 | 15.6257 | 49.7865 | 228.0555 | 218.1794 | 22748.0147 | 1.0405 | 0.011886 | 8.2078 | 21.3475 | 175.2165 | 9 | 25 | 4 | 19 | 298.0034 | 498.5781 | 36.9251 | 1.6731 | 0.78422 | 110 | 41.3582 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.5779 | 21.4167
CID=-295588504 | 9 | 27.5 | 26.1001 | 4 | 21.5 | 4.3 | 0.77937 | 140.4677 | 15.6257 | 53.2055 | 229.4986 | 218.1794 | 24055.4314 | 1.1589 | 0.013716 | 7.3249 | 26.1001 | 191.1817 | 9 | 27.5 | 4 | 21.5 | 298.0034 | 537.3762 | 39.6806 | 1.8033 | 0.80932 | 110 | 48.998 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.3386 | 26.1844
CID=-477156957 | 9 | 30 | 31.4003 | 4 | 24 | 4.8 | 0.77937 | 140.4677 | 15.6257 | 56.6452 | 230.9152 | 218.1794 | 25282.0424 | 1.2747 | 0.015825 | 6.5577 | 31.4003 | 205.9126 | 9 | 30 | 4 | 24 | 298.0034 | 578.4112 | 42.5183 | 1.941 | 0.83188 | 110 | 57.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.0478 | 31.5026
CID=826804958 | 9 | 32.5 | 37.2171 | 4 | 26.5 | 5.3 | 0.77937 | 140.4677 | 15.6257 | 60.1065 | 232.3055 | 218.1794 | 26441.3124 | 1.3882 | 0.01822 | 5.8962 | 37.2171 | 219.4383 | 9 | 32.5 | 4 | 26.5 | 298.0034 | 621.7653 | 45.4056 | 2.0864 | 0.85138 | 110 | 66.4165 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.9917 | 37.3388
CID=-678670055 | 9 | 35 | 41.8531 | 4 | 29 | 5.8 | 0.77937 | 140.4677 | 15.6257 | 63.59 | 233.6698 | 218.1794 | 27299.6002 | 1.467 | 0.020304 | 5.4184 | 41.8531 | 226.7768 | 9 | 35 | 4 | 29 | 298.0034 | 667.522 | 47.8605 | 2.24 | 0.86378 | 110 | 73.6174 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.0271 | 41.988
CID=625291860 | 9 | 37.5 | 48.6592 | 4 | 31.5 | 6.3 | 0.77937 | 140.4677 | 15.6257 | 67.0967 | 235.0082 | 218.1794 | 28378.2749 | 1.5757 | 0.023294 | 4.8923 | 48.6592 | 238.0549 | 9 | 37.5 | 4 | 31.5 | 298.0034 | 715.7661 | 50.8977 | 2.4019 | 0.87804 | 110 | 84.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4302 | 48.8161
CID=443723407 | 9 | 40 | 55.8126 | 4 | 34 | 6.8 | 0.77937 | 140.4677 | 15.6257 | 70.6273 | 236.3208 | 218.1794 | 29381.178 | 1.6817 | 0.026567 | 4.446 | 55.8126 | 248.1456 | 9 | 40 | 4 | 34 | 298.0034 | 766.5841 | 53.8873 | 2.5724 | 0.88915 | 110 | 95.3699 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.739 | 55.9939
CID=1747685322 | 9 | 42.5 | 63.5212 | 4 | 36.5 | 7.3 | 0.77937 | 140.4677 | 15.6257 | 74.1828 | 237.608 | 218.1794 | 30318.7922 | 1.7853 | 0.030224 | 4.0471 | 63.5212 | 257.0785 | 9 | 42.5 | 4 | 36.5 | 298.0034 | 820.0642 | 56.9483 | 2.7519 | 0.89786 | 110 | 107.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9419 | 63.7251
CID=853656149 | 9 | 45 | 68.786 | 4 | 39 | 7.8 | 0.77937 | 140.4677 | 15.6257 | 77.7643 | 238.8698 | 218.1794 | 30896.104 | 1.8545 | 0.033098 | 3.7856 | 68.786 | 260.3956 | 9 | 45 | 4 | 39 | 298.0034 | 876.2965 | 59.2407 | 2.9406 | 0.90234 | 110 | 115.8203 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6277 | 69.0029
CID=-2137349232 | 9 | 47.5 | 76.4455 | 4 | 41.5 | 8.3 | 0.77937 | 140.4677 | 15.6257 | 81.3729 | 240.1064 | 218.1794 | 31676.7204 | 1.9536 | 0.037114 | 3.4962 | 76.4455 | 267.267 | 9 | 47.5 | 4 | 41.5 | 298.0034 | 935.3729 | 62.0034 | 3.1388 | 0.9073 | 110 | 128.0141 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.871 | 76.6845
CID=-1599551572 | 9 | 50 | 84.1858 | 4 | 44 | 8.8 | 0.77937 | 140.4677 | 15.6257 | 85.0099 | 241.318 | 218.1794 | 32510.8489 | 2.0497 | 0.041391 | 3.2424 | 84.1858 | 272.9599 | 9 | 50 | 4 | 44 | 298.0034 | 997.3873 | 64.6899 | 3.3469 | 0.91089 | 110 | 140.4193 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.4252 | 84.4459
CID=-295589657 | 9 | 52.5 | 89.863 | 4 | 46.5 | 9.3 | 0.77937 | 140.4677 | 15.6257 | 88.6765 | 242.5047 | 218.1794 | 33071.305 | 2.1214 | 0.045025 | 3.0572 | 89.863 | 274.7268 | 9 | 52.5 | 4 | 46.5 | 298.0034 | 1062.4359 | 66.8421 | 3.5652 | 0.91287 | 110 | 149.5648 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2376 | 90.1325
CID=-477158110 | 9 | 55 | 89.884 | 4 | 49 | 9.8 | 0.77937 | 140.4677 | 15.6257 | 92.3743 | 243.6666 | 218.1794 | 33142.7802 | 2.1175 | 0.046358 | 2.9637 | 89.884 | 266.3905 | 9 | 55 | 4 | 49 | 298.0034 | 1130.6169 | 68.0334 | 3.794 | 0.91287 | 110 | 149.5988 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.4435 | 90.1325
CID=826803805 | 9 | 57.5 | 89.9077 | 4 | 51.5 | 10.3 | 0.77937 | 140.4677 | 15.6257 | 96.1049 | 244.804 | 218.1794 | 33217.224 | 2.0978 | 0.047785 | 2.8484 | 89.9078 | 256.093 | 9 | 57.5 | 4 | 51.5 | 298.0034 | 1202.031 | 69.5354 | 4.0336 | 0.91288 | 110 | 149.6371 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.1717 | 90.1326
CID=-678671208 | 9 | 60 | 89.9283 | 4 | 54 | 10.8 | 0.77937 | 140.4677 | 15.6257 | 99.8699 | 245.917 | 218.1794 | 33269.2925 | 2.0785 | 0.049316 | 2.7344 | 89.9283 | 245.9013 | 9 | 60 | 4 | 54 | 298.0034 | 1276.7811 | 71.0906 | 4.2845 | 0.91289 | 110 | 149.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2777 | 90.1326
CID=625290707 | 9 | 62.5 | 89.9574 | 4 | 56.5 | 11.3 | 0.77937 | 140.4677 | 15.6257 | 103.6713 | 247.0056 | 218.1794 | 33334.0513 | 2.0574 | 0.050967 | 2.619 | 89.9574 | 235.5939 | 9 | 62.5 | 4 | 56.5 | 298.0034 | 1354.9726 | 72.7357 | 4.5468 | 0.9129 | 110 | 149.7172 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.0994 | 90.1325
CID=443722254 | 9 | 65 | 89.9896 | 4 | 59 | 11.8 | 0.77937 | 140.4677 | 15.6257 | 107.511 | 248.0701 | 218.1794 | 33453.4458 | 2.0195 | 0.052752 | 2.4836 | 89.9896 | 223.496 | 9 | 65 | 4 | 59 | 298.0034 | 1436.7133 | 74.7176 | 4.8211 | 0.9129 | 110 | 149.7693 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5516 | 90.1325
CID=1747684169 | 9 | 67.5 | 90.0209 | 4 | 61.5 | 12.3 | 0.77937 | 140.4677 | 15.6257 | 111.3912 | 249.1105 | 218.1794 | 33576.356 | 1.9798 | 0.054685 | 2.3485 | 90.0209 | 211.4164 | 9 | 67.5 | 4 | 61.5 | 298.0034 | 1522.1141 | 76.7962 | 5.1077 | 0.91291 | 110 | 149.8197 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.8089 | 90.1325
CID=853654996 | 9 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137350385 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599548373 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295586458 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477154911 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826807004 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678668009 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625293906 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443725453 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747687368 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853658195 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137347186 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599541070 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295579155 | 12 | 25 | 14.4122 | 4 | 19 | 3.8 | 0.77968 | 140.3492 | 17.2319 | 49.7865 | 228.1473 | 220.205 | 19873.1581 | 0.88893 | 0.0095581 | 10.5112 | 14.4122 | 151.4905 | 12 | 25 | 4 | 19 | 329.817 | 498.5781 | 34.7527 | 1.5117 | 0.73705 | 110 | 29.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.9035 | 14.4449
CID=-477147608 | 12 | 27.5 | 21.7892 | 4 | 21.5 | 4.3 | 0.77968 | 140.3492 | 17.2319 | 53.2055 | 229.5911 | 220.205 | 22277.628 | 1.104 | 0.01213 | 8.4615 | 21.7892 | 184.3695 | 12 | 27.5 | 4 | 21.5 | 329.817 | 537.3762 | 39.0782 | 1.6293 | 0.78678 | 110 | 42.0769 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.806 | 21.8594
CID=826814307 | 12 | 30 | 26.7543 | 4 | 24 | 4.8 | 0.77968 | 140.3492 | 17.2319 | 56.6452 | 231.0084 | 220.205 | 23594.1421 | 1.2323 | 0.014055 | 7.5336 | 26.7542 | 201.5558 | 12 | 30 | 4 | 24 | 329.817 | 578.4112 | 41.8155 | 1.7537 | 0.81239 | 110 | 50.0361 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6007 | 26.8405
CID=-678660706 | 12 | 32.5 | 32.2429 | 4 | 26.5 | 5.3 | 0.77968 | 140.3492 | 17.2319 | 60.1065 | 232.3994 | 220.205 | 24821.9294 | 1.3581 | 0.016259 | 6.7433 | 32.2429 | 217.4225 | 12 | 32.5 | 4 | 26.5 | 329.817 | 621.7653 | 44.5925 | 1.8852 | 0.83501 | 110 | 58.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4509 | 32.3474
CID=625301209 | 12 | 35 | 38.2603 | 4 | 29 | 5.8 | 0.77968 | 140.3492 | 17.2319 | 63.59 | 233.7644 | 220.205 | 25970.2745 | 1.481 | 0.018761 | 6.0622 | 38.2603 | 231.9428 | 12 | 35 | 4 | 29 | 329.817 | 667.522 | 47.4172 | 2.0239 | 0.85439 | 110 | 68.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.2216 | 38.3861
CID=443732756 | 12 | 37.5 | 43.0407 | 4 | 31.5 | 6.3 | 0.77968 | 140.3492 | 17.2319 | 67.0967 | 235.1035 | 220.205 | 26809.3434 | 1.5657 | 0.020934 | 5.5697 | 43.0407 | 239.7237 | 12 | 37.5 | 4 | 31.5 | 329.817 | 715.7661 | 49.8333 | 2.1702 | 0.86658 | 110 | 75.4618 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1077 | 43.1811
CID=1747694671 | 12 | 40 | 49.9962 | 4 | 34 | 6.8 | 0.77968 | 140.3492 | 17.2319 | 70.6273 | 236.4169 | 220.205 | 27870.4492 | 1.6836 | 0.024029 | 5.0371 | 49.9962 | 251.8338 | 12 | 40 | 4 | 34 | 329.817 | 766.5841 | 52.7577 | 2.3243 | 0.88039 | 110 | 86.2817 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.6528 | 50.1588
CID=853665498 | 12 | 42.5 | 57.64 | 4 | 36.5 | 7.3 | 0.77968 | 140.3492 | 17.2319 | 74.1828 | 237.7047 | 220.205 | 28915.597 | 1.7986 | 0.027547 | 4.5564 | 57.64 | 262.6337 | 12 | 42.5 | 4 | 36.5 | 329.817 | 820.0642 | 55.8064 | 2.4864 | 0.89149 | 110 | 98.2349 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.6832 | 57.8258
CID=-2137339883 | 12 | 45 | 65.4649 | 4 | 39 | 7.8 | 0.77968 | 140.3492 | 17.2319 | 77.7643 | 238.9672 | 220.205 | 29837.3456 | 1.9109 | 0.03132 | 4.1578 | 65.4649 | 272.1903 | 12 | 45 | 4 | 39 | 329.817 | 876.2965 | 58.7297 | 2.6569 | 0.89963 | 110 | 110.5603 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3728 | 65.6764
CID=-1599546319 | 12 | 47.5 | 73.703 | 4 | 41.5 | 8.3 | 0.77968 | 140.3492 | 17.2319 | 81.3729 | 240.2045 | 220.205 | 30684.1473 | 2.0201 | 0.035463 | 3.8053 | 73.703 | 280.4598 | 12 | 47.5 | 4 | 41.5 | 329.817 | 935.3729 | 61.6648 | 2.836 | 0.90571 | 110 | 123.6383 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.1625 | 73.9419
CID=-295584404 | 12 | 50 | 79.2901 | 4 | 44 | 8.8 | 0.77968 | 140.3492 | 17.2319 | 85.0099 | 241.4168 | 220.205 | 31205.9051 | 2.0923 | 0.038737 | 3.5675 | 79.2901 | 282.8711 | 12 | 50 | 4 | 44 | 329.817 | 997.3873 | 63.9125 | 3.0241 | 0.90876 | 110 | 132.564 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.7952 | 79.5389
CID=-477152857 | 12 | 52.5 | 87.6619 | 4 | 46.5 | 9.3 | 0.77968 | 140.3492 | 17.2319 | 88.6765 | 242.6043 | 220.205 | 32014.1409 | 2.197 | 0.043392 | 3.2963 | 87.6619 | 288.9633 | 12 | 52.5 | 4 | 46.5 | 329.817 | 1062.4359 | 66.6775 | 3.2213 | 0.91216 | 110 | 146.0147 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.0954 | 87.9361
CID=826809058 | 12 | 55 | 89.8685 | 4 | 49 | 9.8 | 0.77968 | 140.3492 | 17.2319 | 92.3743 | 243.7669 | 220.205 | 32269.4998 | 2.2186 | 0.045616 | 3.1557 | 89.8685 | 283.6001 | 12 | 55 | 4 | 49 | 329.817 | 1130.6169 | 68.2992 | 3.428 | 0.91287 | 110 | 149.5737 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.3247 | 90.1325
CID=-678665955 | 12 | 57.5 | 89.8873 | 4 | 51.5 | 10.3 | 0.77968 | 140.3492 | 17.2319 | 96.1049 | 244.9051 | 220.205 | 32348.2292 | 2.2078 | 0.046996 | 3.0481 | 89.8874 | 273.9891 | 12 | 57.5 | 4 | 51.5 | 329.817 | 1202.031 | 69.6407 | 3.6445 | 0.91287 | 110 | 149.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.1087 | 90.1325
CID=625295960 | 12 | 60 | 89.9115 | 4 | 54 | 10.8 | 0.77968 | 140.3492 | 17.2319 | 99.8699 | 246.0187 | 220.205 | 32422.385 | 2.193 | 0.048478 | 2.9351 | 89.9115 | 263.8981 | 12 | 60 | 4 | 54 | 329.817 | 1276.7811 | 71.1021 | 3.8712 | 0.91288 | 110 | 149.6432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.939 | 90.1325
CID=443727507 | 12 | 62.5 | 89.9361 | 4 | 56.5 | 11.3 | 0.77968 | 140.3492 | 17.2319 | 103.6713 | 247.1081 | 220.205 | 32505.6897 | 2.171 | 0.050071 | 2.8131 | 89.9361 | 252.9985 | 12 | 62.5 | 4 | 56.5 | 329.817 | 1354.9726 | 72.7291 | 4.1083 | 0.91289 | 110 | 149.6828 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8496 | 90.1325
CID=1747689422 | 12 | 65 | 89.9602 | 4 | 59 | 11.8 | 0.77968 | 140.3492 | 17.2319 | 107.511 | 248.1733 | 220.205 | 32617.6786 | 2.1398 | 0.051789 | 2.6805 | 89.9602 | 241.1417 | 12 | 65 | 4 | 59 | 329.817 | 1436.7133 | 74.553 | 4.3561 | 0.9129 | 110 | 149.7218 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.6734 | 90.1325
CID=853660249 | 12 | 67.5 | 89.9929 | 4 | 61.5 | 12.3 | 0.77968 | 140.3492 | 17.2319 | 111.3912 | 249.2145 | 220.205 | 32727.7811 | 2.0987 | 0.053653 | 2.5376 | 89.9929 | 228.3682 | 12 | 67.5 | 4 | 61.5 | 329.817 | 1522.1141 | 76.5899 | 4.615 | 0.91291 | 110 | 149.7745 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.1983 | 90.1326
CID=-2137345132 | 12 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599547472 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295585557 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477154010 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826807905 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678667108 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625294807 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443726354 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747688269 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853659096 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137346285 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1599544273 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295582358 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477150811 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826811104 | 15 | 27.5 | 10.5358 | 4 | 21.5 | 4.3 | 0.78006 | 140.1792 | 18.9668 | 53.2055 | 229.7083 | 222.216 | 18509.2949 | 0.7615 | 0.0084761 | 12.2156 | 10.5358 | 128.7013 | 15 | 27.5 | 4 | 21.5 | 364.1604 | 537.3762 | 35.1664 | 1.4757 | 0.70386 | 87.912 | 22.7424 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5925 | 10.5456
CID=-678663909 | 15 | 30 | 22.0969 | 4 | 24 | 4.8 | 0.78006 | 140.1792 | 18.9668 | 56.6452 | 231.1265 | 222.216 | 21791.3143 | 1.1691 | 0.012337 | 8.7602 | 22.0969 | 193.5726 | 15 | 30 | 4 | 24 | 364.1604 | 578.4112 | 41.1796 | 1.5883 | 0.78853 | 110 | 42.5763 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.6958 | 22.1642
CID=625298006 | 15 | 32.5 | 27.383 | 4 | 26.5 | 5.3 | 0.78006 | 140.1792 | 18.9668 | 60.1065 | 232.5184 | 222.216 | 23139.659 | 1.3077 | 0.014395 | 7.7415 | 27.383 | 211.9867 | 15 | 32.5 | 4 | 26.5 | 364.1604 | 621.7653 | 43.9902 | 1.7074 | 0.81526 | 110 | 51.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9438 | 27.4707
CID=443729553 | 15 | 35 | 33.0278 | 4 | 29 | 5.8 | 0.78006 | 140.1792 | 18.9668 | 63.59 | 233.8843 | 222.216 | 24354.4391 | 1.4438 | 0.016685 | 6.9343 | 33.0278 | 229.0261 | 15 | 35 | 4 | 29 | 364.1604 | 667.522 | 46.6935 | 1.833 | 0.83783 | 110 | 59.8933 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8586 | 33.1342
CID=1747691468 | 15 | 37.5 | 39.2526 | 4 | 31.5 | 6.3 | 0.78006 | 140.1792 | 18.9668 | 67.0967 | 235.2243 | 222.216 | 25501.403 | 1.577 | 0.019299 | 6.2318 | 39.2526 | 244.6163 | 15 | 37.5 | 4 | 31.5 | 364.1604 | 715.7661 | 49.4646 | 1.9655 | 0.85713 | 110 | 69.579 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.9017 | 39.38
CID=853662295 | 15 | 40 | 45.2487 | 4 | 34 | 6.8 | 0.78006 | 140.1792 | 18.9668 | 70.6273 | 236.5385 | 222.216 | 26478.8415 | 1.6898 | 0.021958 | 5.661 | 45.2487 | 256.1519 | 15 | 40 | 4 | 34 | 364.1604 | 766.5841 | 52.1137 | 2.1051 | 0.87142 | 110 | 78.8924 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8898 | 45.3962
CID=-2137343086 | 15 | 42.5 | 51.3765 | 4 | 36.5 | 7.3 | 0.78006 | 140.1792 | 18.9668 | 74.1828 | 237.8273 | 222.216 | 27388.3744 | 1.7954 | 0.024802 | 5.1733 | 51.3765 | 265.7856 | 15 | 42.5 | 4 | 36.5 | 364.1604 | 820.0642 | 54.7236 | 2.2519 | 0.88267 | 110 | 88.4344 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2373 | 51.5431
CID=-1599553370 | 15 | 45 | 59.2821 | 4 | 39 | 7.8 | 0.78006 | 140.1792 | 18.9668 | 77.7643 | 239.0907 | 222.216 | 28414.2318 | 1.92 | 0.028483 | 4.6785 | 59.2821 | 277.3491 | 15 | 45 | 4 | 39 | 364.1604 | 876.2965 | 57.712 | 2.4063 | 0.89343 | 110 | 100.8136 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.0094 | 59.4744
CID=-295591455 | 15 | 47.5 | 67.4661 | 4 | 41.5 | 8.3 | 0.78006 | 140.1792 | 18.9668 | 81.3729 | 240.3289 | 222.216 | 29353.5675 | 2.0414 | 0.032472 | 4.2617 | 67.4662 | 287.5239 | 15 | 47.5 | 4 | 41.5 | 364.1604 | 935.3729 | 60.6234 | 2.5686 | 0.90131 | 110 | 113.7278 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.7775 | 67.6857
CID=-477159908 | 15 | 50 | 76.2864 | 4 | 44 | 8.8 | 0.78006 | 140.1792 | 18.9668 | 85.0099 | 241.5421 | 222.216 | 30240.8117 | 2.1599 | 0.036941 | 3.8848 | 76.2864 | 296.358 | 15 | 50 | 4 | 44 | 364.1604 | 997.3873 | 63.6186 | 2.7389 | 0.90721 | 110 | 127.76 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.453 | 76.5318
CID=826802007 | 15 | 52.5 | 82.1529 | 4 | 46.5 | 9.3 | 0.78006 | 140.1792 | 18.9668 | 88.6765 | 242.7304 | 222.216 | 30776.9484 | 2.2368 | 0.040421 | 3.6359 | 82.1529 | 298.7017 | 15 | 52.5 | 4 | 46.5 | 364.1604 | 1062.4359 | 65.8952 | 2.9175 | 0.91006 | 110 | 137.1538 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.551 | 82.4122
CID=-678673006 | 15 | 55 | 89.8517 | 4 | 49 | 9.8 | 0.78006 | 140.1792 | 18.9668 | 92.3743 | 243.894 | 222.216 | 31417.8204 | 2.3369 | 0.044903 | 3.377 | 89.8517 | 303.4253 | 15 | 55 | 4 | 49 | 364.1604 | 1130.6169 | 68.4524 | 3.1047 | 0.91286 | 110 | 149.5466 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.9713 | 90.1325
CID=625288909 | 15 | 57.5 | 89.8735 | 4 | 51.5 | 10.3 | 0.78006 | 140.1792 | 18.9668 | 96.1049 | 245.0331 | 222.216 | 31469.2527 | 2.3284 | 0.046241 | 3.2672 | 89.8736 | 293.632 | 15 | 57.5 | 4 | 51.5 | 364.1604 | 1202.031 | 69.7504 | 3.3008 | 0.91287 | 110 | 149.5819 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.3346 | 90.1325
CID=443720456 | 15 | 60 | 89.8928 | 4 | 54 | 10.8 | 0.78006 | 140.1792 | 18.9668 | 99.8699 | 246.1477 | 222.216 | 31553.5632 | 2.3102 | 0.047672 | 3.1443 | 89.8928 | 282.6479 | 15 | 60 | 4 | 54 | 364.1604 | 1276.7811 | 71.2333 | 3.5061 | 0.91288 | 110 | 149.613 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.1963 | 90.1325
CID=1747682371 | 15 | 62.5 | 89.9153 | 4 | 56.5 | 11.3 | 0.78006 | 140.1792 | 18.9668 | 103.6713 | 247.238 | 222.216 | 31653.0379 | 2.2907 | 0.049212 | 3.0201 | 89.9153 | 271.552 | 15 | 62.5 | 4 | 56.5 | 364.1604 | 1354.9726 | 72.7969 | 3.7208 | 0.91288 | 110 | 149.6493 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.6943 | 90.1325
CID=853653198 | 15 | 65 | 89.9415 | 4 | 59 | 11.8 | 0.78006 | 140.1792 | 18.9668 | 107.511 | 248.3041 | 222.216 | 31763.3088 | 2.2659 | 0.050872 | 2.8897 | 89.9415 | 259.9071 | 15 | 65 | 4 | 59 | 364.1604 | 1436.7133 | 74.4945 | 3.9453 | 0.91289 | 110 | 149.6916 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.93 | 90.1325
CID=-2137352183 | 15 | 67.5 | 89.9644 | 4 | 61.5 | 12.3 | 0.78006 | 140.1792 | 18.9668 | 111.3912 | 249.3463 | 222.216 | 31880.2879 | 2.2301 | 0.052665 | 2.7472 | 89.9644 | 247.1531 | 15 | 67.5 | 4 | 61.5 | 364.1604 | 1522.1141 | 76.399 | 4.1798 | 0.9129 | 110 | 149.7286 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5173 | 90.1325
CID=-1599558619 | 15 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-295596704 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-477165157 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=826796758 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-678678255 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=625283660 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=443715207 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1747677122 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=853647949 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2137357432 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=371114953 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471871502 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493508415 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215171964 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291995317 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392751866 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880578517 | 18 | 32.5 | 22.9091 | 4 | 26.5 | 5.3 | 0.78052 | 139.9562 | 20.8387 | 60.1065 | 232.66 | 224.2112 | 21444.4314 | 1.2539 | 0.012718 | 8.9824 | 22.9091 | 205.779 | 18 | 32.5 | 4 | 26.5 | 401.1621 | 621.7653 | 43.4823 | 1.5499 | 0.79304 | 110 | 43.8902 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.4876 | 22.9766
CID=-294291600 | 18 | 35 | 27.9277 | 4 | 29 | 5.8 | 0.78052 | 139.9562 | 20.8387 | 63.59 | 234.0269 | 224.2112 | 22676.1114 | 1.385 | 0.014716 | 7.9654 | 27.9277 | 222.4545 | 18 | 35 | 4 | 29 | 401.1621 | 667.522 | 46.1624 | 1.664 | 0.81769 | 110 | 51.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6985 | 28.0193
CID=-1470645775 | 18 | 37.5 | 33.7827 | 4 | 31.5 | 6.3 | 0.78052 | 139.9562 | 20.8387 | 67.0967 | 235.3679 | 224.2112 | 23896.8113 | 1.532 | 0.017113 | 7.1249 | 33.7827 | 240.6995 | 18 | 37.5 | 4 | 31.5 | 401.1621 | 715.7661 | 48.8372 | 1.7842 | 0.84046 | 110 | 61.0709 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.8592 | 33.8929
CID=-1369889226 | 18 | 40 | 40.2635 | 4 | 34 | 6.8 | 0.78052 | 139.9562 | 20.8387 | 70.6273 | 236.6833 | 224.2112 | 25046.2816 | 1.6759 | 0.019859 | 6.3926 | 40.2635 | 257.3871 | 18 | 40 | 4 | 34 | 401.1621 | 766.5841 | 51.5875 | 1.9109 | 0.8598 | 110 | 71.1489 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.906 | 40.396
CID=371109704 | 18 | 42.5 | 47.3067 | 4 | 36.5 | 7.3 | 0.78052 | 139.9562 | 20.8387 | 74.1828 | 237.9731 | 224.2112 | 26133.6491 | 1.8166 | 0.022954 | 5.7613 | 47.3067 | 272.5474 | 18 | 42.5 | 4 | 36.5 | 401.1621 | 820.0642 | 54.374 | 2.0442 | 0.87553 | 110 | 82.093 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0656 | 47.4637
CID=471866253 | 18 | 45 | 52.7402 | 4 | 39 | 7.8 | 0.78052 | 139.9562 | 20.8387 | 77.7643 | 239.2376 | 224.2112 | 26909.9769 | 1.9114 | 0.025592 | 5.3075 | 52.7403 | 279.9169 | 18 | 45 | 4 | 39 | 401.1621 | 876.2965 | 56.752 | 2.1844 | 0.8848 | 110 | 90.5637 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.496 | 52.9123
CID=1493503166 | 18 | 47.5 | 60.7925 | 4 | 41.5 | 8.3 | 0.78052 | 139.9562 | 20.8387 | 81.3729 | 240.4768 | 224.2112 | 27911.6457 | 2.046 | 0.029398 | 4.8074 | 60.7925 | 292.2536 | 18 | 47.5 | 4 | 41.5 | 401.1621 | 935.3729 | 59.6394 | 2.3317 | 0.8951 | 110 | 103.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.5596 | 60.9897
CID=-1215177213 | 18 | 50 | 69.5234 | 4 | 44 | 8.8 | 0.78052 | 139.9562 | 20.8387 | 85.0099 | 241.6911 | 224.2112 | 28896.1945 | 2.1772 | 0.033684 | 4.3592 | 69.5234 | 303.0689 | 18 | 50 | 4 | 44 | 401.1621 | 997.3873 | 62.6138 | 2.4862 | 0.90289 | 110 | 116.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7665 | 69.7483
CID=1291990068 | 18 | 52.5 | 78.4346 | 4 | 46.5 | 9.3 | 0.78052 | 139.9562 | 20.8387 | 88.6765 | 242.8805 | 224.2112 | 29763.1467 | 2.3052 | 0.038286 | 3.9834 | 78.4346 | 312.4381 | 18 | 52.5 | 4 | 46.5 | 401.1621 | 1062.4359 | 65.4831 | 2.6484 | 0.90834 | 110 | 131.1944 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8781 | 78.6886
CID=1392746617 | 18 | 55 | 87.8192 | 4 | 49 | 9.8 | 0.78052 | 139.9562 | 20.8387 | 92.3743 | 244.0452 | 224.2112 | 30565.5116 | 2.4296 | 0.043357 | 3.6473 | 87.8193 | 320.3048 | 18 | 55 | 4 | 49 | 401.1621 | 1130.6169 | 68.3806 | 2.8184 | 0.91221 | 110 | 146.2683 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.0948 | 88.1043
CID=-1880583766 | 18 | 57.5 | 89.8569 | 4 | 51.5 | 10.3 | 0.78052 | 139.9562 | 20.8387 | 96.1049 | 245.1853 | 224.2112 | 30764.0517 | 2.4496 | 0.045513 | 3.4923 | 89.8569 | 313.8085 | 18 | 57.5 | 4 | 51.5 | 401.1621 | 1202.031 | 69.9961 | 2.9964 | 0.91286 | 110 | 149.555 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.0067 | 90.1325
CID=-294296849 | 18 | 60 | 89.8769 | 4 | 54 | 10.8 | 0.78052 | 139.9562 | 20.8387 | 99.8699 | 246.301 | 224.2112 | 30806.9932 | 2.4377 | 0.0469 | 3.3724 | 89.8769 | 303.1047 | 18 | 60 | 4 | 54 | 401.1621 | 1276.7811 | 71.3814 | 3.1827 | 0.91287 | 110 | 149.5873 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.0194 | 90.1325
CID=-1470651024 | 18 | 62.5 | 89.8982 | 4 | 56.5 | 11.3 | 0.78052 | 139.9562 | 20.8387 | 103.6713 | 247.3925 | 224.2112 | 30874.9362 | 2.4171 | 0.048389 | 3.2409 | 89.8983 | 291.3522 | 18 | 62.5 | 4 | 56.5 | 401.1621 | 1354.9726 | 72.9319 | 3.3776 | 0.91288 | 110 | 149.6218 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.2784 | 90.1325
CID=-1369894475 | 18 | 65 | 89.9222 | 4 | 59 | 11.8 | 0.78052 | 139.9562 | 20.8387 | 107.511 | 248.4598 | 224.2112 | 30963.39 | 2.3912 | 0.049993 | 3.1033 | 89.9222 | 279.0581 | 18 | 65 | 4 | 59 | 401.1621 | 1436.7133 | 74.608 | 3.5814 | 0.91288 | 110 | 149.6605 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0659 | 90.1326
CID=371108551 | 18 | 67.5 | 89.947 | 4 | 61.5 | 12.3 | 0.78052 | 139.9562 | 20.8387 | 111.3912 | 249.5031 | 224.2112 | 31069.4337 | 2.3605 | 0.051725 | 2.9607 | 89.947 | 266.3066 | 18 | 67.5 | 4 | 61.5 | 401.1621 | 1522.1141 | 76.4084 | 3.7943 | 0.91289 | 110 | 149.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.0188 | 90.1325
CID=471865100 | 18 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493502013 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215178366 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291988915 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392745464 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880584919 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294298002 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470652177 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1369895628 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=371111750 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471868299 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493505212 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215175167 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291992114 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392748663 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880581720 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294294803 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470648978 | 21 | 35 | 20.9187 | 4 | 29 | 5.8 | 0.78104 | 139.6784 | 22.8563 | 63.59 | 234.1897 | 226.1892 | 20425.1321 | 1.2558 | 0.012166 | 9.7616 | 20.9187 | 204.1992 | 21 | 35 | 4 | 29 | 440.9531 | 667.522 | 44.8423 | 1.5138 | 0.7817 | 110 | 40.6586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.9152 | 20.974
CID=-1369892429 | 21 | 37.5 | 28.431 | 4 | 31.5 | 6.3 | 0.78104 | 139.6784 | 22.8563 | 67.0967 | 235.532 | 226.1892 | 22217.3015 | 1.464 | 0.015033 | 8.192 | 28.431 | 232.9084 | 21 | 37.5 | 4 | 31.5 | 440.9531 | 715.7661 | 48.3645 | 1.6232 | 0.81988 | 110 | 52.6866 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.8342 | 28.5245
CID=371119053 | 21 | 40 | 34.5157 | 4 | 34 | 6.8 | 0.78104 | 139.6784 | 22.8563 | 70.6273 | 236.8485 | 226.1892 | 23444.5304 | 1.6227 | 0.017546 | 7.3135 | 34.5157 | 252.4299 | 21 | 40 | 4 | 34 | 440.9531 | 766.5841 | 51.0238 | 1.7385 | 0.84293 | 110 | 62.2132 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2151 | 34.6277
CID=471875602 | 21 | 42.5 | 41.1908 | 4 | 36.5 | 7.3 | 0.78104 | 139.6784 | 22.8563 | 74.1828 | 238.1396 | 226.1892 | 24590.3776 | 1.7781 | 0.020406 | 6.5618 | 41.1909 | 270.2851 | 21 | 42.5 | 4 | 36.5 | 440.9531 | 820.0642 | 53.7223 | 1.8598 | 0.86216 | 110 | 72.5889 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.5417 | 41.3248
CID=1493512515 | 21 | 45 | 48.4426 | 4 | 39 | 7.8 | 0.78104 | 139.6784 | 22.8563 | 77.7643 | 239.4053 | 226.1892 | 25663.7349 | 1.9299 | 0.02363 | 5.9131 | 48.4426 | 286.4476 | 21 | 45 | 4 | 39 | 440.9531 | 876.2965 | 56.4587 | 1.9873 | 0.87765 | 110 | 83.8612 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.752 | 48.6019
CID=-1215167864 | 21 | 47.5 | 54.055 | 4 | 41.5 | 8.3 | 0.78104 | 139.6784 | 22.8563 | 81.3729 | 240.6458 | 226.1892 | 26434.1966 | 2.0313 | 0.026389 | 5.4421 | 54.055 | 294.1708 | 21 | 47.5 | 4 | 41.5 | 440.9531 | 935.3729 | 58.8268 | 2.1213 | 0.88673 | 110 | 92.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0805 | 54.2307
CID=1291999417 | 21 | 50 | 62.3016 | 4 | 44 | 8.8 | 0.78104 | 139.6784 | 22.8563 | 85.0099 | 241.8613 | 226.1892 | 27427.0728 | 2.1765 | 0.030343 | 4.9322 | 62.3016 | 307.2837 | 21 | 50 | 4 | 44 | 440.9531 | 997.3873 | 61.6463 | 2.2619 | 0.89666 | 110 | 105.5662 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9077 | 62.5046
CID=1392755966 | 21 | 52.5 | 71.3696 | 4 | 46.5 | 9.3 | 0.78104 | 139.6784 | 22.8563 | 88.6765 | 243.0519 | 226.1892 | 28399.6075 | 2.3181 | 0.034851 | 4.4665 | 71.3696 | 318.7737 | 21 | 52.5 | 4 | 46.5 | 440.9531 | 1062.4359 | 64.5959 | 2.4094 | 0.9042 | 110 | 119.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.2501 | 71.6014
CID=-1880574417 | 21 | 55 | 80.64 | 4 | 49 | 9.8 | 0.78104 | 139.6784 | 22.8563 | 92.3743 | 244.2178 | 226.1892 | 29280.9137 | 2.4561 | 0.039703 | 4.0757 | 80.64 | 328.6629 | 21 | 55 | 4 | 49 | 440.9531 | 1130.6169 | 67.4514 | 2.564 | 0.90939 | 110 | 134.7269 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.3799 | 80.9026
CID=-294287500 | 21 | 57.5 | 89.8444 | 4 | 51.5 | 10.3 | 0.78104 | 139.6784 | 22.8563 | 96.1049 | 245.3592 | 226.1892 | 30063.7541 | 2.5796 | 0.044816 | 3.735 | 89.8445 | 335.5708 | 21 | 57.5 | 4 | 51.5 | 440.9531 | 1202.031 | 70.2719 | 2.726 | 0.91286 | 110 | 149.535 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.5224 | 90.1325
CID=-1470641675 | 21 | 60 | 89.8621 | 4 | 54 | 10.8 | 0.78104 | 139.6784 | 22.8563 | 99.8699 | 246.4762 | 226.1892 | 30120.2798 | 2.568 | 0.046159 | 3.6098 | 89.8622 | 324.3832 | 21 | 60 | 4 | 54 | 440.9531 | 1276.7811 | 71.6376 | 2.8955 | 0.91287 | 110 | 149.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.0509 | 90.1326
CID=-1369885126 | 21 | 62.5 | 89.8809 | 4 | 56.5 | 11.3 | 0.78104 | 139.6784 | 22.8563 | 103.6713 | 247.5689 | 226.1892 | 30178.0588 | 2.5519 | 0.0476 | 3.4786 | 89.8809 | 312.6576 | 21 | 62.5 | 4 | 56.5 | 440.9531 | 1354.9726 | 73.1124 | 3.0728 | 0.91287 | 110 | 149.5938 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.8051 | 90.1326
CID=371113804 | 21 | 65 | 89.9038 | 4 | 59 | 11.8 | 0.78104 | 139.6784 | 22.8563 | 107.511 | 248.6374 | 226.1892 | 30246.6733 | 2.5265 | 0.049151 | 3.3351 | 89.9039 | 299.8368 | 21 | 65 | 4 | 59 | 440.9531 | 1436.7133 | 74.7526 | 3.2582 | 0.91288 | 110 | 149.6308 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3855 | 90.1326
CID=471870353 | 21 | 67.5 | 89.9281 | 4 | 61.5 | 12.3 | 0.78104 | 139.6784 | 22.8563 | 111.3912 | 249.6821 | 226.1892 | 30336.2652 | 2.4961 | 0.050824 | 3.1865 | 89.9281 | 286.5527 | 21 | 67.5 | 4 | 61.5 | 440.9531 | 1522.1141 | 76.5105 | 3.4519 | 0.91289 | 110 | 149.67 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.2427 | 90.1326
CID=1493507266 | 21 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215173113 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291994168 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392750717 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880579666 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294292749 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470646924 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1369890375 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=371112651 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471869200 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493506113 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215174266 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291993015 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392749564 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880580819 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294293902 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470648077 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1369891528 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=371115850 | 24 | 37.5 | 15.6947 | 4 | 31.5 | 6.3 | 0.78162 | 139.3444 | 25.0288 | 67.0967 | 235.714 | 228.1484 | 18860.9628 | 1.1084 | 0.010534 | 11.3734 | 15.6947 | 178.5027 | 24 | 37.5 | 4 | 31.5 | 483.6671 | 715.7661 | 45.3311 | 1.4799 | 0.74686 | 87.9182 | 31.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7318 | 15.7197
CID=471872399 | 24 | 40 | 28.7793 | 4 | 34 | 6.8 | 0.78162 | 139.3444 | 25.0288 | 70.6273 | 237.0319 | 228.1484 | 21745.9112 | 1.5451 | 0.015305 | 8.4568 | 28.7793 | 243.3796 | 24 | 40 | 4 | 34 | 483.6671 | 766.5841 | 50.5251 | 1.5849 | 0.82136 | 110 | 53.2353 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.888 | 28.8692
CID=1493509312 | 24 | 42.5 | 35.2172 | 4 | 36.5 | 7.3 | 0.78162 | 139.3444 | 25.0288 | 74.1828 | 238.3243 | 228.1484 | 22998.1218 | 1.7157 | 0.017982 | 7.5008 | 35.2172 | 264.1573 | 24 | 42.5 | 4 | 36.5 | 483.6671 | 820.0642 | 53.2469 | 1.6955 | 0.84522 | 110 | 63.3058 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.5977 | 35.3309
CID=-1215171067 | 24 | 45 | 42.0534 | 4 | 39 | 7.8 | 0.78162 | 139.3444 | 25.0288 | 77.7643 | 239.5913 | 228.1484 | 24132.7398 | 1.8832 | 0.020946 | 6.7343 | 42.0534 | 283.201 | 24 | 45 | 4 | 39 | 483.6671 | 876.2965 | 55.8861 | 1.8118 | 0.86426 | 110 | 73.9284 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8492 | 42.1901
CID=1291996214 | 24 | 47.5 | 49.5616 | 4 | 41.5 | 8.3 | 0.78162 | 139.3444 | 25.0288 | 81.3729 | 240.8332 | 228.1484 | 25207.2129 | 2.0468 | 0.024322 | 6.0615 | 49.5615 | 300.4153 | 24 | 47.5 | 4 | 41.5 | 483.6671 | 935.3729 | 58.5988 | 1.9339 | 0.87964 | 110 | 85.6042 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2586 | 49.7239
CID=1392752763 | 24 | 50 | 57.7213 | 4 | 44 | 8.8 | 0.78162 | 139.3444 | 25.0288 | 85.0099 | 242.05 | 228.1484 | 26230.283 | 2.2067 | 0.028133 | 5.4722 | 57.7214 | 315.8627 | 24 | 50 | 4 | 44 | 483.6671 | 997.3873 | 61.3685 | 2.0621 | 0.89158 | 110 | 98.3625 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8019 | 57.9119
CID=-1880577620 | 24 | 52.5 | 63.8435 | 4 | 46.5 | 9.3 | 0.78162 | 139.3444 | 25.0288 | 88.6765 | 243.242 | 228.1484 | 26959.8214 | 2.3117 | 0.031334 | 5.0501 | 63.8435 | 322.4146 | 24 | 52.5 | 4 | 46.5 | 483.6671 | 1062.4359 | 63.7365 | 2.1966 | 0.89816 | 110 | 107.9986 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5727 | 64.0509
CID=-294290703 | 24 | 55 | 73.0603 | 4 | 49 | 9.8 | 0.78162 | 139.3444 | 25.0288 | 92.3743 | 244.4093 | 228.1484 | 27903.4778 | 2.4644 | 0.035996 | 4.5797 | 73.0603 | 334.5961 | 24 | 55 | 4 | 49 | 483.6671 | 1130.6169 | 66.5989 | 2.3376 | 0.90531 | 110 | 122.6143 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0461 | 73.2965
CID=-1470644878 | 24 | 57.5 | 82.9266 | 4 | 51.5 | 10.3 | 0.78162 | 139.3444 | 25.0288 | 96.1049 | 245.5521 | 228.1484 | 28830.3848 | 2.6129 | 0.041208 | 4.1605 | 82.9266 | 345.0137 | 24 | 57.5 | 4 | 51.5 | 483.6671 | 1202.031 | 69.5176 | 2.4852 | 0.91039 | 110 | 138.396 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.3599 | 83.1958
CID=-1369888329 | 24 | 60 | 89.8465 | 4 | 54 | 10.8 | 0.78162 | 139.3444 | 25.0288 | 99.8699 | 246.6704 | 228.1484 | 29418.462 | 2.7112 | 0.045448 | 3.871 | 89.8465 | 347.7929 | 24 | 60 | 4 | 54 | 483.6671 | 1276.7811 | 71.8896 | 2.6398 | 0.91286 | 110 | 149.5382 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.9235 | 90.1325
CID=371106753 | 24 | 62.5 | 89.8649 | 4 | 56.5 | 11.3 | 0.78162 | 139.3444 | 25.0288 | 103.6713 | 247.7645 | 228.1484 | 29481.3871 | 2.6965 | 0.046844 | 3.7351 | 89.8648 | 335.6565 | 24 | 62.5 | 4 | 56.5 | 483.6671 | 1354.9726 | 73.3318 | 2.8015 | 0.91287 | 110 | 149.5678 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5949 | 90.1326
CID=471863302 | 24 | 65 | 89.8857 | 4 | 59 | 11.8 | 0.78162 | 139.3444 | 25.0288 | 107.511 | 248.8345 | 228.1484 | 29537.4337 | 2.6766 | 0.048344 | 3.5924 | 89.8857 | 322.9018 | 24 | 65 | 4 | 59 | 483.6671 | 1436.7133 | 74.8889 | 2.9705 | 0.91287 | 110 | 149.6015 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7589 | 90.1326
CID=1493500215 | 24 | 67.5 | 89.9095 | 4 | 61.5 | 12.3 | 0.78162 | 139.3444 | 25.0288 | 111.3912 | 249.8806 | 228.1484 | 29604.6736 | 2.648 | 0.049962 | 3.4387 | 89.9095 | 309.1698 | 24 | 67.5 | 4 | 61.5 | 483.6671 | 1522.1141 | 76.5961 | 3.147 | 0.91288 | 110 | 149.64 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.532 | 90.1326
CID=-1215180164 | 24 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291987117 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392743666 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880586717 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294299800 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470653975 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1369897426 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=371101504 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=471858053 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1493494966 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1215185413 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1291981868 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1392738417 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1880591966 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-294305049 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1470659224 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1369902675 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968631652 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022373729 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639292178 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664669737 | 27 | 42.5 | 29.2594 | 4 | 36.5 | 7.3 | 0.78225 | 138.952 | 27.3663 | 74.1828 | 238.5246 | 230.0873 | 21311.0429 | 1.6359 | 0.015635 | 8.7166 | 29.2594 | 255.0422 | 27 | 42.5 | 4 | 36.5 | 529.4402 | 820.0642 | 52.7387 | 1.5489 | 0.82338 | 110 | 53.991 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.0582 | 29.3459
CID=-1405455280 | 27 | 45 | 35.8153 | 4 | 39 | 7.8 | 0.78225 | 138.952 | 27.3663 | 77.7643 | 239.7931 | 230.0873 | 22542.6696 | 1.8111 | 0.018395 | 7.7025 | 35.8153 | 275.8659 | 27 | 45 | 4 | 39 | 529.4402 | 876.2965 | 55.4682 | 1.6551 | 0.84711 | 110 | 64.2366 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2922 | 35.9335
CID=-101493365 | 27 | 47.5 | 42.8861 | 4 | 41.5 | 8.3 | 0.78225 | 138.952 | 27.3663 | 81.3729 | 241.0365 | 230.0873 | 23682.6089 | 1.9912 | 0.021494 | 6.9048 | 42.8861 | 296.119 | 27 | 47.5 | 4 | 41.5 | 529.4402 | 935.3729 | 58.0923 | 1.7667 | 0.86622 | 110 | 75.2216 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.8597 | 43.0269
CID=281588186 | 27 | 50 | 50.658 | 4 | 44 | 8.8 | 0.78225 | 138.952 | 27.3663 | 85.0099 | 242.2548 | 230.0873 | 24759.0161 | 2.1673 | 0.02503 | 6.2068 | 50.658 | 314.426 | 27 | 50 | 4 | 44 | 529.4402 | 997.3873 | 60.7869 | 1.8839 | 0.8815 | 110 | 87.3135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.4382 | 50.8249
CID=1585550101 | 27 | 52.5 | 59.0301 | 4 | 46.5 | 9.3 | 0.78225 | 138.952 | 27.3663 | 88.6765 | 243.4482 | 230.0873 | 25772.3415 | 2.3394 | 0.028996 | 5.6042 | 59.0301 | 330.8167 | 27 | 52.5 | 4 | 46.5 | 529.4402 | 1062.4359 | 63.5097 | 2.0067 | 0.89314 | 110 | 100.4176 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.9821 | 59.2263
CID=126870924 | 27 | 55 | 65.3011 | 4 | 49 | 9.8 | 0.78225 | 138.952 | 27.3663 | 92.3743 | 244.617 | 230.0873 | 26481.5266 | 2.4515 | 0.032328 | 5.17 | 65.3011 | 337.6072 | 27 | 55 | 4 | 49 | 529.4402 | 1130.6169 | 65.8618 | 2.1355 | 0.89949 | 110 | 110.3014 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.6823 | 65.5153
CID=1430832839 | 27 | 57.5 | 74.7007 | 4 | 51.5 | 10.3 | 0.78225 | 138.952 | 27.3663 | 96.1049 | 245.7613 | 230.0873 | 27416.9437 | 2.6157 | 0.037165 | 4.6915 | 74.7007 | 350.4604 | 27 | 57.5 | 4 | 51.5 | 529.4402 | 1202.031 | 68.6624 | 2.2704 | 0.90631 | 110 | 125.229 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.0535 | 74.9452
CID=1968626403 | 27 | 60 | 84.9767 | 4 | 54 | 10.8 | 0.78225 | 138.952 | 27.3663 | 99.8699 | 246.8812 | 230.0873 | 28338.1402 | 2.7756 | 0.04267 | 4.2534 | 84.9767 | 361.4362 | 27 | 60 | 4 | 54 | 529.4402 | 1276.7811 | 71.5797 | 2.4116 | 0.9112 | 110 | 141.6912 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.1043 | 85.2525
CID=-1022378978 | 27 | 62.5 | 89.8496 | 4 | 56.5 | 11.3 | 0.78225 | 138.952 | 27.3663 | 103.6713 | 247.9768 | 230.0873 | 28769.7854 | 2.8447 | 0.046118 | 4.0025 | 89.8496 | 359.6214 | 27 | 62.5 | 4 | 56.5 | 529.4402 | 1354.9726 | 73.647 | 2.5593 | 0.91286 | 110 | 149.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.5524 | 90.1325
CID=-639297427 | 27 | 65 | 89.8727 | 4 | 59 | 11.8 | 0.78225 | 138.952 | 27.3663 | 107.511 | 249.0483 | 230.0873 | 28854.4508 | 2.8243 | 0.047574 | 3.852 | 89.8727 | 346.1936 | 27 | 65 | 4 | 59 | 529.4402 | 1436.7133 | 75.1859 | 2.7136 | 0.91287 | 110 | 149.5805 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.1555 | 90.1326
CID=664664488 | 27 | 67.5 | 89.8916 | 4 | 61.5 | 12.3 | 0.78225 | 138.952 | 27.3663 | 111.3912 | 250.096 | 230.0873 | 28914.6411 | 2.8004 | 0.049138 | 3.6977 | 89.8916 | 332.3952 | 27 | 67.5 | 4 | 61.5 | 529.4402 | 1522.1141 | 76.8202 | 2.875 | 0.91288 | 110 | 149.611 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9411 | 90.1326
CID=-1405460529 | 27 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101498614 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281582937 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585544852 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126865675 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1430827590 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968625250 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022380131 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639298580 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664663335 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405461682 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101499767 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=281581784 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1585543699 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126864522 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1430826437 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1968628449 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1022376932 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-639295381 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=664666534 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1405458483 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-101496568 | 30 | 45 | 29.9145 | 4 | 39 | 7.8 | 0.78292 | 138.4994 | 29.8795 | 77.7643 | 240.0083 | 232.0042 | 20925.0054 | 1.7389 | 0.016039 | 8.966 | 29.9145 | 268.2143 | 30 | 45 | 4 | 39 | 578.4112 | 876.2965 | 55.0075 | 1.515 | 0.82606 | 110 | 55.0205 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.2153 | 30.0035
CID=281584983 | 30 | 47.5 | 36.3661 | 4 | 41.5 | 8.3 | 0.78292 | 138.4994 | 29.8795 | 81.3729 | 241.2532 | 232.0042 | 22091.6216 | 1.9085 | 0.018805 | 7.905 | 36.3661 | 287.4743 | 30 | 47.5 | 4 | 41.5 | 578.4112 | 935.3729 | 57.7196 | 1.6171 | 0.84882 | 110 | 65.0933 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.6305 | 36.4854
CID=1585546898 | 30 | 50 | 43.6834 | 4 | 44 | 8.8 | 0.78292 | 138.4994 | 29.8795 | 85.0099 | 242.4731 | 232.0042 | 23236.3372 | 2.1023 | 0.022049 | 7.0741 | 43.6834 | 309.0221 | 30 | 50 | 4 | 44 | 578.4112 | 997.3873 | 60.3343 | 1.7244 | 0.86804 | 110 | 76.46 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2979 | 43.826
CID=126867721 | 30 | 52.5 | 51.6561 | 4 | 46.5 | 9.3 | 0.78292 | 138.4994 | 29.8795 | 88.6765 | 243.6681 | 232.0042 | 24306.4647 | 2.2918 | 0.025725 | 6.3589 | 51.656 | 328.474 | 30 | 52.5 | 4 | 46.5 | 578.4112 | 1062.4359 | 62.9896 | 1.8368 | 0.88312 | 110 | 88.8707 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.16 | 51.8244
CID=1430829636 | 30 | 55 | 60.2574 | 4 | 49 | 9.8 | 0.78292 | 138.4994 | 29.8795 | 92.3743 | 244.8385 | 232.0042 | 25311.361 | 2.4766 | 0.029858 | 5.7389 | 60.2574 | 345.8114 | 30 | 55 | 4 | 49 | 578.4112 | 1130.6169 | 65.6808 | 1.9547 | 0.89452 | 110 | 102.3471 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8596 | 60.4554
CID=1968635752 | 30 | 57.5 | 68.3133 | 4 | 51.5 | 10.3 | 0.78292 | 138.4994 | 29.8795 | 96.1049 | 245.9843 | 232.0042 | 26161.3389 | 2.6303 | 0.034003 | 5.2326 | 68.3133 | 357.454 | 30 | 57.5 | 4 | 51.5 | 578.4112 | 1202.031 | 68.2606 | 2.0782 | 0.90198 | 110 | 115.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.677 | 68.5376
CID=-1022369629 | 30 | 60 | 76.3911 | 4 | 54 | 10.8 | 0.78292 | 138.4994 | 29.8795 | 99.8699 | 247.1058 | 232.0042 | 26950.6427 | 2.7725 | 0.038403 | 4.7956 | 76.3911 | 366.3447 | 30 | 60 | 4 | 54 | 578.4112 | 1276.7811 | 70.8094 | 2.2074 | 0.90727 | 110 | 127.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.9058 | 76.6398
CID=-639288078 | 30 | 62.5 | 86.8517 | 4 | 56.5 | 11.3 | 0.78292 | 138.4994 | 29.8795 | 103.6713 | 248.2031 | 232.0042 | 27846.4595 | 2.9444 | 0.044118 | 4.3507 | 86.8517 | 377.8688 | 30 | 62.5 | 4 | 56.5 | 578.4112 | 1354.9726 | 73.6641 | 2.3426 | 0.91188 | 110 | 144.7093 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.8512 | 87.1331
CID=664673837 | 30 | 65 | 89.8542 | 4 | 59 | 11.8 | 0.78292 | 138.4994 | 29.8795 | 107.511 | 249.2763 | 232.0042 | 28137.4529 | 2.981 | 0.046833 | 4.1302 | 89.8542 | 371.1123 | 30 | 65 | 4 | 59 | 578.4112 | 1436.7133 | 75.5227 | 2.4839 | 0.91286 | 110 | 149.5507 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4695 | 90.1325
CID=-1405451180 | 30 | 67.5 | 89.8744 | 4 | 61.5 | 12.3 | 0.78292 | 138.4994 | 29.8795 | 111.3912 | 250.3255 | 232.0042 | 28216.467 | 2.9608 | 0.048349 | 3.9734 | 89.8744 | 357.1113 | 30 | 67.5 | 4 | 61.5 | 578.4112 | 1522.1141 | 77.1029 | 2.6315 | 0.91287 | 110 | 149.5832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.5113 | 90.1325
CID=-101489265 | 30 | 70 | 0 | 4 | 64 | 12.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Calculation A2W35
PN | 2718315 | [5 empty] | 2718315 | TGH285-E-3-MT-SL | 150 | 165 | 380 | R1234ze | Standard Lift | Medium Temp
Calculation Type | FROM_POWER |  | CID=-1793661171 | Calculation Reference |  |  | 2718316 | TGH285-H-3-MT-SL | 150 | 165 | 400 | R1234ze | Standard Lift | Medium Temp
Units | SI |  | 28872.5794 | RPM Actual (Value) |  |  | 2718317 | TGH285-G-3-MT-SL | 131 | 145 | 460 | R1234ze | Standard Lift | Medium Temp
Value | 24.3 |  | 28872.5749 | RPM At Surge (Min) |  |  | 3141631 | TGH285-E-3-ST-SL | 150 | 165 | 380 | R1234ze | Standard Lift | Standard Temp
SSH | 5 | Superheat | 32914.3204 | RPM At Choke (Max) |  |  | 3141632 | TGH285-H-3-ST-SL | 150 | 165 | 400 | R1234ze | Standard Lift | Standard Temp
SDT | 35 | discharge T |  |  |  |  | 3141633 | TGH285-G-3-ST-SL | 131 | 145 | 460 | R1234ze | Standard Lift | Standard Temp
SST | -3 | evap T |  |  |  |  | 2718312 | TTH375-E-1-MT-SL | 210 | 231 | 380 | R134a | Standard Lift | Medium Temp
LLT | 30 | Liquid leaving |  |  |  |  | 2718313 | TTH375-H-1-MT-SL | 210 | 231 | 400 | R134a | Standard Lift | Medium Temp
Use Economizer? | TRUE | [5 empty] | 2718314 | TTH375-G-1-MT-SL | 180 | 198 | 460 | R134a | Standard Lift | Medium Temp
tapp | 5 | [5 empty] | 3141628 | TTH375-E-1-ST-SL | 210 | 231 | 380 | R134a | Standard Lift | Standard Temp
[7 empty] | 3141629 | TTH375-H-1-ST-SL | 210 | 231 | 400 | R134a | Standard Lift | Standard Temp
| Compressor | [5 empty] | 3141630 | TTH375-G-1-ST-SL | 180 | 198 | 460 | R134a | Standard Lift | Standard Temp
PN Type | 2718315 | 2718316 | 2718317 | 3141631 | 3141632 | 3141633 | 2718312 | 2718313 | 2718314 | 3141628 | 3141629 | 3141630
Compressor | TGH285-E-3-MT-SL | TGH285-H-3-MT-SL | TGH285-G-3-MT-SL | TGH285-E-3-ST-SL | TGH285-H-3-ST-SL | TGH285-G-3-ST-SL | TTH375-E-1-MT-SL | TTH375-H-1-MT-SL | TTH375-G-1-MT-SL | TTH375-E-1-ST-SL | TTH375-H-1-ST-SL | TTH375-G-1-ST-SL
CID | CID=-1499112739 | CID=2076851938 | CID=-1841644097 | CID=1734320580 | CID=-737113399 | CID=-1456116018 | CID=-1079644757 | CID=-1798647376 | CID=24885941 | CID=-694116678 | CID=-317645417 | CID=-1036648036
MASS_FLOW_RATE_EVAPORATOR | 0.55011 | 0.55011 | 0.55011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 28872.5794 | 28872.5794 | 28872.5794 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 3.6263 | 3.6263 | 3.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 24.3 | 24.3 | 24.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 88.1183 | 88.1183 | 88.1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_SUCT_SAT | -3 | -3 | -3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_DISCH_SAT | 35 | 35 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_SUCT_SUPER_HEAT | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 30 | 30 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_SUCT_ABSOLUTE | 193.5663 | 193.5663 | 193.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_DISCH_ABSOLUTE | 667.522 | 667.522 | 667.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_DISCH | 51.1744 | 51.1744 | 51.1744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_RATIO | 3.4485 | 3.4485 | 3.4485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOLERANCE | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 28872.5749 | 28872.5749 | 28872.5749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 32914.3204 | 32914.3204 | 32914.3204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 88.1154 | 88.1154 | 88.1154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 221.855 | 221.855 | 221.855 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 24.2996 | 24.2996 | 24.2996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 61.8194 | 61.8194 | 61.8194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10
Water Flow Suction | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14
DERIVED VALUES
Heating Capacity | 112.4183 | 112.4183 | 112.4183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP Heating | 4.6263 | 4.6263 | 4.6263 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
COP Heating | 4.6263 | 4.6263 | 4.6263 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Flow Evaporator | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14
delta T water Evaporator | 2.203 | 2.203 | 2.203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10
delta T water Condenser | 3.5131 | 3.5131 | 3.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Heating Capacity | 283.6744 | 283.6744 | 283.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ECON_SAT_TEMP | 14.6023
ECON_INTERSTAGE_P | 359.4576
ECON_CAPACITY | 20.2431
ECON_MASS_FLOW | 0.12081
TEMPERATURE_ECO_LIQUID_LEAVING | 19.6023
ENTHALPY_LIQUID_ECO_EXIT | 50.6492
ENTROPY_SUCTION | 0.78233
ENTROPY_SUCTION | 0.78233
SPEED_SOUND | 140.7959
DENSITY_SUCTION | 10.2954
ENTHALPY_LIQUID_CONDENSER_EXIT | 50.6492
ENTHALPY_DISCHARGE_ISENTROPIC | 234.5891
ENTHALPY_SUCTION | 210.8324
SPEED_COMPRESSOR | 32914.3204
MASS_FLOW_RATE_EVAPORATOR | 1.385
MASS_FLOW_RATE_MOTOR_COOLING | 0.026574
COEFFICIENT_OF_PERFORMANCE | 3.5888
POWER_INPUT_ELECTRICAL | 61.8194
CAPACITY_EVAPORATOR | 221.855
TEMPERATURE_SUCT_SAT | -3
TEMPERATURE_DISCH_SAT | 35
TEMPERATURE_SUCT_SUPER_HEAT | 5
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 30
PRESSURE_SUCT_ABSOLUTE | 193.5663
PRESSURE_DISCH_ABSOLUTE | 667.522
TEMPERATURE_DISCH | 52.531
PRESSURE_RATIO | 3.4485
POWER_FACTOR | 0.89618
IGV_ANGLE | 110
INPUT_CURRENT | 104.8064 | 99.5661
ECON_SAT_TEMP | 14.6023
ECON_INTERSTAGE_P | 359.4576
ECON_CAPACITY | 20.2431
ECON_MASS_FLOW | 0.12081
TEMPERATURE_ECO_LIQUID_LEAVING | 19.6023
ENTHALPY_LIQUID_ECO_EXIT | 50.6492
Note on D2: Edgar F. Hilton: A unique identifier. We'll be referencing this from other functions to extract specific values. See variables below.
Note on D3: Edgar F. Hilton: Obtain the unique value for the specified variable (in this case, the RPM of the compressor), and specified by the unique combination of inputs on the left. Notice how we reference the unique identifier for the calculation result, above.
Note on D4: Edgar F. Hilton: At the pressure ratio obtained by the inputs on the left, there is a maximum value and minimum value (choke and surge, respectively). This value here is the RPM at surge.
Note on D5: Edgar F. Hilton: The maximum value at the given pressure ratio obtained from the inputs on the left. In this case, this is the RPM of the compressor at Choke. Notice how we reference the calculation query above.

## Tabelle1
PN | 2718315 | 2718315 | TGH285-E-3-MT-SL | Evaporator |  | Condenser |  | Ausseneinheit |  | Gebäude |  | Fixed
Calculation Type | FROM_CAPACITY | 2718312 | TTH375-E-1-MT-SL | kA | 8000 | kA | 8000 | kA | 12000 | T | 22 | cp water | 4100
Units | SI |  |  | mdot in | 10 | mdot in | 8 | mdot air | 41 | d T | 5 | cp air | 1000
Value | 0 | AIR | 2
SSH | 5 | Water | 35
SDT | 35 |  |  | Calculated
SST | -5 | T evap | -5 | mc water | 41000 | mc water | 32800 | mc water | 41000 | T rück | 27
LLT | 30 |  |  | mc air |  |  |  | mc air | 41000
Use Economizer? | TRUE |  |  | mc coolant | 0 | mc coolant | 0 | mc coolant
tapp | 5 |  |  | NTU | 0.19512 | NTU | 0.2439 | NTU | 0.25374
|  |  |  | eps | 0.17727 | eps | 0.21644 | eps | 0.22411
| Compressor | Final |  | q max |  | q max |  | q max
PN Type | 2718315
Compressor | TGH285-E-3-MT-SL
CID | CID=-1957519307
MASS_FLOW_RATE_EVAPORATOR | 0.55011
SPEED_COMPRESSOR | 28872.5794
COEFFICIENT_OF_PERFORMANCE | 3.6263
POWER_INPUT_ELECTRICAL | 24.3
CAPACITY_EVAPORATOR | 88.1183
TEMPERATURE_SUCT_SAT | -3
TEMPERATURE_DISCH_SAT | 35
TEMPERATURE_SUCT_SUPER_HEAT | 5
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 30
PRESSURE_SUCT_ABSOLUTE | 193.5663
PRESSURE_DISCH_ABSOLUTE | 667.522
TEMPERATURE_DISCH | 51.1744
PRESSURE_RATIO | 3.4485
TOLERANCE | 10
SPEED_COMPRESSOR | 28872.5749
SPEED_COMPRESSOR | 32914.3204
CAPACITY_EVAPORATOR | 88.1154
CAPACITY_EVAPORATOR | 221.855
POWER_INPUT_ELECTRICAL | 24.2996
POWER_INPUT_ELECTRICAL | 61.8194
Water Flow Condenser | 8
Water Flow Suction | 10
DERIVED VALUES
Heating Capacity | 112.4183
COP Heating | 4.6263
COP Heating | 4.6263
Water Flow Evaporator | 10
delta T water Evaporator | 2.203
Water Flow Condenser | 8
delta T water Condenser | 3.5131
Maximum Heating Capacity | 283.6744
ECON_SAT_TEMP | 14.6023
ECON_INTERSTAGE_P | 359.4576
ECON_CAPACITY | 20.2431
ECON_MASS_FLOW | 0.12081
TEMPERATURE_ECO_LIQUID_LEAVING | 19.6023
ENTHALPY_LIQUID_ECO_EXIT | 50.6492
ENTROPY_SUCTION | 0.78233
ENTROPY_SUCTION | 0.78233
SPEED_SOUND | 140.7959
DENSITY_SUCTION | 10.2954
ENTHALPY_LIQUID_CONDENSER_EXIT | 50.6492
ENTHALPY_DISCHARGE_ISENTROPIC | 234.5891
ENTHALPY_SUCTION | 210.8324
SPEED_COMPRESSOR | 32914.3204
MASS_FLOW_RATE_EVAPORATOR | 1.385
MASS_FLOW_RATE_MOTOR_COOLING | 0.026574
COEFFICIENT_OF_PERFORMANCE | 3.5888
POWER_INPUT_ELECTRICAL | 61.8194
CAPACITY_EVAPORATOR | 221.855
TEMPERATURE_SUCT_SAT | -3
TEMPERATURE_DISCH_SAT | 35
TEMPERATURE_SUCT_SUPER_HEAT | 5
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 30
PRESSURE_SUCT_ABSOLUTE | 193.5663
PRESSURE_DISCH_ABSOLUTE | 667.522
TEMPERATURE_DISCH | 52.531
PRESSURE_RATIO | 3.4485
POWER_FACTOR | 0.89618
IGV_ANGLE | 110
INPUT_CURRENT | 104.8064
ECON_SAT_TEMP | 14.6023
ECON_INTERSTAGE_P | 359.4576
ECON_CAPACITY | 20.2431
ECON_MASS_FLOW | 0.12081
TEMPERATURE_ECO_LIQUID_LEAVING | 19.6023
ENTHALPY_LIQUID_ECO_EXIT | 50.6492

## Calculation A2W55
PN | 2718315 | [5 empty] | 2718315 | TGH285-E-3-MT-SL | 150 | 165 | 380 | R1234ze | Standard Lift | Medium Temp
Calculation Type | FROM_CAPACITY |  | CID=166781200 | Calculation Reference |  |  | 2718316 | TGH285-H-3-MT-SL | 150 | 165 | 400 | R1234ze | Standard Lift | Medium Temp
Units | SI |  | 34155.8453 | RPM Actual (Value) |  |  | 2718317 | TGH285-G-3-MT-SL | 131 | 145 | 460 | R1234ze | Standard Lift | Medium Temp
Value | 0 |  | 33793.0662 | RPM At Surge (Min) |  |  | 3141631 | TGH285-E-3-ST-SL | 150 | 165 | 380 | R1234ze | Standard Lift | Standard Temp
SSH | 4 | Superheat | 34155.8451 | RPM At Choke (Max) |  |  | 3141632 | TGH285-H-3-ST-SL | 150 | 165 | 400 | R1234ze | Standard Lift | Standard Temp
SDT | 55 | discharge T |  |  |  |  | 3141633 | TGH285-G-3-ST-SL | 131 | 145 | 460 | R1234ze | Standard Lift | Standard Temp
SST | -2 | evap T |  |  |  |  | 2718312 | TTH375-E-1-MT-SL | 210 | 231 | 380 | R134a | Standard Lift | Medium Temp
LLT | 47 | Liquid leaving |  |  |  |  | 2718313 | TTH375-H-1-MT-SL | 210 | 231 | 400 | R134a | Standard Lift | Medium Temp
Use Economizer? | TRUE | [5 empty] | 2718314 | TTH375-G-1-MT-SL | 180 | 198 | 460 | R134a | Standard Lift | Medium Temp
tapp | 5 | [5 empty] | 3141628 | TTH375-E-1-ST-SL | 210 | 231 | 380 | R134a | Standard Lift | Standard Temp
[7 empty] | 3141629 | TTH375-H-1-ST-SL | 210 | 231 | 400 | R134a | Standard Lift | Standard Temp
| Compressor | [5 empty] | 3141630 | TTH375-G-1-ST-SL | 180 | 198 | 460 | R134a | Standard Lift | Standard Temp
PN Type | 2718315 | 2718316 | 2718317 | 3141631 | 3141632 | 3141633 | 2718312 | 2718313 | 2718314 | 3141628 | 3141629 | 3141630
Compressor | TGH285-E-3-MT-SL | TGH285-H-3-MT-SL | TGH285-G-3-MT-SL | TGH285-E-3-ST-SL | TGH285-H-3-ST-SL | TGH285-G-3-ST-SL | TTH375-E-1-MT-SL | TTH375-H-1-MT-SL | TTH375-G-1-MT-SL | TTH375-E-1-ST-SL | TTH375-H-1-ST-SL | TTH375-G-1-ST-SL
CID | CID=-1186015312 | CID=-467012693 | CID=1242421946 | CID=1961424565 | CID=-1948014652 | CID=-1229012033 | CID=-766547330 | CID=-47544711 | CID=337983368 | CID=1056985987 | CID=-1528546670 | CID=-809544051
MASS_FLOW_RATE_EVAPORATOR | 1.3905 | 1.3905 | 1.3905 | 1.3905 | 1.3905 | 1.3905 | 1.8384 | 1.8384 | 1.8384 | 0 | 0 | 0
SPEED_COMPRESSOR | 34155.8453 | 34155.8453 | 34155.8453 | 34155.8453 | 34155.8453 | 34155.8453 | 36057.0547 | 36057.0547 | 36057.0547 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 2.862 | 2.862 | 2.862 | 2.862 | 2.862 | 2.862 | 2.8491 | 2.8491 | 2.8491 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 71.7439 | 71.7439 | 71.7439 | 71.7439 | 71.7439 | 71.7439 | 104.109 | 104.109 | 104.109 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 205.3328 | 205.3328 | 205.3328 | 205.3328 | 205.3328 | 205.3328 | 296.6139 | 296.6139 | 296.6139 | 0 | 0 | 0
TEMPERATURE_SUCT_SAT | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | -2 | 0 | 0 | 0
TEMPERATURE_DISCH_SAT | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 0 | 0
TEMPERATURE_SUCT_SUPER_HEAT | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 0 | 0 | 0
PRESSURE_SUCT_ABSOLUTE | 200.9893 | 200.9893 | 200.9893 | 200.9893 | 200.9893 | 200.9893 | 272.1698 | 272.1698 | 272.1698 | 0 | 0 | 0
PRESSURE_DISCH_ABSOLUTE | 1130.6169 | 1130.6169 | 1130.6169 | 1130.6169 | 1130.6169 | 1130.6169 | 1491.5141 | 1491.5141 | 1491.5141 | 0 | 0 | 0
TEMPERATURE_DISCH | 64.3844 | 64.3844 | 64.3844 | 64.3844 | 64.3844 | 64.3844 | 73.1334 | 73.1334 | 73.1334 | 0 | 0 | 0
PRESSURE_RATIO | 5.6253 | 5.6253 | 5.6253 | 5.6253 | 5.6253 | 5.6253 | 5.4801 | 5.4801 | 5.4801 | 0 | 0 | 0
TOLERANCE | 4.7157 | 4.7157 | 4.7157 | 4.7157 | 4.7157 | 4.7157 | 4.7494 | 4.7494 | 4.7494 | 0 | 0 | 0
SPEED_COMPRESSOR | 33793.0662 | 33793.0662 | 33793.0662 | 33793.0662 | 33793.0662 | 33793.0662 | 35419.7768 | 35419.7768 | 35419.7768 | 0 | 0 | 0
SPEED_COMPRESSOR | 34155.8451 | 34155.8451 | 34155.8451 | 34155.8451 | 34155.8451 | 34155.8451 | 36057.055 | 36057.055 | 36057.055 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 143.7127 | 143.7127 | 143.7127 | 143.7127 | 143.7127 | 143.7127 | 198.2622 | 198.2622 | 198.2622 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 205.3328 | 205.3328 | 205.3328 | 205.3328 | 205.3328 | 205.3328 | 296.614 | 296.614 | 296.614 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 65.1607 | 65.1607 | 65.1607 | 65.1607 | 65.1607 | 65.1607 | 87.9354 | 87.9354 | 87.9354 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 71.7439 | 71.7439 | 71.7439 | 71.7439 | 71.7439 | 71.7439 | 104.109 | 104.109 | 104.109 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10
Water Flow Suction | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14
DERIVED VALUES
Heating Capacity | 277.0767 | 277.0767 | 277.0767 | 277.0767 | 277.0767 | 277.0767 | 400.7229 | 400.7229 | 400.7229 | 0 | 0 | 0
COP Heating | 3.862 | 3.862 | 3.862 | 3.862 | 3.862 | 3.862 | 3.8491 | 3.8491 | 3.8491 | #DIV/0! | #DIV/0! | #DIV/0!
COP Heating | 3.862 | 3.862 | 3.862 | 3.862 | 3.862 | 3.862 | 3.8491 | 3.8491 | 3.8491 | 1 | 1 | 1
Water Flow Evaporator | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14
delta T water Evaporator | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.1333 | 5.2967 | 5.2967 | 5.2967 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10
delta T water Condenser | 8.6586 | 8.6586 | 8.6586 | 8.6586 | 8.6586 | 8.6586 | 10.0181 | 10.0181 | 10.0181 | 0 | 0 | 0
Maximum Heating Capacity | 277.0767 | 277.0767 | 277.0767 | 277.0767 | 277.0767 | 277.0767 | 400.723 | 400.723 | 400.723 | 0 | 0 | 0
Note on D2: Edgar F. Hilton: A unique identifier. We'll be referencing this from other functions to extract specific values. See variables below.
Note on D3: Edgar F. Hilton: Obtain the unique value for the specified variable (in this case, the RPM of the compressor), and specified by the unique combination of inputs on the left. Notice how we reference the unique identifier for the calculation result, above.
Note on D4: Edgar F. Hilton: At the pressure ratio obtained by the inputs on the left, there is a maximum value and minimum value (choke and surge, respectively). This value here is the RPM at surge.
Note on D5: Edgar F. Hilton: The maximum value at the given pressure ratio obtained from the inputs on the left. In this case, this is the RPM of the compressor at Choke. Notice how we reference the calculation query above.

## Calculation A2W55 (2)
PN | 2718315
Calculation Type | FROM_POWER
Units | SI
Value | 0
SSH | 4
SDT | 2.5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 30 | 32.5 | 35 | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55
SST | -16
LLT | 47 | -3 | -0.5 | 2 | 4.5 | 7 | 9.5 | 12 | 14.5 | 17 | 19.5 | 22 | 24.5 | 27 | 29.5 | 32 | 34.5 | 37 | 39.5 | 42 | 44.5 | 47
Use Economizer? | TRUE
tapp | 2
Compressor
PN Type | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315
Compressor | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL
CID | CID=1610616501 | CID=-1965348176 | CID=1953147859 | CID=-1622816818 | CID=848617161 | CID=1567619780 | CID=-55821417 | CID=663181202 | CID=-1160352115 | CID=-441349496 | CID=-817820757 | CID=-98818138 | CID=-1922351455 | CID=-1203348836 | CID=-77254801 | CID=641747818 | CID=-1181785499 | CID=-462782880 | CID=-839254141 | CID=-120251522 | CID=-1943784839 | CID=-1224782220
Error | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Success | Success | Success | Success | Success | Success | Success | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor
MASS_FLOW_RATE_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57089 | 0.60957 | 0.63512 | 0.67363 | 0.72508 | 0.81556 | 0.78919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29432.6668 | 30319.414 | 31032.4814 | 31899.421 | 32787.2532 | 33851.7419 | 33967.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5282 | 4.2181 | 3.9547 | 3.7048 | 3.4797 | 3.299 | 3.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.804 | 24.789 | 27.3235 | 30.6827 | 34.8748 | 41.0365 | 40.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7336 | 104.5621 | 108.0567 | 113.6724 | 121.3543 | 135.3815 | 129.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_SUCT_SAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16 | -16 | -16 | -16 | -16 | -16 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_DISCH_SAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22.5 | 25 | 27.5 | 30 | 32.5 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_SUCT_SUPER_HEAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14.5 | 17 | 19.5 | 22 | 24.5 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_SUCT_ABSOLUTE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.0483 | 115.0483 | 115.0483 | 115.0483 | 115.0483 | 115.0483 | 115.0483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_DISCH_ABSOLUTE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 427.3713 | 461.9363 | 498.5781 | 537.3762 | 578.4112 | 621.7653 | 667.522 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_DISCH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.9693 | 34.7558 | 37.3674 | 40.1212 | 42.8771 | 45.382 | 46.5021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_RATIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7147 | 4.0152 | 4.3336 | 4.6709 | 5.0276 | 5.4044 | 5.8021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOLERANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 5 | 5 | 7.0351 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29432.6668 | 30319.414 | 31032.4814 | 31899.421 | 32787.2532 | 33851.7419 | 33967.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29432.6668 | 30319.414 | 31032.4814 | 31899.421 | 32787.2532 | 33851.7419 | 33967.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7336 | 104.5621 | 108.0567 | 113.6724 | 121.3543 | 135.3815 | 129.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.7336 | 104.5621 | 108.0567 | 113.6724 | 121.3543 | 135.3815 | 129.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.804 | 24.789 | 27.3235 | 30.6827 | 34.8748 | 41.0365 | 40.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.804 | 24.789 | 27.3235 | 30.6827 | 34.8748 | 41.0365 | 40.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.5903 | 19.3823 | 21.9993 | 25.7978 | 29.6237 | 34.7581 | 40.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3783 | 40.7485 | 40.7946 | 40.5157 | 41.0643 | 41.6996 | 40.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.0546 | 66.8629 | 72.3051 | 77.6638 | 84.8738 | 91.7347 | 100.4912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152.6637 | 151.3732 | 147.8576 | 144.4063 | 140.9543 | 137.5423 | 129.9314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29309.0841 | 30208.2997 | 31027.7849 | 31543.7551 | 32470.2729 | 33274.1634 | 33992.4263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33380.6953 | 33494.7464 | 33520.3779 | 33532.1346 | 33728.5429 | 33949.8974 | 33967.7614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6801 | 3.4497 | 3.2867 | 3.0105 | 2.8651 | 2.6392 | 2.5034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7808 | 3.7148 | 3.6244 | 3.5642 | 3.4325 | 3.2984 | 3.2284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Water Flow Suction | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
DERIVED VALUES
Heating Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5376 | 129.351 | 135.3802 | 144.3551 | 156.2291 | 176.418 | 170.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP Heating | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 5.5282 | 5.2181 | 4.9547 | 4.7048 | 4.4797 | 4.299 | 4.2284 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
COP Heating | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5.5282 | 5.2181 | 4.9547 | 4.7048 | 4.4797 | 4.299 | 4.2284 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Flow Evaporator | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
delta T water Evaporator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7631 | 1.8672 | 1.9296 | 2.0299 | 2.167 | 2.4175 | 2.3202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
delta T water Condenser | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0134 | 3.2338 | 3.3845 | 3.6089 | 3.9057 | 4.4105 | 4.2544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Heating Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5376 | 129.351 | 135.3802 | 144.3551 | 156.2291 | 176.418 | 170.1772 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Calculation A2W55 (3)
PN | 2718315
Calculation Type | FROM_POWER
Units | SI
Value | 0
SSH | 4
SDT | 2.5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 30 | 32.5 | 35 | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55 | 57.5 | 60 | 62.5 | 65 | 67.5 | 70
SST | 12
LLT | 33 | -3 | -0.5 | 2 | 4.5 | 7 | 9.5 | 12 | 14.5 | 17 | 19.5 | 22 | 24.5 | 27 | 29.5 | 32 | 34.5 | 37 | 39.5 | 42 | 44.5 | 47 | 49.5 | 52 | 54.5 | 57 | 59.5 | 62
Use Economizer? | TRUE
tapp | 2
Compressor
PN Type | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315 | 2718315
Compressor | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL | TGH285-E-3-MT-SL
CID | CID=1789269680 | CID=1070267061 | CID=2131801038 | CID=1412798419 | CID=1027270340 | CID=308267721 | CID=122831762 | CID=-596170857 | CID=-981698936 | CID=-1700701555 | CID=-639167578 | CID=-1358170197 | CID=-1743698276 | CID=1832266401 | CID=101398378 | CID=-617604241 | CID=-1003132320 | CID=-1722134939 | CID=-660600962 | CID=-1379603581 | CID=-1765131660 | CID=1810833017 | CID=1625397058 | CID=906394439 | CID=520866360 | CID=-1150418878 | CID=-1150315355 | CID=-1150346876
Error | com.turbocor.cpr.engine.exception.CPREngineException: Input parameters produce negative head factor. | com.turbocor.cpr.engine.exception.CPREngineException: Input parameters produce negative head factor. | com.turbocor.cpr.engine.exception.CPREngineException: Input parameters produce negative head factor. | com.turbocor.cpr.engine.exception.CPREngineException: Input parameters produce negative head factor. | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Success | Success | Success | Success | Success | Success | Success | Success | Success | Success | Success | Success | Success | Success | Success | PRESSURE_DISCH_ABSOLUTE value exceeds critical value of 1611.0 kPa, actual value is 1611.2888917536097
MASS_FLOW_RATE_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82385 | 0.85928 | 0.93064 | 1.0019 | 1.073 | 1.1798 | 1.2865 | 1.3572 | 1.3919 | 1.4622 | 1.5682 | 1.6024 | 1.6366 | 1.742 | 1.7402 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21033.023 | 21930.7867 | 22943.9067 | 23873.7258 | 24798.6168 | 25803.0365 | 26705.3483 | 27447.439 | 28015.2937 | 28720.5615 | 29467.5136 | 30018.0853 | 30548.9353 | 31182.3592 | 31630.6936 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.328 | 7.5531 | 6.9079 | 6.3593 | 5.8544 | 5.4177 | 5.0416 | 4.7058 | 4.4133 | 4.1267 | 3.8795 | 3.638 | 3.431 | 3.2451 | 3.0691 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.198 | 18.4466 | 21.6312 | 25.0485 | 28.8527 | 33.945 | 39.3818 | 44.0656 | 47.7059 | 53.0588 | 59.9199 | 64.6276 | 69.2767 | 77.1649 | 80.6695 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.8969 | 139.3293 | 149.4273 | 159.2912 | 168.9144 | 183.9034 | 198.5458 | 207.3631 | 210.5407 | 218.9562 | 232.4568 | 235.1173 | 237.6853 | 250.406 | 247.5805 | 0
TEMPERATURE_SUCT_SAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 0
TEMPERATURE_DISCH_SAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.5 | 35 | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55 | 57.5 | 60 | 62.5 | 65 | 67.5 | 0
TEMPERATURE_SUCT_SUPER_HEAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24.5 | 27 | 29.5 | 32 | 34.5 | 37 | 39.5 | 42 | 44.5 | 47 | 49.5 | 52 | 54.5 | 57 | 59.5 | 0
PRESSURE_SUCT_ABSOLUTE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 329.817 | 0
PRESSURE_DISCH_ABSOLUTE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 621.7653 | 667.522 | 715.7661 | 766.5841 | 820.0642 | 876.2965 | 935.3729 | 997.3873 | 1062.4359 | 1130.6169 | 1202.031 | 1276.7811 | 1354.9726 | 1436.7133 | 1522.1141 | 0
TEMPERATURE_DISCH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.3448 | 42.7816 | 45.2188 | 47.6235 | 50.1252 | 52.6284 | 55.0834 | 57.5279 | 59.9178 | 62.4752 | 64.9767 | 67.5936 | 70.1253 | 72.6566 | 75.2239 | 0
PRESSURE_RATIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8852 | 2.0239 | 2.1702 | 2.3243 | 2.4864 | 2.6569 | 2.836 | 3.0241 | 3.2213 | 3.428 | 3.6445 | 3.8712 | 4.1083 | 4.3561 | 4.615 | 0
TOLERANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.092 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6.4464 | 5 | 10 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21033.023 | 21930.7867 | 22943.9067 | 23873.7258 | 24798.6168 | 25803.0365 | 26705.3483 | 27447.439 | 28015.2937 | 28720.5615 | 29467.5136 | 30018.0853 | 30548.9353 | 31182.3592 | 31630.6936 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21033.023 | 21930.7867 | 22943.9067 | 23873.7258 | 24798.6168 | 25803.0365 | 26705.3483 | 27447.439 | 28015.2937 | 28720.5615 | 29467.5136 | 30018.0853 | 30548.9353 | 31182.3592 | 31630.6936 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.8969 | 139.3293 | 149.4273 | 159.2912 | 168.9144 | 183.9034 | 198.5458 | 207.3631 | 210.5407 | 218.9562 | 232.4568 | 235.1173 | 237.6853 | 250.406 | 247.5805 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134.8969 | 139.3293 | 149.4273 | 159.2912 | 168.9144 | 183.9034 | 198.5458 | 207.3631 | 210.5407 | 218.9562 | 232.4568 | 235.1173 | 237.6853 | 250.406 | 247.5805 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.198 | 18.4466 | 21.6312 | 25.0485 | 28.8527 | 33.945 | 39.3818 | 44.0656 | 47.7059 | 53.0588 | 59.9199 | 64.6276 | 69.2767 | 77.1649 | 80.6695 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.198 | 18.4466 | 21.6312 | 25.0485 | 28.8527 | 33.945 | 39.3818 | 44.0656 | 47.7059 | 53.0588 | 59.9199 | 64.6276 | 69.2767 | 77.1649 | 80.6695 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.5834 | 13.4532 | 15.4655 | 18.1983 | 21.4603 | 24.4259 | 27.5407 | 31.5819 | 35.3455 | 40.1634 | 44.5882 | 50.2113 | 56.0055 | 61.7795 | 69.7042 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.8277 | 39.203 | 44.3621 | 51.8817 | 60.2395 | 68.9061 | 78.1447 | 84.6025 | 90.1325 | 90.1325 | 90.1325 | 90.1325 | 90.1325 | 90.1325 | 90.1325 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6762 | 86.6544 | 91.5123 | 97.0932 | 106.5009 | 110.9213 | 115.2266 | 124.0469 | 128.9208 | 137.1525 | 141.8991 | 150.7586 | 159.3991 | 167.7974 | 174.0623 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222.8092 | 240.6411 | 251.9482 | 268.2549 | 283.7809 | 298.5723 | 312.6308 | 320.6175 | 325.9434 | 320.2123 | 313.4963 | 306.399 | 297.9414 | 286.8845 | 275.0176 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20431.4528 | 21659.5753 | 22429.8734 | 23555.819 | 24321.7191 | 25140.7485 | 25958.2586 | 26941.9598 | 27766.3827 | 28728.6575 | 29354.7946 | 29927.5125 | 30585.7194 | 31177.5768 | 31505.3977 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24841.3224 | 25990.6038 | 26829.3782 | 27891.5213 | 28937.3277 | 29858.9604 | 30705.4944 | 31225.7305 | 31694.026 | 31717.3471 | 31771.4355 | 31828.2421 | 31902.881 | 32002.1184 | 32131.5546 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0511 | 6.4412 | 5.9172 | 5.3353 | 4.9627 | 4.5411 | 4.1839 | 3.9278 | 3.6474 | 3.4149 | 3.1824 | 3.0025 | 2.8461 | 2.7161 | 2.4972 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7872 | 6.1383 | 5.6794 | 5.1705 | 4.7109 | 4.333 | 4.0007 | 3.7897 | 3.6163 | 3.5527 | 3.4782 | 3.3994 | 3.3056 | 3.1829 | 3.0513 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Water Flow Suction | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
DERIVED VALUES
Heating Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.0949 | 157.7759 | 171.0586 | 184.3397 | 197.7671 | 217.8485 | 237.9275 | 251.4287 | 258.2465 | 272.015 | 292.3767 | 299.7449 | 306.9621 | 327.5709 | 328.25 | 0
COP Heating | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 9.328 | 8.5531 | 7.9079 | 7.3593 | 6.8544 | 6.4177 | 6.0416 | 5.7058 | 5.4133 | 5.1267 | 4.8795 | 4.638 | 4.431 | 4.2451 | 4.0691 | #DIV/0!
COP Heating | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 9.328 | 8.5531 | 7.9079 | 7.3593 | 6.8544 | 6.4177 | 6.0416 | 5.7058 | 5.4133 | 5.1267 | 4.8795 | 4.638 | 4.431 | 4.2451 | 4.0691 | 1
Water Flow Evaporator | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
delta T water Evaporator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4089 | 2.488 | 2.6683 | 2.8445 | 3.0163 | 3.284 | 3.5455 | 3.7029 | 3.7597 | 3.9099 | 4.151 | 4.1985 | 4.2444 | 4.4715 | 4.4211 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
delta T water Condenser | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7774 | 3.9444 | 4.2765 | 4.6085 | 4.9442 | 5.4462 | 5.9482 | 6.2857 | 6.4562 | 6.8004 | 7.3094 | 7.4936 | 7.6741 | 8.1893 | 8.2062 | 0
Maximum Heating Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.0949 | 157.7759 | 171.0586 | 184.3397 | 197.7671 | 217.8485 | 237.9275 | 251.4287 | 258.2465 | 410.3448 | 292.3767 | 299.7449 | 306.9621 | 327.5709 | 328.25 | 0
Minimum Heating Capacity | [15 empty] | 115.2914 | 127.9612 | 135.3472 | 142.7673 | 155.6289 | 164.2663 | 177.3159 | 186.4873 | 200.9699 | 215.4046 | 229.577 | 243.7665 | 0
Opt efficiency Power | [15 empty] | 184.3397 | 197.7671 | 217.8485 | 237.9275 | 251.4287 | 258.2465 | 272.015 | 292.3767 | 299.7449 | 306.9621 | 327.5709 | 328.25 | 0
TGH285-E-3-MT-SL | Aussentemperatur Luft | Verdampfungstemp | max Vorlauf | Min Leistung | opt. Leistung | Max. Leistung | COP min | COP max | el. Leistung
Aussentemperatur Luft | -10 | -15 | 35.5 | 130 | 147 | 147 | 3.2 | 3.8 | 38.6842
| -7 | -12 | 38 | 133 | 175 | 175 | 3.2 | 3.9 | 44.8718
| -4 | -9 | 43 | 149 | 188 | 188 | 3.2 | 3.7 | 50.8108
| -1 | -6 | 48 | 165 | 204 | 204 | 3.1 | 3.7 | 55.1351
| 2 | -3 | 53 | 219 | 265 | 249 | 3.3 | 3.9 | 63.8462
| 5 | 0 | 58 | 242 | 291 | 291 | 3.2 | 3.8 | 76.5789
| 8 | 3 | 63 | 266 | 330 | 330 | 3.1 | 3.7 | 89.1892
| 11 | 6 | 66 | 271 | 331 | 331 | 3.1 | 3.8 | 87.1053
| 14 | 9 | 66 | 256 | 342 | 342 | 3.4 | 3.9 | 87.6923
| 17 | 12 | 66 | 244 | 328 | 328 | 3.5 | 4.1 | 80

## Calculation A2W55 (4)
PN | 2718312
Calculation Type | FROM_POWER
Units | SI
Value | 0
SSH | 4
SDT | 2.5 | 5 | 7.5 | 10 | 12.5 | 15 | 17.5 | 20 | 22.5 | 25 | 27.5 | 30 | 32.5 | 35 | 37.5 | 40 | 42.5 | 45 | 47.5 | 50 | 52.5 | 55 | 57.5 | 60 | 62.5 | 65 | 67.5 | 70 | 72.5 | 75
SST | -18
LLT | 33 | -3 | -0.5 | 2 | 4.5 | 7 | 9.5 | 12 | 14.5 | 17 | 19.5 | 22 | 24.5 | 27 | 29.5 | 32 | 34.5 | 37 | 39.5 | 42 | 44.5 | 47 | 49.5 | 52 | 54.5 | 57 | 59.5 | 62 | 64.5 | 67
Use Economizer? | TRUE
tapp | 2
Compressor
PN Type | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312 | 2718312
Compressor | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL | TTH375-E-1-MT-SL
CID | CID=872448979 | CID=1591451598 | CID=529917621 | CID=1248920240 | CID=1634448319 | CID=-1941516358 | CID=1291916961 | CID=2010919580 | CID=-1898519637 | CID=-1179517018 | CID=2053916301 | CID=-1522048376 | CID=-1136520297 | CID=-417517678 | CID=1270483577 | CID=1989486196 | CID=-1919953021 | CID=-1200950402 | CID=2032482917 | CID=-1543481760 | CID=-1157953681 | CID=-438951062 | CID=-1500485039 | CID=-781482420 | CID=-395954341 | CID=-1158675479 | CID=-1158571956 | CID=-1158603477 | CID=-1158787194 | CID=-1158818971
Error | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Negative Economized Flow. Please turn off the economizer and try again. | Success | Success | Success | Success | Success | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor | Error finding minimum Flow Factor
MASS_FLOW_RATE_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.75357 | 0.7844 | 0.84662 | 0.95601 | 0.97109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32607.6276 | 33420.316 | 34387.5963 | 35538.7005 | 36006.4808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9946 | 3.7443 | 3.5087 | 3.3147 | 3.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3848 | 38.9972 | 44.576 | 52.8776 | 55.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.3495 | 146.0162 | 156.405 | 175.2746 | 176.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_SUCT_SAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18 | -18 | -18 | -18 | -18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_DISCH_SAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22.5 | 25 | 27.5 | 30 | 32.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_SUCT_SUPER_HEAT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_CONDENSER_LIQUID_LEAVING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.5 | 17 | 19.5 | 22 | 24.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_SUCT_ABSOLUTE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.6004 | 144.6004 | 144.6004 | 144.6004 | 144.6004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_DISCH_ABSOLUTE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 617.2019 | 665.3809 | 716.3449 | 770.1963 | 827.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEMPERATURE_DISCH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42.5254 | 45.572 | 48.7624 | 51.7216 | 53.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PRESSURE_RATIO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2683 | 4.6015 | 4.954 | 5.3264 | 5.7195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOLERANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0001 | 8.4121 | 10 | 5 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32607.6276 | 33420.316 | 34387.5963 | 35538.7005 | 36006.4808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32607.6276 | 33420.316 | 34387.5963 | 35538.7005 | 36006.4808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.3495 | 146.0162 | 156.405 | 175.2746 | 176.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.3495 | 146.0162 | 156.405 | 175.2746 | 176.6908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3848 | 38.9972 | 44.576 | 52.8776 | 55.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35.3848 | 38.9972 | 44.576 | 52.8776 | 55.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.2147 | 33.1457 | 38.3662 | 44.4172 | 52.8346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWER_INPUT_ELECTRICAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.5588 | 54.7795 | 55.3423 | 55.6414 | 55.353 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.4747 | 100.6973 | 110.5577 | 120.0307 | 130.7585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAPACITY_EVAPORATOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.3281 | 195.7918 | 191.2903 | 183.9243 | 176.6909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32608.8076 | 33199.9132 | 34102.7332 | 35013.8959 | 35821.3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPEED_COMPRESSOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35436.2005 | 35497.0081 | 35682.8739 | 35858.2004 | 36006.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.313 | 3.038 | 2.8816 | 2.7023 | 2.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COEFFICIENT_OF_PERFORMANCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6168 | 3.5742 | 3.4565 | 3.3055 | 3.1921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Water Flow Suction | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
DERIVED VALUES
Heating Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.7344 | 185.0134 | 200.9809 | 228.1522 | 232.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
COP Heating | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4.9946 | 4.7443 | 4.5087 | 4.3147 | 4.1921 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
COP Heating | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4.9946 | 4.7443 | 4.5087 | 4.3147 | 4.1921 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Water Flow Evaporator | 10 | 10 | 10 | 10 | 10 | 10 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
delta T water Evaporator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5241 | 2.6074 | 2.7929 | 3.1299 | 3.1552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Water Flow Condenser | 8 | 8 | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
delta T water Condenser | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4184 | 4.6253 | 5.0245 | 5.7038 | 5.8011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum Heating Capacity | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176.7344 | 185.0134 | 200.9809 | 228.1522 | 232.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Heating Capacity | [6 empty] | 0 | 0 | 121.6894 | 133.843 | 148.9238 | 164.4479 | 183.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Opt efficiency Power | [6 empty] | 0 | 0 | 176.7344 | 185.0134 | 200.9809 | 228.1522 | 232.0438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TTH375-E-1-MT-SL | Aussentemperatur Luft | Verdampfungstemp | max Vorlauf | Min Leistung | opt. Leistung | Max. Leistung | COP min | COP max | el Leistung
| -13 | -18 | 31 | 184 | 232 | 232 | 3.5 | 4.2 | 55.2381
Aussentemperatur Luft | -10 | -15 | 36 | 209 | 254 | 254 | 3.4 | 4.1 | 61.9512
| -7 | -12 | 41 | 235 | 282 | 282 | 3.4 | 4.1 | 68.7805
| -4 | -9 | 46 | 263 | 303 | 303 | 3.3 | 3.9 | 77.6923
| -1 | -6 | 51 | 293 | 334 | 334 | 3.2 | 3.8 | 87.8947
| 2 | -3 | 56 | 325 | 367 | 367 | 3.1 | 3.7 | 99.1892
| 5 | 0 | 58 | 332 | 422 | 422 | 3.1 | 3.8 | 111.0526
| 8 | 3 | 63 | 367 | 461 | 461 | 3.1 | 3.7 | 124.5946
| 11 | 6 | 66 | 371 | 463 | 463 | 3.1 | 3.7 | 125.1351
| 14 | 9 | 68 | 377 | 468 | 468 | 3.2 | 3.7 | 126.4865
| 17 | 12 | 68 | 359 | 481 | 481 | 3.9 | 3.4 | 141.4706