## Server Version
Server Version | 2760
2760
2760
Note on B1: Edgar F. Hilton: This queries the server to obtain the version of the server. This is generally a good thing to check for before contacting support.

## Feature Discovery
Index | Supported Variable | SI | British | Supported Units | Supported Calculation Type
1 | ENTROPY_SUCTION | kJ/kg_K | Btu/(lb) (R) | SI | FROM_CAPACITY
2 | SPEED_SOUND | m/s | ft/sec | British | FROM_EVAP_MASS_FLOW
3 | DENSITY_SUCTION | kg/m3 | lb/ft3 |  | FROM_POWER
4 | ENTHALPY_LIQUID_CONDENSER_EXIT | kJ/kg | Btu/lb
5 | ENTHALPY_DISCHARGE_ISENTROPIC | kJ/kg | Btu/lb
6 | ENTHALPY_SUCTION | kJ/kg | Btu/lb
7 | SPEED_COMPRESSOR | RPM | RPM
8 | MASS_FLOW_RATE_EVAPORATOR | kg/s | lbs/sec
9 | MASS_FLOW_RATE_MOTOR_COOLING | kg/s | lbs/sec
10 | COEFFICIENT_OF_PERFORMANCE | kW/kW | kW/ton
11 | POWER_INPUT_ELECTRICAL | kW | kW
12 | CAPACITY_EVAPORATOR | kW | Ton
13 | TEMPERATURE_SUCT_SAT | C | F
14 | TEMPERATURE_DISCH_SAT | C | F
15 | TEMPERATURE_SUCT_SUPER_HEAT | C | F
16 | TEMPERATURE_CONDENSER_LIQUID_LEAVING | C | F
17 | PRESSURE_SUCT_ABSOLUTE | kPa | PSI
18 | PRESSURE_DISCH_ABSOLUTE | kPa | PSI
19 | TEMPERATURE_DISCH | C | F
20 | PRESSURE_RATIO
21 | POWER_FACTOR
22 | IGV_ANGLE | % | %
23 | INPUT_CURRENT | A | A
24 | ECON_SAT_TEMP | C | F
25 | ECON_INTERSTAGE_P | kPa | PSI
26 | ECON_CAPACITY | kW | Ton
27 | ECON_MASS_FLOW | kg/s | lbs/sec
28 | TEMPERATURE_ECO_LIQUID_LEAVING | C | F
29 | ENTHALPY_LIQUID_ECO_EXIT | kJ/kg | Btu/lb
Note on A1: Edgar F. Hilton: Just a counter. We'll be using these counters to help us with the columns to the right.
Note on B1: Edgar F. Hilton: This is a list of variables which the server knows about. You may want to call NumberOfVariables() first to obtain the total number of variables available to you.
Note on C1: Edgar F. Hilton: SI units for the variables in the previous column.
Note on D1: Edgar F. Hilton: British Units for the variables column.
Note on F1: Edgar F. Hilton: The list of supported units.
Note on H1: Edgar F. Hilton: The list of calculation types supported by the server. We'll be using these when we start querying the server to do a calculation for us.

## TTH375-noEcon_A
PN | 2718312
Calculation Type | FROM_POWER
Units | SI
Use Economizer? | FALSE
Compressor | TTH375-E-1-MT-SL
| Step SST | Step SDT | Percent Power |  | Subcooling
| 3 | 2.5 |  |  | 6 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 11 | 11
| INPUT BLOCK | [5 empty] | 1: OUTPUT
CID | SST Verd. Temp | SDT Kond. Temperatur | Value Power | SSH Superheat | LLT Leaving Liquid Temp | tapp T approach Economizer | ENTROPY_SUCTION | SPEED_SOUND | DENSITY_SUCTION | ENTHALPY_LIQUID_CONDENSER_EXIT | ENTHALPY_DISCHARGE_ISENTROPIC | ENTHALPY_SUCTION | SPEED_COMPRESSOR | MASS_FLOW_RATE_EVAPORATOR | MASS_FLOW_RATE_MOTOR_COOLING | COEFFICIENT_OF_PERFORMANCE | POWER_INPUT_ELECTRICAL | CAPACITY_EVAPORATOR | TEMPERATURE_SUCT_SAT | TEMPERATURE_DISCH_SAT | TEMPERATURE_SUCT_SUPER_HEAT | TEMPERATURE_CONDENSER_LIQUID_LEAVING | PRESSURE_SUCT_ABSOLUTE | PRESSURE_DISCH_ABSOLUTE | TEMPERATURE_DISCH | PRESSURE_RATIO | POWER_FACTOR | IGV_ANGLE | INPUT_CURRENT | ECON_SAT_TEMP | ECON_INTERSTAGE_P | ECON_CAPACITY | ECON_MASS_FLOW | TEMPERATURE_ECO_LIQUID_LEAVING | ENTHALPY_LIQUID_ECO_EXIT | TOLERANCE | POWER_INPUT_ELECTRICAL | POWER_INPUT_ELECTRICAL
CID=-132218218 | -18 | -5 | 0 | 4 | -11 | 0 | 1.7524 | 147.8757 | 7.2169 | 185.3801 | 401.7246 | 391.078 | 20057.8231 | 0.31403 | 0.0061287 | 10.3337 | 6.251 | 64.5957 | -18 | -5 | 4 | -11 | 144.6004 | 243.3424 | 7.6445 | 1.6829 | 0.66014 | 110 | 14.3869 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5498 | 11.5167
CID=-132218187 | -18 | -2.5 | 0 | 4 | -8.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 188.676 | 403.6805 | 391.078 | 21487.03 | 0.34573 | 0.0064464 | 9.1651 | 7.6351 | 69.9765 | -18 | -2.5 | 4 | -8.5 | 144.6004 | 267.1911 | 11.0385 | 1.8478 | 0.67515 | 110 | 17.1818 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.577 | 14.6204
CID=-132218156 | -18 | 0 | 0 | 4 | -6 | 0 | 1.7524 | 147.8757 | 7.2169 | 191.9873 | 405.6071 | 391.078 | 23237.1826 | 0.40622 | 0.0070358 | 8.1973 | 9.866 | 80.8746 | -18 | 0 | 4 | -6 | 144.6004 | 292.8032 | 14.5622 | 2.0249 | 0.69755 | 110 | 21.4894 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.7893 | 18.1802
CID=-132218373 | -18 | 2.5 | 0 | 4 | -3.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 195.3144 | 407.5045 | 391.078 | 24299.4692 | 0.42473 | 0.0074851 | 7.4185 | 11.208 | 83.147 | -18 | 2.5 | 4 | -3.5 | 144.6004 | 320.2635 | 17.5713 | 2.2148 | 0.71002 | 110 | 23.9835 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8511 | 21.3458
CID=-132218342 | -18 | 5 | 0 | 4 | -1 | 0 | 1.7524 | 147.8757 | 7.2169 | 198.6579 | 409.3731 | 391.078 | 25443.8929 | 0.45615 | 0.0080864 | 6.7478 | 13.0075 | 87.7716 | -18 | 5 | 4 | -1 | 144.6004 | 349.6586 | 20.6586 | 2.4181 | 0.72566 | 110 | 27.2344 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5588 | 25.7708
CID=-132218311 | -18 | 7.5 | 0 | 4 | 1.5 | 0.3 | 1.7524 | 147.8757 | 7.2169 | 202.0183 | 411.2128 | 391.078 | 26738.1424 | 0.50333 | 0.0089241 | 6.1317 | 15.5193 | 95.1599 | -18 | 7.5 | 4 | 1.5 | 144.6004 | 381.0767 | 23.9737 | 2.6354 | 0.74555 | 110 | 31.6264 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.097 | 30.644
CID=-132218280 | -18 | 10 | 0 | 4 | 4 | 0.8 | 1.7524 | 147.8757 | 7.2169 | 205.396 | 413.024 | 391.078 | 28046.8451 | 0.56628 | 0.01001 | 5.6166 | 18.7209 | 105.1476 | -18 | 10 | 4 | 4 | 144.6004 | 414.6075 | 27.2012 | 2.8673 | 0.76799 | 110 | 37.0363 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0916 | 35.9571
CID=-132218497 | -18 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7524 | 147.8757 | 7.2169 | 208.7918 | 414.8068 | 391.078 | 29112.3591 | 0.61325 | 0.011058 | 5.174 | 21.6056 | 111.7878 | -18 | 12.5 | 4 | 6.5 | 144.6004 | 450.3422 | 30.278 | 3.1144 | 0.78572 | 110 | 41.7785 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2624 | 39.94
CID=-132218466 | -18 | 15 | 0 | 4 | 9 | 1.8 | 1.7524 | 147.8757 | 7.2169 | 212.2062 | 416.5615 | 391.078 | 29993.8042 | 0.64428 | 0.012051 | 4.7707 | 24.1563 | 115.2431 | -18 | 15 | 4 | 9 | 144.6004 | 488.3739 | 33.3817 | 3.3774 | 0.79967 | 110 | 45.896 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.7059 | 45.4484
CID=-487156954 | -18 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7524 | 147.8757 | 7.2169 | 215.6398 | 418.2881 | 391.078 | 30971.5862 | 0.69101 | 0.013341 | 4.4072 | 27.5075 | 121.2299 | -18 | 17.5 | 4 | 11.5 | 144.6004 | 528.7968 | 36.5572 | 3.657 | 0.81582 | 110 | 51.2286 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3419 | 50.6552
CID=-487156923 | -18 | 20 | 0 | 4 | 14 | 2.8 | 1.7524 | 147.8757 | 7.2169 | 219.0933 | 419.9871 | 391.078 | 31819.7093 | 0.72178 | 0.014589 | 4.0633 | 30.5506 | 124.135 | -18 | 20 | 4 | 14 | 144.6004 | 571.7069 | 39.8786 | 3.9537 | 0.8286 | 110 | 56.0185 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3788 | 51.6444
CID=-487156892 | -18 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7524 | 147.8757 | 7.2169 | 222.5675 | 421.6585 | 391.078 | 32607.6276 | 0.75249 | 0.015898 | 3.7731 | 33.6066 | 126.8019 | -18 | 22.5 | 4 | 16.5 | 144.6004 | 617.2019 | 43.0121 | 4.2683 | 0.83985 | 110 | 60.7962 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0001 | 26.5651 | 51.5068
CID=-487156861 | -18 | 25 | 0 | 4 | 19 | 3.8 | 1.7524 | 147.8757 | 7.2169 | 226.0633 | 423.3026 | 391.078 | 33420.316 | 0.78308 | 0.017321 | 3.5091 | 36.8244 | 129.2198 | -18 | 25 | 4 | 19 | 144.6004 | 665.3809 | 46.1645 | 4.6015 | 0.85021 | 109.8635 | 65.806 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4121 | 30.9668 | 51.5623
CID=-487157078 | -18 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7524 | 147.8757 | 7.2169 | 229.5813 | 424.9196 | 391.078 | 34387.5973 | 0.845 | 0.019429 | 3.262 | 41.8353 | 136.4652 | -18 | 27.5 | 4 | 21.5 | 144.6004 | 716.3449 | 49.4628 | 4.954 | 0.86374 | 109.5721 | 73.5896 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.6287 | 51.8719
CID=-487157047 | -18 | 30 | 0 | 4 | 24 | 4.8 | 1.7524 | 147.8757 | 7.2169 | 233.1226 | 426.5097 | 391.078 | 35538.7005 | 0.95397 | 0.022518 | 3.0547 | 49.329 | 150.6849 | -18 | 30 | 4 | 24 | 144.6004 | 770.1963 | 52.5394 | 5.3264 | 0.87924 | 110 | 85.2419 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.9637 | 51.8934
CID=-487157016 | -18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7524 | 147.8757 | 7.2169 | 236.688 | 428.0733 | 391.078 | 36006.4808 | 0.96871 | 0.023785 | 2.9103 | 51.389 | 149.5593 | -18 | 32.5 | 4 | 26.5 | 144.6004 | 827.0396 | 54.7307 | 5.7195 | 0.88269 | 110 | 88.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.2998 | 51.389
CID=-487156985 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-487157202 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-487157171 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1483503169 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354671 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354702 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354733 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354516 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354547 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354578 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354609 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354392 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1737354423 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1171412981 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1171413012 | -18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-293067002 | -15 | -5 | 0 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-293066971 | -15 | -2.5 | 0 | 4 | -8.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 188.676 | 402.9994 | 392.9623 | 19515.5724 | 0.3369 | 0.0061807 | 10.8703 | 6.3314 | 68.8245 | -15 | -2.5 | 4 | -8.5 | 163.9401 | 267.1911 | 9.5396 | 1.6298 | 0.66103 | 103.7476 | 14.5524 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.9292 | 11.8126
CID=-293067188 | -15 | 0 | 0 | 4 | -6 | 0 | 1.7499 | 148.1062 | 8.1279 | 191.9873 | 404.9188 | 392.9623 | 20958.1076 | 0.37267 | 0.0065275 | 9.5778 | 7.8199 | 74.8972 | -15 | 0 | 4 | -6 | 163.9401 | 292.8032 | 12.9422 | 1.786 | 0.67709 | 108.7305 | 17.5473 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2695 | 5.7776 | 15.1388
CID=-293067157 | -15 | 2.5 | 0 | 4 | -3.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 195.3144 | 406.8092 | 392.9623 | 22549.3618 | 0.42628 | 0.007087 | 8.5403 | 9.8654 | 84.2534 | -15 | 2.5 | 4 | -3.5 | 163.9401 | 320.2635 | 16.3169 | 1.9535 | 0.69754 | 110 | 21.4881 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.9172 | 18.8847
CID=-293067126 | -15 | 5 | 0 | 4 | -1 | 0 | 1.7499 | 148.1062 | 8.1279 | 198.6579 | 408.6707 | 392.9623 | 23717.9395 | 0.45257 | 0.0076045 | 7.6757 | 11.4564 | 87.9358 | -15 | 5 | 4 | -1 | 163.9401 | 349.6586 | 19.4463 | 2.1328 | 0.71225 | 110 | 24.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3095 | 23.1137
CID=-293067095 | -15 | 7.5 | 0 | 4 | 1.5 | 0.3 | 1.7499 | 148.1062 | 8.1279 | 202.0183 | 410.5034 | 392.9623 | 25136.7484 | 0.5152 | 0.0084484 | 6.9711 | 14.1118 | 98.3751 | -15 | 7.5 | 4 | 1.5 | 163.9401 | 381.0767 | 22.6084 | 2.3245 | 0.73467 | 110 | 29.1841 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.7669 | 26.7752
CID=-293067312 | -15 | 10 | 0 | 4 | 4 | 0.8 | 1.7499 | 148.1062 | 8.1279 | 205.396 | 412.3077 | 392.9623 | 26253.8682 | 0.55055 | 0.0092136 | 6.3391 | 16.2902 | 103.2651 | -15 | 10 | 4 | 4 | 163.9401 | 414.6075 | 25.7298 | 2.529 | 0.75124 | 110 | 32.946 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7699 | 32.0031
CID=-293067281 | -15 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7499 | 148.1062 | 8.1279 | 208.7918 | 414.0836 | 392.9623 | 27467.315 | 0.60369 | 0.010243 | 5.781 | 19.2324 | 111.1827 | -15 | 12.5 | 4 | 6.5 | 163.9401 | 450.3422 | 28.9508 | 2.747 | 0.7713 | 110 | 37.885 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.601 | 37.5469
CID=-100268829 | -15 | 15 | 0 | 4 | 9 | 1.8 | 1.7499 | 148.1062 | 8.1279 | 212.2062 | 415.8315 | 392.9623 | 28420.5259 | 0.63886 | 0.01119 | 5.3131 | 21.7345 | 115.4779 | -15 | 15 | 4 | 9 | 163.9401 | 488.3739 | 31.9916 | 2.979 | 0.78647 | 110 | 41.9881 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8508 | 41.9673
CID=-100268798 | -15 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7499 | 148.1062 | 8.1279 | 215.6398 | 417.5513 | 392.9623 | 29300.8739 | 0.67395 | 0.012213 | 4.9104 | 24.3373 | 119.507 | -15 | 17.5 | 4 | 11.5 | 163.9401 | 528.7968 | 34.9506 | 3.2255 | 0.8006 | 110 | 46.186 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.3412 | 47.8386
CID=-100268767 | -15 | 20 | 0 | 4 | 14 | 2.8 | 1.7499 | 148.1062 | 8.1279 | 219.0933 | 419.2435 | 392.9623 | 30324.9327 | 0.72673 | 0.013604 | 4.5197 | 27.957 | 126.3561 | -15 | 20 | 4 | 14 | 163.9401 | 571.7069 | 38.1902 | 3.4873 | 0.81781 | 110 | 51.9388 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.1691 | 53.5948
CID=-100268736 | -15 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7499 | 148.1062 | 8.1279 | 222.5675 | 420.9082 | 392.9623 | 31268.0825 | 0.77938 | 0.015124 | 4.1796 | 31.7739 | 132.8028 | -15 | 22.5 | 4 | 16.5 | 163.9401 | 617.2019 | 41.353 | 3.7648 | 0.83328 | 110 | 57.9341 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0585 | 58.447
CID=-100268953 | -15 | 25 | 0 | 4 | 19 | 3.8 | 1.7499 | 148.1062 | 8.1279 | 226.0633 | 422.5457 | 392.9623 | 32093.2632 | 0.81406 | 0.016556 | 3.8685 | 35.1212 | 135.8666 | -15 | 25 | 4 | 19 | 163.9401 | 665.3809 | 44.5449 | 4.0587 | 0.84491 | 110 | 63.1563 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8402 | 58.803
CID=-100268922 | -15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7499 | 148.1062 | 8.1279 | 229.5813 | 424.156 | 392.9623 | 32925.0949 | 0.86645 | 0.018341 | 3.6015 | 39.3061 | 141.5616 | -15 | 27.5 | 4 | 21.5 | 163.9401 | 716.3449 | 47.6105 | 4.3696 | 0.85727 | 110 | 69.662 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.3546 | 58.5759
CID=-100268891 | -15 | 30 | 0 | 4 | 24 | 4.8 | 1.7499 | 148.1062 | 8.1279 | 233.1226 | 425.7396 | 392.9623 | 33738.4285 | 0.90086 | 0.020044 | 3.3475 | 43.0158 | 143.9936 | -15 | 30 | 4 | 24 | 163.9401 | 770.1963 | 50.7925 | 4.698 | 0.86652 | 109.8574 | 75.4231 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5653 | 36.422 | 57.9392
CID=-100268860 | -15 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7499 | 148.1062 | 8.1279 | 236.688 | 427.2966 | 392.9623 | 34663.6049 | 0.97062 | 0.022516 | 3.1181 | 48.6461 | 151.6825 | -15 | 32.5 | 4 | 26.5 | 163.9401 | 827.0396 | 53.9902 | 5.0448 | 0.87802 | 109.3476 | 84.178 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.4958 | 58.3942
CID=-100269077 | -15 | 35 | 0 | 4 | 29 | 5.8 | 1.7499 | 148.1062 | 8.1279 | 240.2788 | 428.8272 | 392.9623 | 35882.0706 | 1.1111 | 0.026476 | 2.9251 | 57.9975 | 169.6487 | -15 | 35 | 4 | 29 | 163.9401 | 886.981 | 56.9779 | 5.4104 | 0.89192 | 110 | 98.796 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0343 | 58.9531
CID=-100269046 | -15 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7499 | 148.1062 | 8.1279 | 243.8959 | 430.3317 | 392.9623 | 35987.6855 | 1.0749 | 0.026587 | 2.8317 | 56.5848 | 160.2296 | -15 | 37.5 | 4 | 31.5 | 163.9401 | 950.1287 | 58.3938 | 5.7956 | 0.89016 | 110 | 96.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.3815 | 56.5848
CID=-455207534 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-455207503 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-455207472 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-455207441 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1507833021 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1507832990 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1507832959 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1507832928 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1507833145 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1507833114 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1705405220 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1705405251 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1705405282 | -15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1515452682 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1515452465 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1515452496 | -12 | 0 | 0 | 4 | -6 | 0 | 1.7476 | 148.2918 | 9.1273 | 191.9873 | 404.2823 | 394.8346 | 19508.1508 | 0.37947 | 0.0062807 | 11.4183 | 6.7413 | 76.9742 | -12 | 0 | 4 | -6 | 185.2442 | 292.8032 | 11.6831 | 1.5806 | 0.66556 | 98.191 | 15.3891 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.4538 | 12.3991
CID=1515452527 | -12 | 2.5 | 0 | 4 | -3.5 | 0 | 1.7476 | 148.2918 | 9.1273 | 195.3144 | 406.166 | 394.8346 | 20417.2478 | 0.39945 | 0.0066012 | 10.0224 | 7.952 | 79.6986 | -12 | 2.5 | 4 | -3.5 | 185.2442 | 320.2635 | 14.845 | 1.7289 | 0.67847 | 108.4714 | 17.8076 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8214 | 5.9439 | 15.6403
CID=1515452558 | -12 | 5 | 0 | 4 | -1 | 0 | 1.7476 | 148.2918 | 9.1273 | 198.6579 | 408.021 | 394.8346 | 21792.1083 | 0.43955 | 0.0071096 | 8.8559 | 9.7369 | 86.229 | -12 | 5 | 4 | -1 | 185.2442 | 349.6586 | 18.1926 | 1.8876 | 0.69631 | 110 | 21.2458 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3298 | 19.5445
CID=1515452341 | -12 | 7.5 | 0 | 4 | 1.5 | 0.3 | 1.7476 | 148.2918 | 9.1273 | 202.0183 | 409.8472 | 394.8346 | 23309.477 | 0.49973 | 0.007834 | 7.9539 | 12.1144 | 96.3563 | -12 | 7.5 | 4 | 1.5 | 185.2442 | 381.0767 | 21.4023 | 2.0572 | 0.71805 | 110 | 25.6332 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5649 | 23.9769
CID=1515452372 | -12 | 10 | 0 | 4 | 4 | 0.8 | 1.7476 | 148.2918 | 9.1273 | 205.396 | 411.6451 | 394.8346 | 24496.5222 | 0.53963 | 0.0085443 | 7.1908 | 14.2161 | 102.2259 | -12 | 10 | 4 | 4 | 185.2442 | 414.6075 | 24.475 | 2.2382 | 0.7355 | 110 | 29.3667 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.993 | 27.8065
CID=-388915324 | -12 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7476 | 148.2918 | 9.1273 | 208.7918 | 413.4146 | 394.8346 | 25601.6948 | 0.57943 | 0.0093413 | 6.5442 | 16.4725 | 107.7996 | -12 | 12.5 | 4 | 6.5 | 185.2442 | 450.3422 | 27.5016 | 2.4311 | 0.75256 | 110 | 33.2564 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1391 | 33.2299
CID=-388915293 | -12 | 15 | 0 | 4 | 9 | 1.8 | 1.7476 | 148.2918 | 9.1273 | 212.2062 | 415.1561 | 394.8346 | 26846.1426 | 0.63924 | 0.01044 | 5.9551 | 19.6042 | 116.744 | -12 | 15 | 4 | 9 | 185.2442 | 488.3739 | 30.7104 | 2.6364 | 0.77366 | 110 | 38.4997 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0304 | 39.1019
CID=-388915262 | -12 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7476 | 148.2918 | 9.1273 | 215.6398 | 416.8697 | 394.8346 | 27977.9009 | 0.69893 | 0.011659 | 5.4578 | 22.9479 | 125.2451 | -12 | 17.5 | 4 | 11.5 | 185.2442 | 528.7968 | 33.8135 | 2.8546 | 0.79325 | 110 | 43.9528 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.4121 | 45.5079
CID=-388915231 | -12 | 20 | 0 | 4 | 14 | 2.8 | 1.7476 | 148.2918 | 9.1273 | 219.0933 | 418.5557 | 394.8346 | 29014.4548 | 0.7585 | 0.012997 | 5.0326 | 26.4872 | 133.3002 | -12 | 20 | 4 | 14 | 185.2442 | 571.7069 | 36.8191 | 3.0862 | 0.81115 | 110 | 49.6126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.032 | 50.1624
CID=-388915448 | -12 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7476 | 148.2918 | 9.1273 | 222.5675 | 420.2141 | 394.8346 | 29869.1208 | 0.79786 | 0.014249 | 4.6483 | 29.5688 | 137.4442 | -12 | 22.5 | 4 | 16.5 | 185.2442 | 617.2019 | 39.8279 | 3.3318 | 0.82466 | 110 | 54.4774 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.8538 | 56.7855
CID=-388915417 | -12 | 25 | 0 | 4 | 19 | 3.8 | 1.7476 | 148.2918 | 9.1273 | 226.0633 | 421.8454 | 394.8346 | 30942.1165 | 0.87715 | 0.016159 | 4.2942 | 34.474 | 148.0386 | -12 | 25 | 4 | 19 | 185.2442 | 665.3809 | 42.978 | 3.5919 | 0.84279 | 110 | 62.1483 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9272 | 62.9919
CID=-388915386 | -12 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7476 | 148.2918 | 9.1273 | 229.5813 | 423.4496 | 394.8346 | 31641.0012 | 0.89616 | 0.017459 | 3.9694 | 37.3089 | 148.0931 | -12 | 27.5 | 4 | 21.5 | 185.2442 | 716.3449 | 46.1199 | 3.867 | 0.85165 | 110 | 66.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.6206 | 65.6702
CID=-388915355 | -12 | 30 | 0 | 4 | 24 | 4.8 | 1.7476 | 148.2918 | 9.1273 | 233.1226 | 425.027 | 394.8346 | 32334.9668 | 0.91509 | 0.018825 | 3.6847 | 40.161 | 147.9818 | -12 | 30 | 4 | 24 | 185.2442 | 770.1963 | 49.1894 | 4.1577 | 0.85954 | 109.6756 | 70.9897 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2439 | 32.3085 | 65.9405
CID=-388915572 | -12 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7476 | 148.2918 | 9.1273 | 236.688 | 426.5779 | 394.8346 | 33157.497 | 0.97393 | 0.020894 | 3.4369 | 44.8145 | 154.0243 | -12 | 32.5 | 4 | 26.5 | 185.2442 | 827.0396 | 52.184 | 4.4646 | 0.8705 | 109.895 | 78.2176 | 0 | 0 | 0 | 0 | 0 | 0 | 5.875 | 36.6126 | 65.8016
CID=-388915541 | -12 | 35 | 0 | 4 | 29 | 5.8 | 1.7476 | 148.2918 | 9.1273 | 240.2788 | 428.1024 | 394.8346 | 33936.1707 | 1.0125 | 0.022896 | 3.1934 | 49.0057 | 156.4935 | -12 | 35 | 4 | 29 | 185.2442 | 886.981 | 55.3809 | 4.7882 | 0.87867 | 109.4152 | 84.7381 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.4028 | 65.639
CID=-196117089 | -12 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7476 | 148.2918 | 9.1273 | 243.8959 | 429.6009 | 394.8346 | 35002.58 | 1.1307 | 0.026513 | 2.9799 | 57.2741 | 170.6716 | -12 | 37.5 | 4 | 31.5 | 185.2442 | 950.1287 | 58.5205 | 5.1291 | 0.89103 | 109.971 | 97.6608 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2418 | 47.9875 | 66.1098
CID=-196117058 | -12 | 40 | 0 | 4 | 34 | 6.8 | 1.7476 | 148.2918 | 9.1273 | 247.5407 | 431.0734 | 394.8346 | 36031.55 | 1.2688 | 0.030529 | 2.8274 | 66.0993 | 186.8919 | -12 | 40 | 4 | 34 | 185.2442 | 1016.593 | 60.9572 | 5.4879 | 0.90018 | 110 | 111.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7449 | 55.8685 | 66.0993
CID=-196117027 | -12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7476 | 148.2918 | 9.1273 | 251.2145 | 432.5204 | 394.8346 | 36100.3634 | 1.208 | 0.030475 | 2.7125 | 63.9602 | 173.4908 | -12 | 42.5 | 4 | 36.5 | 185.2442 | 1086.4865 | 62.7844 | 5.8652 | 0.89827 | 110 | 108.1828 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1387 | 63.9602
CID=-196116996 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-196117213 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-185531969 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-185532000 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-185532031 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-185531814 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-185531845 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2003266584 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1902510035 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=316223118 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1270063799 | -12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1428260321 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-124298406 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1744313513 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1246691868 | -9 | 2.5 | 0 | 4 | -3.5 | 0 | 1.7455 | 148.4312 | 10.2212 | 195.3144 | 405.5712 | 396.6938 | 19526.164 | 0.4033 | 0.0063269 | 12.0428 | 6.744 | 81.2166 | -9 | 2.5 | 4 | -3.5 | 208.6448 | 320.2635 | 13.5876 | 1.535 | 0.66559 | 81.9115 | 15.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.8776 | 10.3709
CID=1334380771 | -9 | 5 | 0 | 4 | -1 | 0 | 1.7455 | 148.4312 | 10.2212 | 198.6579 | 407.4201 | 396.6938 | 20132.9411 | 0.44838 | 0.0067616 | 10.4632 | 8.4865 | 88.7955 | -9 | 5 | 4 | -1 | 208.6448 | 349.6586 | 16.9635 | 1.6759 | 0.68395 | 110 | 18.8519 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9672 | 16.0914
CID=-1656624610 | -9 | 7.5 | 0 | 4 | 1.5 | 0.3 | 1.7455 | 148.4312 | 10.2212 | 202.0183 | 409.2404 | 396.6938 | 21494.3834 | 0.49333 | 0.0073233 | 9.2412 | 10.3926 | 96.0399 | -9 | 7.5 | 4 | 1.5 | 208.6448 | 381.0767 | 20.1772 | 1.8264 | 0.70253 | 110 | 22.4758 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3549 | 20.1873
CID=-507378932 | -9 | 10 | 0 | 4 | 4 | 0.8 | 1.7455 | 148.4312 | 10.2212 | 205.396 | 411.0322 | 396.6938 | 22589.5041 | 0.51555 | 0.007865 | 8.2214 | 11.9959 | 98.6233 | -9 | 10 | 4 | 4 | 208.6448 | 414.6075 | 23.3107 | 1.9871 | 0.71702 | 108.9194 | 25.4191 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7014 | 8.9222 | 24.8293
CID=796582983 | -9 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7455 | 148.4312 | 10.2212 | 208.7918 | 412.7959 | 396.6938 | 23909.5066 | 0.56999 | 0.0086761 | 7.4176 | 14.4388 | 107.1016 | -9 | 12.5 | 4 | 6.5 | 208.6448 | 450.3422 | 26.3987 | 2.1584 | 0.73726 | 109.6894 | 29.7556 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5529 | 10.5321 | 29.3656
CID=-1629772394 | -9 | 15 | 0 | 4 | 9 | 1.8 | 1.7455 | 148.4312 | 10.2212 | 212.2062 | 414.5315 | 396.6938 | 25282.6168 | 0.65016 | 0.0097999 | 6.7463 | 17.7794 | 119.9459 | -9 | 15 | 4 | 9 | 208.6448 | 488.3739 | 29.4624 | 2.3407 | 0.76171 | 110 | 35.4637 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3102 | 34.4149
CID=-325810479 | -9 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7455 | 148.4312 | 10.2212 | 215.6398 | 416.2392 | 396.6938 | 26362.4244 | 0.69467 | 0.010796 | 6.1392 | 20.4869 | 125.7737 | -9 | 17.5 | 4 | 11.5 | 208.6448 | 528.7968 | 32.5317 | 2.5344 | 0.77911 | 110 | 39.9518 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7558 | 40.7191
CID=-1428259296 | -9 | 20 | 0 | 4 | 14 | 2.8 | 1.7455 | 148.4312 | 10.2212 | 219.0933 | 417.9194 | 396.6938 | 27396.6641 | 0.73908 | 0.011907 | 5.6067 | 23.4115 | 131.2607 | -9 | 20 | 4 | 14 | 208.6448 | 571.7069 | 35.6252 | 2.7401 | 0.79576 | 110 | 44.6997 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9978 | 47.3518
CID=-124297381 | -9 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7455 | 148.4312 | 10.2212 | 222.5675 | 419.5721 | 396.6938 | 28444.8635 | 0.80592 | 0.013338 | 5.1629 | 27.1807 | 140.3316 | -9 | 22.5 | 4 | 16.5 | 208.6448 | 617.2019 | 38.6142 | 2.9581 | 0.81435 | 110 | 50.7117 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.6774 | 52.6566
CID=1744314538 | -9 | 25 | 0 | 4 | 19 | 3.8 | 1.7455 | 148.4312 | 10.2212 | 226.0633 | 421.1976 | 396.6938 | 29296.3406 | 0.85012 | 0.014649 | 4.7751 | 30.3775 | 145.0568 | -9 | 25 | 4 | 19 | 208.6448 | 665.3809 | 41.5186 | 3.1891 | 0.82792 | 110 | 55.7471 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5308 | 59.4656
CID=-1246690843 | -9 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7455 | 148.4312 | 10.2212 | 229.5813 | 422.7961 | 396.6938 | 30274.7007 | 0.91662 | 0.016421 | 4.4043 | 34.7795 | 153.1788 | -9 | 27.5 | 4 | 21.5 | 208.6448 | 716.3449 | 44.6329 | 3.4333 | 0.84379 | 110 | 62.6242 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.7566 | 66.4236
CID=1334381796 | -9 | 30 | 0 | 4 | 24 | 4.8 | 1.7455 | 148.4312 | 10.2212 | 233.1226 | 424.3678 | 396.6938 | 31181.507 | 0.98296 | 0.018351 | 4.0811 | 39.3976 | 160.7845 | -9 | 30 | 4 | 24 | 208.6448 | 770.1963 | 47.6688 | 3.6914 | 0.85752 | 110 | 69.8042 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1758 | 73.3333
CID=-1656623585 | -9 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7455 | 148.4312 | 10.2212 | 236.688 | 425.913 | 396.6938 | 31974.1754 | 1.0266 | 0.0202 | 3.7742 | 43.5232 | 164.2664 | -9 | 32.5 | 4 | 26.5 | 208.6448 | 827.0396 | 50.8344 | 3.9639 | 0.86768 | 110 | 76.2112 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.425 | 73.7137
CID=-507377911 | -9 | 35 | 0 | 4 | 29 | 5.8 | 1.7455 | 148.4312 | 10.2212 | 240.2788 | 427.4319 | 396.6938 | 32706.1711 | 1.0702 | 0.022146 | 3.5116 | 47.669 | 167.3947 | -9 | 35 | 4 | 29 | 208.6448 | 886.981 | 53.8473 | 4.2512 | 0.87622 | 110 | 82.6568 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.4523 | 73.3536
CID=796584004 | -9 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7455 | 148.4312 | 10.2212 | 243.8959 | 428.9247 | 396.6938 | 33449.9217 | 1.1136 | 0.024243 | 3.2747 | 51.961 | 170.1578 | -9 | 37.5 | 4 | 31.5 | 208.6448 | 950.1287 | 56.8316 | 4.5538 | 0.8836 | 109.9708 | 89.3467 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7312 | 42.9142 | 73.3866
CID=316221072 | -9 | 40 | 0 | 4 | 34 | 6.8 | 1.7455 | 148.4312 | 10.2212 | 247.5407 | 430.3916 | 396.6938 | 34193.896 | 1.1568 | 0.026596 | 3.0457 | 56.6483 | 172.5365 | -9 | 40 | 4 | 34 | 208.6448 | 1016.593 | 59.9805 | 4.8724 | 0.89024 | 109.4 | 96.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.0108 | 74.0486
CID=-1270065845 | -9 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7455 | 148.4312 | 10.2212 | 251.2145 | 431.833 | 396.6938 | 35322.8077 | 1.3114 | 0.031286 | 2.8443 | 67.0742 | 190.7792 | -9 | 42.5 | 4 | 36.5 | 208.6448 | 1086.4865 | 63.0779 | 5.2074 | 0.90099 | 110 | 113.1069 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.1264 | 74.5178
CID=1082384174 | -9 | 45 | 0 | 4 | 39 | 7.8 | 1.7455 | 148.4312 | 10.2212 | 254.9187 | 433.2489 | 396.6938 | 36133.4385 | 1.4214 | 0.035054 | 2.704 | 74.5276 | 201.5194 | -9 | 45 | 4 | 39 | 208.6448 | 1159.9242 | 65.3918 | 5.5593 | 0.90621 | 110 | 124.9528 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7374 | 64.4822 | 74.5276
CID=981627625 | -9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7455 | 148.4312 | 10.2212 | 258.655 | 434.6398 | 396.6938 | 36119.6991 | 1.3082 | 0.034478 | 2.5514 | 70.7774 | 180.5813 | -9 | 47.5 | 4 | 41.5 | 208.6448 | 1237.0237 | 67.9309 | 5.9289 | 0.90379 | 109.5196 | 118.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.7723 | 70.7774
CID=-604659292 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2104021087 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-449942030 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-550698579 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2003263513 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1902506964 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=316220047 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1270066870 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1082383149 | -9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-124295335 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1744316584 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1246688797 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1334383842 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1656621539 | -6 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-507384057 | -6 | 7.5 | 0 | 4 | 1.5 | 0.3 | 1.7436 | 148.523 | 11.416 | 202.0183 | 408.6791 | 398.5385 | 19574.35 | 0.4764 | 0.0068262 | 10.9571 | 8.5445 | 93.6227 | -6 | 7.5 | 4 | 1.5 | 234.2779 | 381.0767 | 18.9119 | 1.6266 | 0.68454 | 103.9688 | 18.9645 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.453 | 16.4601
CID=796577858 | -6 | 10 | 0 | 4 | 4 | 0.8 | 1.7436 | 148.523 | 11.416 | 205.396 | 410.4654 | 398.5385 | 20973.4122 | 0.52666 | 0.0074324 | 9.5989 | 10.5971 | 101.7208 | -6 | 10 | 4 | 4 | 234.2779 | 414.6075 | 22.1817 | 1.7697 | 0.70443 | 109.8301 | 22.8562 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1699 | 7.6696 | 20.8178
CID=-1629777519 | -6 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7436 | 148.523 | 11.416 | 208.7918 | 412.2236 | 398.5385 | 22271.1088 | 0.57681 | 0.0081503 | 8.5359 | 12.8221 | 109.4479 | -6 | 12.5 | 4 | 6.5 | 234.2779 | 450.3422 | 25.3154 | 1.9223 | 0.7241 | 110 | 26.9039 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2176 | 25.6674
CID=-325815604 | -6 | 15 | 0 | 4 | 9 | 1.8 | 1.7436 | 148.523 | 11.416 | 212.2062 | 413.9537 | 398.5385 | 23322.3457 | 0.60159 | 0.0088027 | 7.6627 | 14.6287 | 112.0959 | -6 | 15 | 4 | 9 | 234.2779 | 488.3739 | 28.3243 | 2.0846 | 0.73874 | 108.1186 | 30.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7035 | 10.7286 | 31.091
CID=-1428264421 | -6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7436 | 148.523 | 11.416 | 215.6398 | 415.6561 | 398.5385 | 24647.725 | 0.67679 | 0.0099009 | 6.9411 | 17.8335 | 123.7844 | -6 | 17.5 | 4 | 11.5 | 234.2779 | 528.7968 | 31.3909 | 2.2571 | 0.76208 | 110 | 35.5545 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.814 | 35.6449
CID=-124302506 | -6 | 20 | 0 | 4 | 14 | 2.8 | 1.7436 | 148.523 | 11.416 | 219.0933 | 417.3308 | 398.5385 | 25717.8911 | 0.72663 | 0.010933 | 6.3233 | 20.6205 | 130.3896 | -6 | 20 | 4 | 14 | 234.2779 | 571.7069 | 34.3682 | 2.4403 | 0.77991 | 110 | 40.1706 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1569 | 42.1821
CID=1744309413 | -6 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7436 | 148.523 | 11.416 | 222.5675 | 418.9782 | 398.5385 | 26912.4836 | 0.80151 | 0.012346 | 5.7654 | 24.4636 | 141.0429 | -6 | 22.5 | 4 | 16.5 | 234.2779 | 617.2019 | 37.481 | 2.6345 | 0.80125 | 110 | 46.3882 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.5255 | 49.1571
CID=-1246695968 | -6 | 25 | 0 | 4 | 19 | 3.8 | 1.7436 | 148.523 | 11.416 | 226.0633 | 420.5983 | 398.5385 | 28004.9091 | 0.87625 | 0.01391 | 5.2904 | 28.5671 | 151.131 | -6 | 25 | 4 | 19 | 234.2779 | 665.3809 | 40.5119 | 2.8401 | 0.82046 | 110 | 52.901 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3432 | 56.7809
CID=1334376671 | -6 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7436 | 148.523 | 11.416 | 229.5813 | 422.1916 | 398.5385 | 29011.5445 | 0.95083 | 0.015626 | 4.8816 | 32.9096 | 160.6497 | -6 | 27.5 | 4 | 21.5 | 234.2779 | 716.3449 | 43.4636 | 3.0577 | 0.83741 | 110 | 59.7087 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3062 | 62.1448
CID=-1656628710 | -6 | 30 | 0 | 4 | 24 | 4.8 | 1.7436 | 148.523 | 11.416 | 233.1226 | 423.758 | 398.5385 | 29702.6432 | 0.975 | 0.016893 | 4.5201 | 35.6807 | 161.28 | -6 | 30 | 4 | 24 | 234.2779 | 770.1963 | 46.3361 | 3.2875 | 0.84669 | 110 | 64.027 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4924 | 69.9107
CID=-507383032 | -6 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7436 | 148.523 | 11.416 | 236.688 | 425.298 | 398.5385 | 30537.5867 | 1.0241 | 0.018654 | 4.1741 | 39.7099 | 165.7515 | -6 | 32.5 | 4 | 26.5 | 234.2779 | 827.0396 | 49.4097 | 3.5302 | 0.85835 | 110 | 70.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2611 | 77.2504
CID=1902513110 | -6 | 35 | 0 | 4 | 29 | 5.8 | 1.7436 | 148.523 | 11.416 | 240.2788 | 426.8116 | 398.5385 | 31423.5637 | 1.0981 | 0.020922 | 3.8674 | 44.9372 | 173.7902 | -6 | 35 | 4 | 29 | 234.2779 | 886.981 | 52.4695 | 3.786 | 0.87076 | 110 | 78.4082 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.2819 | 82.4485
CID=316226193 | -6 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7436 | 148.523 | 11.416 | 243.8959 | 428.2991 | 398.5385 | 32187.7296 | 1.1469 | 0.02303 | 3.5895 | 49.4098 | 177.3583 | -6 | 37.5 | 4 | 31.5 | 234.2779 | 950.1287 | 55.5171 | 4.0556 | 0.87938 | 110 | 85.3676 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.1102 | 82.9524
CID=-1270060724 | -6 | 40 | 0 | 4 | 34 | 6.8 | 1.7436 | 148.523 | 11.416 | 247.5407 | 429.7609 | 398.5385 | 32891.1846 | 1.1955 | 0.025274 | 3.3453 | 53.9619 | 180.52 | -6 | 40 | 4 | 34 | 234.2779 | 1016.593 | 58.4728 | 4.3393 | 0.8866 | 110 | 92.4732 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.5036 | 82.5148
CID=1082389295 | -6 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7436 | 148.523 | 11.416 | 251.2145 | 431.197 | 398.5385 | 33627.8547 | 1.2439 | 0.027747 | 3.1162 | 58.8072 | 183.2573 | -6 | 42.5 | 4 | 36.5 | 234.2779 | 1086.4865 | 61.4999 | 4.6376 | 0.89288 | 109.795 | 100.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.8837 | 81.3364
CID=981632746 | -6 | 45 | 0 | 4 | 39 | 7.8 | 1.7436 | 148.523 | 11.416 | 254.9187 | 432.6077 | 398.5385 | 34423.8713 | 1.317 | 0.030944 | 2.9028 | 65.1617 | 189.1485 | -6 | 45 | 4 | 39 | 234.2779 | 1159.9242 | 64.5909 | 4.9511 | 0.89936 | 109.4664 | 110.0809 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.269 | 82.5395
CID=-604654171 | -6 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7436 | 148.523 | 11.416 | 258.655 | 433.9933 | 398.5385 | 35623.0425 | 1.5145 | 0.036957 | 2.7129 | 78.0887 | 211.8481 | -6 | 47.5 | 4 | 41.5 | 234.2779 | 1237.0237 | 67.637 | 5.2802 | 0.90816 | 110 | 130.641 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.1967 | 82.9402
CID=2104026208 | -6 | 50 | 0 | 4 | 44 | 8.8 | 1.7436 | 148.523 | 11.416 | 262.425 | 435.3541 | 398.5385 | 36114.0211 | 1.5626 | 0.039729 | 2.5834 | 82.3271 | 212.6847 | -6 | 50 | 4 | 44 | 234.2779 | 1317.9055 | 69.8365 | 5.6254 | 0.91014 | 110 | 137.4333 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7151 | 73.7545 | 82.3271
CID=-449936909 | -6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7436 | 148.523 | 11.416 | 266.2308 | 436.6902 | 398.5385 | 36189.9086 | 1.461 | 0.039595 | 2.437 | 79.3179 | 193.2958 | -6 | 52.5 | 4 | 46.5 | 234.2779 | 1402.6932 | 72.3832 | 5.9873 | 0.90877 | 109.5619 | 132.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 81.6054 | 79.3179
CID=-550693458 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2003268638 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1902512089 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=316225172 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1270061745 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1082388274 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=981631725 | -6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1744311459 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1246693922 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1334378717 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1656626664 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-507380986 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=796580929 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1629774448 | -3 | 10 | 0 | 4 | 4 | 0.8 | 1.7418 | 148.5658 | 12.7186 | 205.396 | 409.9411 | 400.3675 | 19544.2097 | 0.53152 | 0.0069993 | 11.4183 | 9.076 | 103.6318 | -3 | 10 | 4 | 4 | 262.283 | 414.6075 | 21.0972 | 1.5808 | 0.68986 | 99.6706 | 19.9888 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.2395 | 17.0303
CID=-325812533 | -3 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7418 | 148.5658 | 12.7186 | 208.7918 | 411.6941 | 400.3675 | 20431.365 | 0.55934 | 0.0075209 | 10.008 | 10.7072 | 107.1569 | -3 | 12.5 | 4 | 6.5 | 262.283 | 450.3422 | 24.1413 | 1.717 | 0.70545 | 108.6831 | 23.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2923 | 7.8059 | 21.4254
CID=-1428261350 | -3 | 15 | 0 | 4 | 9 | 1.8 | 1.7418 | 148.5658 | 12.7186 | 212.2062 | 413.4192 | 400.3675 | 21745.3832 | 0.61525 | 0.0083003 | 8.8232 | 13.1206 | 115.7666 | -3 | 15 | 4 | 9 | 262.283 | 488.3739 | 27.3608 | 1.862 | 0.7266 | 110 | 27.4356 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5793 | 26.4523
CID=-124299435 | -3 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7418 | 148.5658 | 12.7186 | 215.6398 | 415.1165 | 400.3675 | 22800.6697 | 0.6429 | 0.008997 | 7.895 | 15.0426 | 118.7612 | -3 | 17.5 | 4 | 11.5 | 262.283 | 528.7968 | 30.3694 | 2.0161 | 0.74194 | 107.1772 | 30.8041 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.3834 | 32.0983
CID=1744312484 | -3 | 20 | 0 | 4 | 14 | 2.8 | 1.7418 | 148.5658 | 12.7186 | 219.0933 | 416.7863 | 400.3675 | 24162.9838 | 0.72676 | 0.01017 | 7.1451 | 18.4381 | 131.7421 | -3 | 20 | 4 | 14 | 262.283 | 571.7069 | 33.3873 | 2.1797 | 0.76613 | 110 | 36.5653 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.1276 | 36.8384
CID=-1246692897 | -3 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7418 | 148.5658 | 12.7186 | 222.5675 | 418.4287 | 400.3675 | 25384.4623 | 0.81045 | 0.0115 | 6.5101 | 22.1348 | 144.0989 | -3 | 22.5 | 4 | 16.5 | 262.283 | 617.2019 | 36.3389 | 2.3532 | 0.78874 | 110 | 42.6378 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3536 | 43.5534
CID=1334379742 | -3 | 25 | 0 | 4 | 19 | 3.8 | 1.7418 | 148.5658 | 12.7186 | 226.0633 | 420.0439 | 400.3675 | 26280.8628 | 0.83778 | 0.012517 | 5.9288 | 24.6306 | 146.0289 | -3 | 25 | 4 | 19 | 262.283 | 665.3809 | 39.3339 | 2.5369 | 0.8021 | 110 | 46.6554 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2962 | 51.0495
CID=-1656625639 | -3 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7418 | 148.5658 | 12.7186 | 229.5813 | 421.6322 | 400.3675 | 27421.7685 | 0.92114 | 0.014187 | 5.4255 | 28.9963 | 157.3183 | -3 | 27.5 | 4 | 21.5 | 262.283 | 716.3449 | 42.3853 | 2.7312 | 0.82228 | 110 | 53.577 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.9887 | 58.877
CID=-507388157 | -3 | 30 | 0 | 4 | 24 | 4.8 | 1.7418 | 148.5658 | 12.7186 | 233.1226 | 423.1938 | 400.3675 | 28432.5898 | 1.0044 | 0.016008 | 5.0028 | 33.5758 | 167.9725 | -3 | 30 | 4 | 24 | 262.283 | 770.1963 | 45.3059 | 2.9365 | 0.83975 | 110 | 60.7483 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0589 | 65.4577
CID=796573758 | -3 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7418 | 148.5658 | 12.7186 | 236.688 | 424.7289 | 400.3675 | 29258.5241 | 1.0594 | 0.017677 | 4.6292 | 37.4572 | 173.3968 | -3 | 32.5 | 4 | 26.5 | 262.283 | 827.0396 | 48.1749 | 3.1532 | 0.85208 | 110 | 66.7897 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.3282 | 72.9534
CID=316231318 | -3 | 35 | 0 | 4 | 29 | 5.8 | 1.7418 | 148.5658 | 12.7186 | 240.2788 | 426.2376 | 400.3675 | 30191.9762 | 1.1422 | 0.019913 | 4.2789 | 42.7326 | 182.8471 | -3 | 35 | 4 | 29 | 262.283 | 886.981 | 51.1785 | 3.3818 | 0.86587 | 110 | 74.9832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.2318 | 81.2868
CID=-1270055599 | -3 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7418 | 148.5658 | 12.7186 | 243.8959 | 427.7203 | 400.3675 | 31076.4211 | 1.2247 | 0.022362 | 3.9681 | 48.2942 | 191.6374 | -3 | 37.5 | 4 | 31.5 | 262.283 | 950.1287 | 54.1442 | 3.6225 | 0.87738 | 110 | 83.6301 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.4207 | 89.2568
CID=1082394420 | -3 | 40 | 0 | 4 | 34 | 6.8 | 1.7418 | 148.5658 | 12.7186 | 247.5407 | 429.1772 | 400.3675 | 31732.5779 | 1.2512 | 0.024288 | 3.6702 | 52.098 | 191.2106 | -3 | 40 | 4 | 34 | 262.283 | 1016.593 | 57.2385 | 3.8759 | 0.88381 | 110 | 89.5605 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.004 | 91.6597
CID=981637871 | -3 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7418 | 148.5658 | 12.7186 | 251.2145 | 430.6085 | 400.3675 | 32371.9045 | 1.2775 | 0.026285 | 3.4135 | 55.8207 | 190.544 | -3 | 42.5 | 4 | 36.5 | 262.283 | 1086.4865 | 60.2033 | 4.1424 | 0.88916 | 109.7471 | 95.3826 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5288 | 44.8066 | 92.0158
CID=-604649046 | -3 | 45 | 0 | 4 | 39 | 7.8 | 1.7418 | 148.5658 | 12.7186 | 254.9187 | 432.0144 | 400.3675 | 33131.6897 | 1.3595 | 0.029357 | 3.1864 | 62.0556 | 197.7324 | -3 | 45 | 4 | 39 | 262.283 | 1159.9242 | 63.1135 | 4.4224 | 0.89642 | 110 | 105.1785 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.0122 | 91.8833
CID=2104031333 | -3 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7418 | 148.5658 | 12.7186 | 258.655 | 433.3951 | 400.3675 | 33861.1215 | 1.4132 | 0.032307 | 2.9646 | 67.5538 | 200.2682 | -3 | 47.5 | 4 | 41.5 | 262.283 | 1237.0237 | 66.1788 | 4.7164 | 0.90138 | 109.8363 | 113.8667 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0927 | 57.2677 | 91.0918
CID=-449931784 | -3 | 50 | 0 | 4 | 44 | 8.8 | 1.7418 | 148.5658 | 12.7186 | 262.425 | 434.7511 | 400.3675 | 34714.1277 | 1.5223 | 0.036614 | 2.7641 | 75.9691 | 209.9852 | -3 | 50 | 4 | 44 | 262.283 | 1317.9055 | 69.2239 | 5.0247 | 0.90703 | 109.4659 | 127.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4507 | 64.1843 | 92.3763
CID=-550688333 | -3 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7418 | 148.5658 | 12.7186 | 266.2308 | 436.0824 | 400.3675 | 35692.1155 | 1.6865 | 0.042441 | 2.5881 | 87.4077 | 226.2214 | -3 | 52.5 | 4 | 46.5 | 262.283 | 1402.6932 | 72.1393 | 5.348 | 0.91207 | 110 | 145.6051 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.1709 | 92.7477
CID=2003273759 | -3 | 55 | 0 | 4 | 49 | 9.8 | 1.7418 | 148.5658 | 12.7186 | 270.0745 | 437.3893 | 400.3675 | 36170.0882 | 1.7399 | 0.045685 | 2.4634 | 92.0281 | 226.702 | -3 | 55 | 4 | 49 | 262.283 | 1491.5141 | 74.3465 | 5.6867 | 0.9135 | 110 | 153.0621 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7082 | 83.791 | 92.0281
CID=1902517210 | -3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7418 | 148.5658 | 12.7186 | 273.9586 | 438.6721 | 400.3675 | 36239.4688 | 1.6267 | 0.045541 | 2.3224 | 88.544 | 205.6311 | -3 | 57.5 | 4 | 51.5 | 262.283 | 1584.4992 | 76.8958 | 6.0412 | 0.91245 | 109.5992 | 147.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.1977 | 88.544
CID=316230293 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1270056624 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1082393395 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=981636846 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-604650071 | -3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1246699043 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1334373596 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1656631785 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2104896656 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-518609739 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503027174 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=603783723 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269190276 | 0 | 12.5 | 0 | 4 | 6.5 | 1.3 | 1.7401 | 148.5582 | 14.1363 | 208.7918 | 411.2041 | 402.1796 | 19542.876 | 0.55997 | 0.007046 | 11.9925 | 9.0299 | 108.2913 | 0 | 12.5 | 4 | 6.5 | 292.8032 | 450.3422 | 23.062 | 1.538 | 0.68941 | 82.8912 | 19.9005 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.6527 | 15.5267
CID=-1439490103 | 0 | 15 | 0 | 4 | 9 | 1.8 | 1.7401 | 148.5582 | 14.1363 | 212.2062 | 412.9246 | 402.1796 | 19888.8021 | 0.59091 | 0.0076092 | 10.3898 | 10.8045 | 112.2567 | 0 | 15 | 4 | 9 | 292.8032 | 488.3739 | 26.2132 | 1.6679 | 0.70635 | 106.8987 | 23.2403 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.8476 | 21.9668
CID=-417853190 | 0 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7401 | 148.5582 | 14.1363 | 215.6398 | 414.6172 | 402.1796 | 21449.3608 | 0.68443 | 0.0085932 | 9.1743 | 13.9164 | 127.6727 | 0 | 17.5 | 4 | 11.5 | 292.8032 | 528.7968 | 29.3828 | 1.806 | 0.73311 | 110 | 28.8413 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6303 | 27.2198
CID=-317096641 | 0 | 20 | 0 | 4 | 14 | 2.8 | 1.7401 | 148.5582 | 14.1363 | 219.0933 | 416.2824 | 402.1796 | 22480.2069 | 0.71516 | 0.0093638 | 8.1674 | 16.0314 | 130.9353 | 0 | 20 | 4 | 14 | 292.8032 | 571.7069 | 32.4116 | 1.9525 | 0.74935 | 110 | 32.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4976 | 33.1226
CID=-263135928 | 0 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7401 | 148.5582 | 14.1363 | 222.5675 | 417.9202 | 402.1796 | 23492.6255 | 0.74583 | 0.010194 | 7.3575 | 18.2072 | 133.9595 | 0 | 22.5 | 4 | 16.5 | 292.8032 | 617.2019 | 35.3509 | 2.1079 | 0.76459 | 108.6612 | 36.1799 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9999 | 13.7099 | 39.6483
CID=1323150989 | 0 | 25 | 0 | 4 | 19 | 3.8 | 1.7401 | 148.5582 | 14.1363 | 226.0633 | 419.5308 | 402.1796 | 24756.2791 | 0.83892 | 0.011604 | 6.68 | 22.118 | 147.7473 | 0 | 25 | 4 | 19 | 292.8032 | 665.3809 | 38.3388 | 2.2725 | 0.78865 | 110 | 42.6105 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0491 | 44.9885
CID=-2104895631 | 0 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7401 | 148.5582 | 14.1363 | 229.5813 | 421.1145 | 402.1796 | 25790.0586 | 0.90061 | 0.012919 | 6.0948 | 25.504 | 155.443 | 0 | 27.5 | 4 | 21.5 | 292.8032 | 716.3449 | 41.2676 | 2.4465 | 0.80645 | 110 | 48.0495 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.7183 | 52.7648
CID=-518608714 | 0 | 30 | 0 | 4 | 24 | 4.8 | 1.7401 | 148.5582 | 14.1363 | 233.1226 | 422.6716 | 402.1796 | 26937.8939 | 0.99331 | 0.014714 | 5.5678 | 30.1601 | 167.9267 | 0 | 30 | 4 | 24 | 292.8032 | 770.1963 | 44.3032 | 2.6304 | 0.82705 | 110 | 55.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.6284 | 60.943
CID=1235810802 | 0 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7401 | 148.5582 | 14.1363 | 236.688 | 424.2021 | 402.1796 | 27993.6501 | 1.0858 | 0.016702 | 5.1145 | 35.1345 | 179.6954 | 0 | 32.5 | 4 | 26.5 | 292.8032 | 827.0396 | 47.2801 | 2.8246 | 0.84495 | 110 | 63.177 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9262 | 69.8742
CID=-68151113 | 0 | 35 | 0 | 4 | 29 | 5.8 | 1.7401 | 148.5582 | 14.1363 | 240.2788 | 425.7063 | 402.1796 | 28844.0754 | 1.147 | 0.018513 | 4.7231 | 39.3182 | 185.7034 | 0 | 35 | 4 | 29 | 292.8032 | 886.981 | 50.1637 | 3.0293 | 0.85731 | 110 | 69.6808 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2143 | 76.0029
CID=1437323900 | 0 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7401 | 148.5582 | 14.1363 | 243.8959 | 427.1845 | 402.1796 | 29618.5837 | 1.2081 | 0.02046 | 4.3821 | 43.6359 | 191.2183 | 0 | 37.5 | 4 | 31.5 | 292.8032 | 950.1287 | 52.9803 | 3.2449 | 0.86793 | 110 | 76.3863 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0433 | 84.9985
CID=133361985 | 0 | 40 | 0 | 4 | 34 | 6.8 | 1.7401 | 148.5582 | 14.1363 | 247.5407 | 428.6369 | 402.1796 | 30423.5814 | 1.2689 | 0.022684 | 4.0497 | 48.452 | 196.2138 | 0 | 40 | 4 | 34 | 292.8032 | 1016.593 | 55.9938 | 3.4719 | 0.87767 | 110 | 83.8758 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5584 | 93.5253
CID=314930438 | 0 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7401 | 148.5582 | 14.1363 | 251.2145 | 430.0637 | 402.1796 | 31269.9982 | 1.3605 | 0.025529 | 3.7594 | 54.6338 | 205.3894 | 0 | 42.5 | 4 | 36.5 | 292.8032 | 1086.4865 | 58.9432 | 3.7106 | 0.88755 | 110 | 93.5243 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6283 | 101.9065
CID=-989031477 | 0 | 45 | 0 | 4 | 39 | 7.8 | 1.7401 | 148.5582 | 14.1363 | 254.9187 | 431.4651 | 402.1796 | 32007.6369 | 1.4208 | 0.028234 | 3.4839 | 60.0558 | 209.2291 | 0 | 45 | 4 | 39 | 292.8032 | 1159.9242 | 61.996 | 3.9614 | 0.8943 | 110 | 102.03 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.0942 | 101.9148
CID=-95002304 | 0 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7401 | 148.5582 | 14.1363 | 258.655 | 432.8414 | 402.1796 | 32609.2619 | 1.45 | 0.030572 | 3.2437 | 64.1575 | 208.1063 | 0 | 47.5 | 4 | 41.5 | 292.8032 | 1237.0237 | 64.9266 | 4.2248 | 0.89845 | 109.5338 | 108.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 7.331 | 51.0502 | 101.2467
CID=-1398964219 | 0 | 50 | 0 | 4 | 44 | 8.8 | 1.7401 | 148.5582 | 14.1363 | 262.425 | 434.1928 | 402.1796 | 33281.6694 | 1.5099 | 0.033608 | 3.029 | 69.6667 | 211.0202 | 0 | 50 | 4 | 44 | 292.8032 | 1317.9055 | 67.804 | 4.501 | 0.903 | 109.6833 | 117.2179 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6396 | 57.491 | 102.1367
CID=-1936764053 | 0 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7401 | 148.5582 | 14.1363 | 266.2308 | 435.5196 | 402.1796 | 33979.2293 | 1.5695 | 0.037052 | 2.8175 | 75.7299 | 213.3705 | 0 | 52.5 | 4 | 46.5 | 292.8032 | 1402.6932 | 70.8627 | 4.7906 | 0.9069 | 109.4797 | 126.8713 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65.2952 | 101.6651
CID=1054241328 | 0 | 55 | 0 | 4 | 49 | 9.8 | 1.7401 | 148.5582 | 14.1363 | 270.0745 | 436.822 | 402.1796 | 34805.5293 | 1.6905 | 0.042079 | 2.6267 | 85.02 | 223.3195 | 0 | 55 | 4 | 49 | 292.8032 | 1491.5141 | 73.8868 | 5.0939 | 0.91121 | 109.3031 | 141.7608 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9999 | 72.7779 | 102.0387
CID=1235809781 | 0 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7401 | 148.5582 | 14.1363 | 273.9586 | 438.1003 | 402.1796 | 35755.2485 | 1.8727 | 0.048859 | 2.4606 | 97.5865 | 240.1187 | 0 | 57.5 | 4 | 51.5 | 292.8032 | 1584.4992 | 76.7508 | 5.4115 | 0.91488 | 110 | 162.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82.0777 | 102.54
CID=-68152134 | 0 | 60 | 0 | 4 | 54 | 10.8 | 1.7401 | 148.5582 | 14.1363 | 277.8855 | 439.3549 | 402.1796 | 36125.0627 | 1.9012 | 0.051894 | 2.3423 | 100.8854 | 236.3028 | 0 | 60 | 4 | 54 | 292.8032 | 1681.7842 | 78.9273 | 5.7437 | 0.91556 | 110 | 167.4163 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.1756 | 100.8854
CID=1437322879 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=133360964 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=314929417 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-989032498 | 0 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263133882 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1323153035 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2104893585 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-518606668 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503030245 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=603786794 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269193347 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1439487032 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-417850119 | 3 | 15 | 0 | 4 | 9 | 1.8 | 1.7385 | 148.4988 | 15.6766 | 212.2062 | 412.4664 | 403.9734 | 19534.7636 | 0.58654 | 0.0070838 | 12.5877 | 8.9357 | 112.4798 | 3 | 15 | 4 | 9 | 325.9849 | 488.3739 | 25.077 | 1.4981 | 0.68847 | 69.7562 | 19.7197 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.4251 | 11.1654
CID=-317093570 | 3 | 17.5 | 0 | 4 | 11.5 | 2.3 | 1.7385 | 148.4988 | 15.6766 | 215.6398 | 414.1547 | 403.9734 | 19590.5247 | 0.65564 | 0.0078286 | 10.8393 | 11.3918 | 123.4786 | 3 | 17.5 | 4 | 11.5 | 325.9849 | 528.7968 | 28.3138 | 1.6222 | 0.71168 | 104.1701 | 24.3201 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.626 | 22.4048
CID=-263132857 | 3 | 20 | 0 | 4 | 14 | 2.8 | 1.7385 | 148.4988 | 15.6766 | 219.0933 | 415.8156 | 403.9734 | 20709.1554 | 0.68985 | 0.0085396 | 9.4821 | 13.4505 | 127.5387 | 3 | 20 | 4 | 14 | 325.9849 | 571.7069 | 31.4142 | 1.7538 | 0.72932 | 108.3535 | 28.0203 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.0707 | 27.9674
CID=1323154060 | 3 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7385 | 148.4988 | 15.6766 | 222.5675 | 417.4491 | 403.9734 | 21947.4202 | 0.75868 | 0.0095417 | 8.4218 | 16.3421 | 137.6293 | 3 | 22.5 | 4 | 16.5 | 325.9849 | 617.2019 | 34.4874 | 1.8933 | 0.75162 | 108.8908 | 33.0344 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7729 | 12.1238 | 34.0823
CID=-2104900756 | 3 | 25 | 0 | 4 | 19 | 3.8 | 1.7385 | 148.4988 | 15.6766 | 226.0633 | 419.0555 | 403.9734 | 23155.7454 | 0.8274 | 0.010664 | 7.5754 | 19.4316 | 147.2025 | 3 | 25 | 4 | 19 | 325.9849 | 665.3809 | 37.4468 | 2.0411 | 0.77257 | 109.6062 | 38.2146 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9846 | 14.0916 | 40.8543
CID=-518613839 | 3 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7385 | 148.4988 | 15.6766 | 229.5813 | 420.635 | 403.9734 | 24268.3634 | 0.89598 | 0.011919 | 6.8666 | 22.7555 | 156.252 | 3 | 27.5 | 4 | 21.5 | 325.9849 | 716.3449 | 40.3629 | 2.1975 | 0.7922 | 110 | 43.6422 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.1927 | 46.3828
CID=1235815927 | 3 | 30 | 0 | 4 | 24 | 4.8 | 1.7385 | 148.4988 | 15.6766 | 233.1226 | 422.1878 | 403.9734 | 25289.21 | 0.96443 | 0.013308 | 6.2657 | 26.2978 | 164.774 | 3 | 30 | 4 | 24 | 325.9849 | 770.1963 | 43.2339 | 2.3627 | 0.81026 | 110 | 49.312 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.1571 | 54.3477
CID=-68145988 | 3 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7385 | 148.4988 | 15.6766 | 236.688 | 423.7141 | 403.9734 | 26305.9477 | 1.0327 | 0.014891 | 5.7154 | 30.2259 | 172.7534 | 3 | 32.5 | 4 | 26.5 | 325.9849 | 827.0396 | 46.2195 | 2.537 | 0.82731 | 110 | 55.5092 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.4325 | 63.1245
CID=1437329025 | 3 | 35 | 0 | 4 | 29 | 5.8 | 1.7385 | 148.4988 | 15.6766 | 240.2788 | 425.2142 | 403.9734 | 27407.3136 | 1.1353 | 0.017004 | 5.2373 | 35.4856 | 185.8477 | 3 | 35 | 4 | 29 | 325.9849 | 886.981 | 49.2132 | 2.7209 | 0.84607 | 110 | 63.7234 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6165 | 72.2476
CID=133367110 | 3 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7385 | 148.4988 | 15.6766 | 243.8959 | 426.6882 | 403.9734 | 28382.7698 | 1.2378 | 0.019304 | 4.8348 | 40.9822 | 198.1421 | 3 | 37.5 | 4 | 31.5 | 325.9849 | 950.1287 | 52.0827 | 2.9146 | 0.86164 | 110 | 72.2649 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.0856 | 80.3364
CID=314935563 | 3 | 40 | 0 | 4 | 34 | 6.8 | 1.7385 | 148.4988 | 15.6766 | 247.5407 | 428.1364 | 403.9734 | 29184.4925 | 1.3055 | 0.021418 | 4.4748 | 45.639 | 204.2251 | 3 | 40 | 4 | 34 | 325.9849 | 1016.593 | 54.9299 | 3.1185 | 0.87223 | 110 | 79.4991 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.953 | 88.4142
CID=-989026352 | 3 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7385 | 148.4988 | 15.6766 | 251.2145 | 429.559 | 403.9734 | 30075.7503 | 1.4075 | 0.02422 | 4.144 | 51.8836 | 215.0034 | 3 | 42.5 | 4 | 36.5 | 325.9849 | 1086.4865 | 57.8445 | 3.3329 | 0.88348 | 110 | 89.2259 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.6354 | 98.2926
CID=-94997179 | 3 | 45 | 0 | 4 | 39 | 7.8 | 1.7385 | 148.4988 | 15.6766 | 254.9187 | 430.9562 | 403.9734 | 30622.6812 | 1.4058 | 0.025862 | 3.8343 | 54.6499 | 209.5453 | 3 | 45 | 4 | 39 | 325.9849 | 1159.9242 | 60.8059 | 3.5582 | 0.88757 | 110 | 93.5494 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9298 | 107.3472
CID=-1398959094 | 3 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7385 | 148.4988 | 15.6766 | 258.655 | 432.3283 | 403.9734 | 31453.3479 | 1.5073 | 0.029194 | 3.5577 | 61.5653 | 219.0317 | 3 | 47.5 | 4 | 41.5 | 325.9849 | 1237.0237 | 63.7835 | 3.7947 | 0.89591 | 110 | 104.406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.1667 | 112.8128
CID=-1936758932 | 3 | 50 | 0 | 4 | 44 | 8.8 | 1.7385 | 148.4988 | 15.6766 | 262.425 | 433.6755 | 403.9734 | 32073.3181 | 1.5397 | 0.031702 | 3.3055 | 65.9309 | 217.9371 | 3 | 50 | 4 | 44 | 325.9849 | 1317.9055 | 66.7401 | 4.0428 | 0.90004 | 109.8616 | 111.2974 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7304 | 53.1496 | 113.4849
CID=1054246449 | 3 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7385 | 148.4988 | 15.6766 | 266.2308 | 434.9982 | 403.9734 | 32814.2885 | 1.6405 | 0.035591 | 3.0816 | 73.3285 | 225.9712 | 3 | 52.5 | 4 | 46.5 | 325.9849 | 1402.6932 | 69.6462 | 4.3029 | 0.90548 | 110 | 123.0415 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.3888 | 112.6148
CID=1235814902 | 3 | 55 | 0 | 4 | 49 | 9.8 | 1.7385 | 148.4988 | 15.6766 | 270.0745 | 436.2964 | 403.9734 | 33422.4056 | 1.6792 | 0.038674 | 2.8736 | 78.2448 | 224.8421 | 3 | 55 | 4 | 49 | 325.9849 | 1491.5141 | 72.5553 | 4.5754 | 0.90824 | 109.5524 | 130.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3048 | 65.8924 | 112.3073
CID=-68147013 | 3 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7385 | 148.4988 | 15.6766 | 273.9586 | 437.5705 | 403.9734 | 34072.8906 | 1.7383 | 0.042549 | 2.6733 | 84.5426 | 226.0091 | 3 | 57.5 | 4 | 51.5 | 325.9849 | 1584.4992 | 75.584 | 4.8607 | 0.91103 | 109.2 | 140.993 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.9935 | 113.0467
CID=1437328000 | 3 | 60 | 0 | 4 | 54 | 10.8 | 1.7385 | 148.4988 | 15.6766 | 277.8855 | 438.8208 | 403.9734 | 35045.5941 | 1.9405 | 0.049926 | 2.4934 | 98.1274 | 244.6698 | 3 | 60 | 4 | 54 | 325.9849 | 1681.7842 | 78.5728 | 5.1591 | 0.915 | 109.9925 | 162.9389 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0622 | 82.0539 | 113.39
CID=133366085 | 3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7385 | 148.4988 | 15.6766 | 281.8586 | 440.0476 | 403.9734 | 35981.6923 | 2.142 | 0.057939 | 2.3352 | 112.0107 | 261.5668 | 3 | 62.5 | 4 | 56.5 | 325.9849 | 1783.5096 | 81.4008 | 5.4711 | 0.91725 | 110 | 185.5363 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 92.802 | 113.8644
CID=314934538 | 3 | 65 | 0 | 4 | 59 | 11.8 | 1.7385 | 148.4988 | 15.6766 | 285.881 | 441.2512 | 403.9734 | 36149.4461 | 2.1051 | 0.059895 | 2.2202 | 111.9723 | 248.5962 | 3 | 65 | 4 | 59 | 325.9849 | 1889.8218 | 83.5874 | 5.7973 | 0.91724 | 110 | 185.4735 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 105.0584 | 111.9723
CID=-989027377 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-94998204 | 3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1323147914 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2104898710 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-518611793 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503025120 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=603781669 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269188222 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1439492157 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-417855244 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-317098695 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263137982 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1323148935 | 6 | 20 | 0 | 4 | 14 | 2.8 | 1.7371 | 148.3861 | 17.3476 | 219.0933 | 415.3827 | 405.7474 | 19520.5815 | 0.72556 | 0.0080755 | 11.238 | 12.0509 | 135.4282 | 6 | 20 | 4 | 14 | 361.9781 | 571.7069 | 30.5367 | 1.5794 | 0.7175 | 101.0561 | 25.5186 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.5417 | 22.8585
CID=-2104897685 | 6 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7371 | 148.3861 | 17.3476 | 222.5675 | 417.0123 | 405.7474 | 20389.2818 | 0.76342 | 0.0088256 | 9.8627 | 14.179 | 139.843 | 6 | 22.5 | 4 | 16.5 | 361.9781 | 617.2019 | 33.4926 | 1.7051 | 0.7352 | 108.839 | 29.3017 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9025 | 10.1644 | 28.6739
CID=-518610768 | 6 | 25 | 0 | 4 | 19 | 3.8 | 1.7371 | 148.3861 | 17.3476 | 226.0633 | 418.6147 | 405.7474 | 21646.5149 | 0.83954 | 0.0099318 | 8.6973 | 17.3447 | 150.8516 | 6 | 25 | 4 | 19 | 361.9781 | 665.3809 | 36.6113 | 1.8382 | 0.75872 | 110 | 34.7327 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3537 | 34.9853
CID=1235812856 | 6 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7371 | 148.3861 | 17.3476 | 229.5813 | 420.1903 | 405.7474 | 22638.6033 | 0.87719 | 0.010893 | 7.792 | 19.832 | 154.5309 | 6 | 27.5 | 4 | 21.5 | 361.9781 | 716.3449 | 39.5383 | 1.979 | 0.77508 | 108.4056 | 38.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 8.986 | 14.739 | 42.0253
CID=-68149059 | 6 | 30 | 0 | 4 | 24 | 4.8 | 1.7371 | 148.3861 | 17.3476 | 233.1226 | 421.7392 | 405.7474 | 23778.916 | 0.95308 | 0.012224 | 7.0523 | 23.3294 | 164.5256 | 6 | 30 | 4 | 24 | 361.9781 | 770.1963 | 42.4335 | 2.1277 | 0.79532 | 109.6856 | 44.5676 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5722 | 17.1012 | 49.1455
CID=1437325954 | 6 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7371 | 148.3861 | 17.3476 | 236.688 | 423.2616 | 405.7474 | 24856.467 | 1.0372 | 0.013788 | 6.4146 | 27.3353 | 175.3437 | 6 | 32.5 | 4 | 26.5 | 361.9781 | 827.0396 | 45.3375 | 2.2848 | 0.81505 | 110 | 50.9562 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7427 | 55.9665
CID=133364039 | 6 | 35 | 0 | 4 | 29 | 5.8 | 1.7371 | 148.3861 | 17.3476 | 240.2788 | 424.7577 | 405.7474 | 25964.2714 | 1.1426 | 0.015733 | 5.8635 | 32.2455 | 189.0701 | 6 | 35 | 4 | 29 | 361.9781 | 886.981 | 48.2405 | 2.4504 | 0.83502 | 110 | 58.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.991 | 65.1
CID=314932492 | 6 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7371 | 148.3861 | 17.3476 | 243.8959 | 426.2278 | 405.7474 | 26922.7613 | 1.218 | 0.017632 | 5.3645 | 36.747 | 197.1286 | 6 | 37.5 | 4 | 31.5 | 361.9781 | 950.1287 | 51.1952 | 2.6248 | 0.84998 | 110 | 65.6856 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.3835 | 74.5803
CID=-989029423 | 6 | 40 | 0 | 4 | 34 | 6.8 | 1.7371 | 148.3861 | 17.3476 | 247.5407 | 427.6721 | 405.7474 | 27943.7115 | 1.3313 | 0.020141 | 4.9318 | 42.7059 | 210.6186 | 6 | 40 | 4 | 34 | 361.9781 | 1016.593 | 54.1331 | 2.8084 | 0.8658 | 110 | 74.9417 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2032 | 84.9212
CID=-95000250 | 6 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7371 | 148.3861 | 17.3476 | 251.2145 | 429.0909 | 405.7474 | 28758.9577 | 1.4062 | 0.02241 | 4.5602 | 47.6541 | 217.3107 | 6 | 42.5 | 4 | 36.5 | 361.9781 | 1086.4865 | 56.9689 | 3.0015 | 0.87619 | 110 | 82.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7881 | 91.8398
CID=-1398962165 | 6 | 45 | 0 | 4 | 39 | 7.8 | 1.7371 | 148.3861 | 17.3476 | 254.9187 | 430.4842 | 405.7474 | 29380.7468 | 1.4429 | 0.02434 | 4.2365 | 51.3718 | 217.6345 | 6 | 45 | 4 | 39 | 361.9781 | 1159.9242 | 59.7177 | 3.2044 | 0.88266 | 110 | 88.427 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.4962 | 102.1436
CID=-1936753807 | 6 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7371 | 148.3861 | 17.3476 | 258.655 | 431.8524 | 405.7474 | 30272.866 | 1.5555 | 0.027646 | 3.916 | 58.4265 | 228.7959 | 6 | 47.5 | 4 | 41.5 | 361.9781 | 1237.0237 | 62.7078 | 3.4174 | 0.89243 | 110 | 99.4694 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.1636 | 112.1825
CID=1054251574 | 6 | 50 | 0 | 4 | 44 | 8.8 | 1.7371 | 148.3861 | 17.3476 | 262.425 | 433.1958 | 405.7474 | 31096.5664 | 1.6677 | 0.031224 | 3.6373 | 65.7134 | 239.0208 | 6 | 50 | 4 | 44 | 361.9781 | 1317.9055 | 65.6025 | 3.6408 | 0.89985 | 110 | 110.9533 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3056 | 122.2097
CID=1235820027 | 6 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7371 | 148.3861 | 17.3476 | 266.2308 | 434.5145 | 405.7474 | 31704.3007 | 1.7035 | 0.034028 | 3.368 | 70.5676 | 237.6695 | 6 | 52.5 | 4 | 46.5 | 361.9781 | 1402.6932 | 68.6237 | 3.8751 | 0.90364 | 110 | 118.6488 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.1646 | 124.2598
CID=-68141888 | 6 | 55 | 0 | 4 | 49 | 9.8 | 1.7371 | 148.3861 | 17.3476 | 270.0745 | 435.8088 | 405.7474 | 32294.2784 | 1.7392 | 0.036949 | 3.1337 | 75.2987 | 235.9641 | 6 | 55 | 4 | 49 | 361.9781 | 1491.5141 | 71.5309 | 4.1205 | 0.90666 | 109.8679 | 126.183 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3211 | 60.3101 | 124.6468
CID=1437333125 | 6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7371 | 148.3861 | 17.3476 | 273.9586 | 437.0791 | 405.7474 | 32995.3491 | 1.8505 | 0.041512 | 2.9223 | 83.4531 | 243.8736 | 6 | 57.5 | 4 | 51.5 | 361.9781 | 1584.4992 | 74.4143 | 4.3773 | 0.9106 | 110 | 139.2418 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66.4309 | 124.7604
CID=133371210 | 6 | 60 | 0 | 4 | 54 | 10.8 | 1.7371 | 148.3861 | 17.3476 | 277.8855 | 438.3255 | 405.7474 | 33502.6369 | 1.8477 | 0.044279 | 2.7202 | 86.8498 | 236.253 | 6 | 60 | 4 | 54 | 361.9781 | 1681.7842 | 77.3549 | 4.6461 | 0.91188 | 109.5958 | 144.7063 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.0155 | 124.137
CID=314939663 | 6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7371 | 148.3861 | 17.3476 | 281.8586 | 439.5483 | 405.7474 | 34229.3816 | 1.9581 | 0.049776 | 2.5311 | 95.8405 | 242.5819 | 6 | 62.5 | 4 | 56.5 | 361.9781 | 1783.5096 | 80.3565 | 4.9271 | 0.91448 | 109.4 | 159.2316 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.3904 | 125.2286
CID=-989022252 | 6 | 65 | 0 | 4 | 59 | 11.8 | 1.7371 | 148.3861 | 17.3476 | 285.881 | 440.748 | 405.7474 | 35094.9053 | 2.1433 | 0.057613 | 2.357 | 108.9973 | 256.9078 | 6 | 65 | 4 | 59 | 361.9781 | 1889.8218 | 83.35 | 5.2208 | 0.91687 | 109.7119 | 180.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 7.4005 | 92.0266 | 125.5368
CID=-94993079 | 6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7371 | 148.3861 | 17.3476 | 289.9569 | 441.9247 | 405.7474 | 36024.9213 | 2.4039 | 0.067322 | 2.2299 | 124.8224 | 278.3442 | 6 | 67.5 | 4 | 61.5 | 361.9781 | 2000.8736 | 85.7552 | 5.5276 | 0.91841 | 110 | 206.4952 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7481 | 104.302 | 124.8224
CID=-1398954994 | 6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7371 | 148.3861 | 17.3476 | 294.074 | 443.0743 | 405.7474 | 36152.987 | 2.3247 | 0.0693 | 2.0966 | 123.8195 | 259.6025 | 6 | 69.99 | 4 | 63.99 | 361.9781 | 2116.3519 | 88.3144 | 5.8466 | 0.91834 | 110 | 204.8518 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 116.6406 | 123.8195
CID=-2104903831 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-518616914 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=503019999 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=603776548 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1269183101 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1439497278 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-417860365 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-317103816 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-263143103 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1323143814 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=219410517 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523372432 | 9 | 22.5 | 0 | 4 | 16.5 | 3.3 | 1.7357 | 148.2186 | 19.1581 | 222.5675 | 416.6065 | 407.5003 | 19498.2107 | 0.75857 | 0.0081162 | 11.7646 | 11.9244 | 140.285 | 9 | 22.5 | 4 | 16.5 | 400.9358 | 617.2019 | 32.5594 | 1.5394 | 0.71639 | 83.8079 | 25.2895 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.8546 | 22.6697
CID=154082648 | 9 | 25 | 0 | 4 | 19 | 3.8 | 1.7357 | 148.2186 | 19.1581 | 226.0633 | 418.2053 | 407.5003 | 19848.6208 | 0.80036 | 0.0089246 | 10.206 | 14.2284 | 145.2147 | 9 | 25 | 4 | 19 | 400.9358 | 665.3809 | 35.6236 | 1.6596 | 0.7356 | 106.9529 | 29.3881 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.2198 | 29.301
CID=-1432204269 | 9 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7357 | 148.2186 | 19.1581 | 229.5813 | 419.7772 | 407.5003 | 21110.3389 | 0.88441 | 0.010065 | 9.0131 | 17.4581 | 157.3528 | 9 | 27.5 | 4 | 21.5 | 400.9358 | 716.3449 | 38.6439 | 1.7867 | 0.75951 | 105.2919 | 34.9238 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7081 | 12.4687 | 35.877
CID=355595746 | 9 | 30 | 0 | 4 | 24 | 4.8 | 1.7357 | 148.2186 | 19.1581 | 233.1226 | 421.3224 | 407.5003 | 22321.3833 | 0.96829 | 0.011372 | 8.0369 | 21.009 | 168.8476 | 9 | 30 | 4 | 24 | 400.9358 | 770.1963 | 41.6415 | 1.921 | 0.78223 | 110 | 40.806 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.9305 | 43.1989
CID=254839197 | 9 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7357 | 148.2186 | 19.1581 | 236.688 | 422.8412 | 407.5003 | 23268.9629 | 1.0098 | 0.012501 | 7.2511 | 23.7864 | 172.478 | 9 | 32.5 | 4 | 26.5 | 400.9358 | 827.0396 | 44.5057 | 2.0628 | 0.79774 | 108.1697 | 45.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5757 | 17.2579 | 51.2247
CID=-766797716 | 9 | 35 | 0 | 4 | 29 | 5.8 | 1.7357 | 148.2186 | 19.1581 | 240.2788 | 424.3337 | 407.5003 | 24332.2908 | 1.0934 | 0.014084 | 6.5833 | 27.7721 | 182.8327 | 9 | 35 | 4 | 29 | 400.9358 | 886.981 | 47.3935 | 2.2123 | 0.817 | 109.6879 | 51.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5603 | 20.0505 | 57.5838
CID=1941882663 | 9 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7357 | 148.2186 | 19.1581 | 243.8959 | 425.8002 | 407.5003 | 25310.7547 | 1.1768 | 0.015822 | 6.0199 | 31.9823 | 192.5305 | 9 | 37.5 | 4 | 31.5 | 400.9358 | 950.1287 | 50.2211 | 2.3698 | 0.83406 | 110 | 58.26 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6818 | 66.9124
CID=-1176730458 | 9 | 40 | 0 | 4 | 34 | 6.8 | 1.7357 | 148.2186 | 19.1581 | 247.5407 | 427.2409 | 407.5003 | 26289.7812 | 1.26 | 0.017812 | 5.4971 | 36.6649 | 201.5496 | 9 | 40 | 4 | 34 | 400.9358 | 1016.593 | 53.1764 | 2.5356 | 0.84973 | 110 | 65.5581 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2008 | 77.061
CID=-1277487007 | 9 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7357 | 148.2186 | 19.1581 | 251.2145 | 428.656 | 407.5003 | 27353.3581 | 1.3851 | 0.020468 | 5.0427 | 42.9284 | 216.4761 | 9 | 42.5 | 4 | 36.5 | 400.9358 | 1086.4865 | 56.1279 | 2.7099 | 0.86632 | 110 | 75.2872 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9216 | 87.5743
CID=1276475085 | 9 | 45 | 0 | 4 | 39 | 7.8 | 1.7357 | 148.2186 | 19.1581 | 254.9187 | 430.0457 | 407.5003 | 28295.0438 | 1.51 | 0.023356 | 4.6592 | 49.4507 | 230.4017 | 9 | 45 | 4 | 39 | 400.9358 | 1159.9242 | 58.9628 | 2.893 | 0.87945 | 110 | 85.4314 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.7915 | 97.396
CID=1175718536 | 9 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7357 | 148.2186 | 19.1581 | 258.655 | 431.4103 | 407.5003 | 29073.4267 | 1.5925 | 0.026021 | 4.3119 | 54.9747 | 237.0431 | 9 | 47.5 | 4 | 41.5 | 400.9358 | 1237.0237 | 61.8007 | 3.0853 | 0.88802 | 110 | 94.0577 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.4856 | 105.939
CID=154081623 | 9 | 50 | 0 | 4 | 44 | 8.8 | 1.7357 | 148.2186 | 19.1581 | 262.425 | 432.7501 | 407.5003 | 29699.8688 | 1.6328 | 0.028357 | 3.9965 | 59.2716 | 236.8795 | 9 | 50 | 4 | 44 | 400.9358 | 1317.9055 | 64.6415 | 3.2871 | 0.89342 | 110 | 100.7971 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3087 | 117.1977
CID=-1432205294 | 9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7357 | 148.2186 | 19.1581 | 266.2308 | 434.0651 | 407.5003 | 30442.2593 | 1.7148 | 0.03158 | 3.7002 | 65.4671 | 242.2443 | 9 | 52.5 | 4 | 46.5 | 400.9358 | 1402.6932 | 67.5824 | 3.4985 | 0.89963 | 110 | 110.5638 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.6486 | 126.9601
CID=355594721 | 9 | 55 | 0 | 4 | 49 | 9.8 | 1.7357 | 148.2186 | 19.1581 | 270.0745 | 435.3559 | 407.5003 | 31238.3174 | 1.8384 | 0.035755 | 3.4359 | 73.5296 | 252.6399 | 9 | 55 | 4 | 49 | 400.9358 | 1491.5141 | 70.4942 | 3.7201 | 0.9056 | 110 | 123.362 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.9361 | 126.9601
CID=254838172 | 9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7357 | 148.2186 | 19.1581 | 273.9586 | 436.6225 | 407.5003 | 31827.693 | 1.8777 | 0.038974 | 3.1857 | 78.7134 | 250.7579 | 9 | 57.5 | 4 | 51.5 | 400.9358 | 1584.4992 | 73.4719 | 3.952 | 0.90848 | 110 | 131.6406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5619 | 126.9602
CID=-766798741 | 9 | 60 | 0 | 4 | 54 | 10.8 | 1.7357 | 148.2186 | 19.1581 | 277.8855 | 437.8652 | 407.5003 | 32393.6368 | 1.917 | 0.042361 | 2.9648 | 83.8052 | 248.4658 | 9 | 60 | 4 | 54 | 400.9358 | 1681.7842 | 76.3634 | 4.1946 | 0.91074 | 109.3362 | 139.8075 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.5145 | 126.9601
CID=1941881638 | 9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7357 | 148.2186 | 19.1581 | 281.8586 | 439.0844 | 407.5003 | 33088.5851 | 2.0395 | 0.047648 | 2.7661 | 92.6362 | 256.2402 | 9 | 62.5 | 4 | 56.5 | 400.9358 | 1783.5096 | 79.2119 | 4.4484 | 0.91367 | 110 | 154.0451 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.8839 | 126.9602
CID=-1176731483 | 9 | 65 | 0 | 4 | 59 | 11.8 | 1.7357 | 148.2186 | 19.1581 | 285.881 | 440.2804 | 407.5003 | 33660.1253 | 2.0778 | 0.051867 | 2.5692 | 98.3578 | 252.7037 | 9 | 65 | 4 | 59 | 400.9358 | 1889.8218 | 82.207 | 4.7135 | 0.91505 | 109.6788 | 163.3127 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84.545 | 126.9602
CID=-1277488032 | 9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7357 | 148.2186 | 19.1581 | 289.9569 | 441.4534 | 407.5003 | 34361.8821 | 2.1991 | 0.058374 | 2.3888 | 108.2069 | 258.4897 | 9 | 67.5 | 4 | 61.5 | 400.9358 | 2000.8736 | 85.1894 | 4.9905 | 0.91676 | 109.4345 | 179.3312 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 93.4753 | 126.9601
CID=1276474064 | 9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7357 | 148.2186 | 19.1581 | 294.074 | 442.5993 | 407.5003 | 35290.2133 | 2.4444 | 0.068642 | 2.2242 | 124.6538 | 277.2587 | 9 | 69.99 | 4 | 63.99 | 400.9358 | 2116.3519 | 88.1332 | 5.2785 | 0.9184 | 110 | 206.219 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 102.6563 | 126.9602
CID=1523374478 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1467630903 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-163668988 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-701467801 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=602494114 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1906456029 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1084549352 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2061173291 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-929832090 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=219413588 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523375503 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=154079577 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1432207340 | 12 | 25 | 0 | 4 | 19 | 3.8 | 1.7345 | 147.9949 | 21.1172 | 226.0633 | 417.8241 | 409.2305 | 19468.4803 | 0.78878 | 0.0081562 | 12.2599 | 11.7846 | 144.4785 | 12 | 25 | 4 | 19 | 443.0145 | 665.3809 | 34.6841 | 1.5019 | 0.71516 | 70.7701 | 25.036 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.795 | 16.7083
CID=355592675 | 12 | 27.5 | 0 | 4 | 21.5 | 4.3 | 1.7345 | 147.9949 | 21.1172 | 229.5813 | 419.3925 | 409.2305 | 19549.0267 | 0.88147 | 0.0092173 | 10.609 | 14.9266 | 158.3562 | 12 | 27.5 | 4 | 21.5 | 443.0145 | 716.3449 | 37.7661 | 1.617 | 0.74105 | 104.3966 | 30.6033 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.1128 | 29.8031
CID=254836126 | 12 | 30 | 0 | 4 | 24 | 4.8 | 1.7345 | 147.9949 | 21.1172 | 233.1226 | 420.9344 | 409.2305 | 20606.0888 | 0.92737 | 0.010197 | 9.3038 | 17.5539 | 163.3179 | 12 | 30 | 4 | 24 | 443.0145 | 770.1963 | 40.7772 | 1.7385 | 0.76017 | 108.2983 | 35.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9999 | 13.0293 | 36.7366
CID=-766800787 | 12 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7345 | 147.9949 | 21.1172 | 236.688 | 422.4497 | 409.2305 | 21790.8496 | 1.0197 | 0.011581 | 8.2665 | 21.2847 | 175.9496 | 12 | 32.5 | 4 | 26.5 | 443.0145 | 827.0396 | 43.7819 | 1.8668 | 0.78386 | 109.6452 | 41.2559 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8869 | 15.6766 | 44.2749
CID=1941879592 | 12 | 35 | 0 | 4 | 29 | 5.8 | 1.7345 | 147.9949 | 21.1172 | 240.2788 | 423.9389 | 409.2305 | 22749.2611 | 1.0654 | 0.012774 | 7.4371 | 24.2038 | 180.0066 | 12 | 35 | 4 | 29 | 443.0145 | 886.981 | 46.6546 | 2.0021 | 0.79992 | 106.8463 | 45.9721 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.1723 | 52.5653
CID=-1176733529 | 12 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7345 | 147.9949 | 21.1172 | 243.8959 | 425.402 | 409.2305 | 23840.9434 | 1.1575 | 0.014443 | 6.7471 | 28.3646 | 191.378 | 12 | 37.5 | 4 | 31.5 | 443.0145 | 950.1287 | 49.5137 | 2.1447 | 0.81959 | 109.0831 | 52.5819 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5845 | 20.8063 | 59.3536
CID=-1277490078 | 12 | 40 | 0 | 4 | 34 | 6.8 | 1.7345 | 147.9949 | 21.1172 | 247.5407 | 426.8393 | 409.2305 | 24995.7887 | 1.2959 | 0.016726 | 6.1511 | 34.0639 | 209.5294 | 12 | 40 | 4 | 34 | 443.0145 | 1016.593 | 52.393 | 2.2947 | 0.84141 | 110 | 61.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0173 | 68.7122
CID=1276480210 | 12 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7345 | 147.9949 | 21.1172 | 251.2145 | 428.251 | 409.2305 | 25947.4983 | 1.3875 | 0.018843 | 5.6267 | 38.9657 | 219.2492 | 12 | 42.5 | 4 | 36.5 | 443.0145 | 1086.4865 | 55.2602 | 2.4525 | 0.85635 | 110 | 69.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0083 | 79.3022
CID=1175723661 | 12 | 45 | 0 | 4 | 39 | 7.8 | 1.7345 | 147.9949 | 21.1172 | 254.9187 | 429.6374 | 409.2305 | 26867.1519 | 1.4789 | 0.021214 | 5.1554 | 44.2662 | 228.2115 | 12 | 45 | 4 | 39 | 443.0145 | 1159.9242 | 58.1759 | 2.6183 | 0.86932 | 110 | 77.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.8335 | 90.1739
CID=154086748 | 12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7345 | 147.9949 | 21.1172 | 258.655 | 430.9986 | 409.2305 | 27751.0549 | 1.579 | 0.023923 | 4.7418 | 50.1399 | 237.7555 | 12 | 47.5 | 4 | 41.5 | 443.0145 | 1237.0237 | 61.0785 | 2.7923 | 0.88063 | 110 | 86.5056 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2059 | 102.0198
CID=-1432200169 | 12 | 50 | 0 | 4 | 44 | 8.8 | 1.7345 | 147.9949 | 21.1172 | 262.425 | 432.335 | 409.2305 | 28513.2973 | 1.661 | 0.026612 | 4.3875 | 55.5775 | 243.846 | 12 | 50 | 4 | 44 | 443.0145 | 1317.9055 | 63.8869 | 2.9749 | 0.88884 | 110 | 95.0016 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.3372 | 109.7483
CID=355599846 | 12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7345 | 147.9949 | 21.1172 | 266.2308 | 433.6467 | 409.2305 | 29229.6458 | 1.7518 | 0.029616 | 4.0775 | 61.4347 | 250.5022 | 12 | 52.5 | 4 | 46.5 | 443.0145 | 1402.6932 | 66.6332 | 3.1662 | 0.89578 | 110 | 104.2003 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5194 | 121.423
CID=254843297 | 12 | 55 | 0 | 4 | 49 | 9.8 | 1.7345 | 147.9949 | 21.1172 | 270.0745 | 434.934 | 409.2305 | 30088.4972 | 1.8883 | 0.033759 | 3.7709 | 69.6817 | 262.7626 | 12 | 55 | 4 | 49 | 443.0145 | 1491.5141 | 69.5771 | 3.3667 | 0.90301 | 110 | 117.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8145 | 126.9602
CID=-766793616 | 12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7345 | 147.9949 | 21.1172 | 273.9586 | 436.1972 | 409.2305 | 30900.6145 | 2.0243 | 0.038317 | 3.496 | 78.3292 | 273.8361 | 12 | 57.5 | 4 | 51.5 | 443.0145 | 1584.4992 | 72.4946 | 3.5766 | 0.90829 | 110 | 131.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5802 | 126.9601
CID=1941886763 | 12 | 60 | 0 | 4 | 54 | 10.8 | 1.7345 | 147.9949 | 21.1172 | 277.8855 | 437.4365 | 409.2305 | 31363.2175 | 2.0216 | 0.041006 | 3.2406 | 81.94 | 265.5334 | 12 | 60 | 4 | 54 | 443.0145 | 1681.7842 | 75.4282 | 3.7962 | 0.90997 | 110 | 136.812 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.8856 | 126.9602
CID=-1176726358 | 12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7345 | 147.9949 | 21.1172 | 281.8586 | 438.6523 | 409.2305 | 31932.5639 | 2.0648 | 0.044695 | 3.0089 | 87.4068 | 263.0025 | 12 | 62.5 | 4 | 56.5 | 443.0145 | 1783.5096 | 78.3522 | 4.0258 | 0.91207 | 109.9338 | 145.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 5.8269 | 70.1201 | 126.9601
CID=-1277482907 | 12 | 65 | 0 | 4 | 59 | 11.8 | 1.7345 | 147.9949 | 21.1172 | 285.881 | 439.8448 | 409.2305 | 32628.7755 | 2.1997 | 0.050476 | 2.8001 | 96.901 | 271.3309 | 12 | 65 | 4 | 59 | 443.0145 | 1889.8218 | 81.2448 | 4.2658 | 0.91473 | 110 | 160.9503 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0001 | 76.1762 | 126.9602
CID=1276479185 | 12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7345 | 147.9949 | 21.1172 | 289.9569 | 441.0144 | 409.2305 | 33160.9011 | 2.2422 | 0.054857 | 2.6081 | 102.5384 | 267.4342 | 12 | 67.5 | 4 | 61.5 | 443.0145 | 2000.8736 | 84.1019 | 4.5165 | 0.91586 | 109.6654 | 170.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7887 | 84.6298 | 126.9602
CID=1175722636 | 12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7345 | 147.9949 | 21.1172 | 294.074 | 442.1569 | 409.2305 | 33789.3306 | 2.3299 | 0.06089 | 2.4197 | 110.8825 | 268.3047 | 12 | 69.99 | 4 | 63.99 | 443.0145 | 2116.3519 | 87.0971 | 4.7772 | 0.91711 | 109.7005 | 183.6949 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.7107 | 126.9601
CID=-1467636024 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-163674109 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-701472922 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=602488993 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1906450908 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1084554473 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2061168170 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-929837211 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=219408463 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523370378 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=154084702 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1432202215 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=355597800 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=254841251 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-766795662 | 15 | 30 | 0 | 4 | 24 | 4.8 | 1.7333 | 147.7132 | 23.2347 | 233.1226 | 420.5719 | 410.9364 | 19434.9692 | 0.96859 | 0.0095473 | 10.9585 | 15.7164 | 172.229 | 15 | 30 | 4 | 24 | 488.3739 | 770.1963 | 40.0259 | 1.5771 | 0.74703 | 102.0844 | 31.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.3198 | 30.1197
CID=1941884717 | 15 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7333 | 147.7132 | 23.2347 | 236.688 | 422.0841 | 410.9364 | 20289.0656 | 1.019 | 0.010575 | 9.6389 | 18.4219 | 177.567 | 15 | 32.5 | 4 | 26.5 | 488.3739 | 827.0396 | 42.9212 | 1.6935 | 0.76602 | 108.909 | 36.5384 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7276 | 13.0742 | 37.5319
CID=-1176728404 | 15 | 35 | 0 | 4 | 29 | 5.8 | 1.7333 | 147.7132 | 23.2347 | 240.2788 | 423.5701 | 410.9364 | 21492.1682 | 1.1205 | 0.012087 | 8.5123 | 22.4642 | 191.2211 | 15 | 35 | 4 | 29 | 488.3739 | 886.981 | 45.9617 | 1.8162 | 0.79059 | 110 | 43.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.7101 | 45.2884
CID=-1277484953 | 15 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7333 | 147.7132 | 23.2347 | 243.8959 | 425.03 | 410.9364 | 22427.3093 | 1.1707 | 0.013376 | 7.6435 | 25.5841 | 195.5523 | 15 | 37.5 | 4 | 31.5 | 488.3739 | 950.1287 | 48.8188 | 1.9455 | 0.80684 | 109.4075 | 48.1771 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4812 | 18.4587 | 53.9129
CID=1276477139 | 15 | 40 | 0 | 4 | 34 | 6.8 | 1.7333 | 147.7132 | 23.2347 | 247.5407 | 426.4641 | 410.9364 | 23341.0721 | 1.2208 | 0.01477 | 6.9205 | 28.823 | 199.4693 | 15 | 40 | 4 | 34 | 488.3739 | 1016.593 | 51.6411 | 2.0816 | 0.82155 | 108.5827 | 53.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.4735 | 63.3068
CID=1175720590 | 15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7333 | 147.7132 | 23.2347 | 251.2145 | 427.8727 | 410.9364 | 24353.8265 | 1.3218 | 0.016743 | 6.298 | 33.5211 | 211.1146 | 15 | 42.5 | 4 | 36.5 | 488.3739 | 1086.4865 | 54.4931 | 2.2247 | 0.83956 | 109.1895 | 60.663 | 0 | 0 | 0 | 0 | 0 | 0 | 9.0524 | 24.7682 | 70.5569
CID=154083677 | 15 | 45 | 0 | 4 | 39 | 7.8 | 1.7333 | 147.7132 | 23.2347 | 254.9187 | 429.2559 | 410.9364 | 25289.4852 | 1.4226 | 0.018904 | 5.7709 | 38.4595 | 221.9453 | 15 | 45 | 4 | 39 | 488.3739 | 1159.9242 | 57.2858 | 2.3751 | 0.85495 | 110 | 68.347 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.93 | 81.3534
CID=-1432203240 | 15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7333 | 147.7132 | 23.2347 | 258.655 | 430.614 | 410.9364 | 26234.3212 | 1.523 | 0.021396 | 5.2722 | 43.9911 | 231.9298 | 15 | 47.5 | 4 | 41.5 | 488.3739 | 1237.0237 | 60.2292 | 2.5329 | 0.86872 | 110 | 76.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.6346 | 92.9494
CID=355596775 | 15 | 50 | 0 | 4 | 44 | 8.8 | 1.7333 | 147.7132 | 23.2347 | 262.425 | 431.9472 | 410.9364 | 27259.7062 | 1.6742 | 0.024716 | 4.8409 | 51.3608 | 248.6314 | 15 | 50 | 4 | 44 | 488.3739 | 1317.9055 | 63.1494 | 2.6986 | 0.88265 | 110 | 88.4098 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.943 | 104.9514
CID=254840226 | 15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7333 | 147.7132 | 23.2347 | 266.2308 | 433.2557 | 410.9364 | 28168.8519 | 1.825 | 0.028331 | 4.4747 | 59.017 | 264.0856 | 15 | 52.5 | 4 | 46.5 | 488.3739 | 1402.6932 | 65.9655 | 2.8722 | 0.89312 | 110 | 100.397 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2093 | 116.6989
CID=-766796687 | 15 | 55 | 0 | 4 | 49 | 9.8 | 1.7333 | 147.7132 | 23.2347 | 270.0745 | 434.5399 | 410.9364 | 28924.3876 | 1.9246 | 0.031684 | 4.1391 | 65.498 | 271.102 | 15 | 55 | 4 | 49 | 488.3739 | 1491.5141 | 68.8058 | 3.054 | 0.89966 | 110 | 110.6127 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8297 | 125.5944
CID=1941883692 | 15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7333 | 147.7132 | 23.2347 | 273.9586 | 435.7999 | 410.9364 | 29505.4639 | 1.9732 | 0.034572 | 3.8417 | 70.3552 | 270.283 | 15 | 57.5 | 4 | 51.5 | 488.3739 | 1584.4992 | 71.5935 | 3.2444 | 0.90349 | 110 | 118.3113 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.704 | 126.9601
CID=-1176729429 | 15 | 60 | 0 | 4 | 54 | 10.8 | 1.7333 | 147.7132 | 23.2347 | 277.8855 | 437.0361 | 410.9364 | 30227.5934 | 2.0721 | 0.038649 | 3.5527 | 77.6013 | 275.691 | 15 | 60 | 4 | 54 | 488.3739 | 1681.7842 | 74.5356 | 3.4436 | 0.90791 | 110 | 129.8614 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.1896 | 126.9601
CID=-1277485978 | 15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7333 | 147.7132 | 23.2347 | 281.8586 | 438.2486 | 410.9364 | 30996.2737 | 2.2213 | 0.043891 | 3.2988 | 86.9164 | 286.7172 | 15 | 62.5 | 4 | 56.5 | 488.3739 | 1783.5096 | 77.4081 | 3.6519 | 0.9119 | 110 | 144.8134 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.9624 | 126.9602
CID=1276484310 | 15 | 65 | 0 | 4 | 59 | 11.8 | 1.7333 | 147.7132 | 23.2347 | 285.881 | 439.4379 | 410.9364 | 31460.0386 | 2.2181 | 0.047083 | 3.0522 | 90.8811 | 277.383 | 15 | 65 | 4 | 59 | 488.3739 | 1889.8218 | 80.3882 | 3.8696 | 0.91317 | 110 | 151.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71.2677 | 126.9602
CID=1175727761 | 15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7333 | 147.7132 | 23.2347 | 289.9569 | 440.6043 | 410.9364 | 32069.0312 | 2.2958 | 0.051962 | 2.835 | 97.9703 | 277.7445 | 15 | 67.5 | 4 | 61.5 | 488.3739 | 2000.8736 | 83.2879 | 4.097 | 0.91497 | 109.844 | 162.6842 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9499 | 78.9695 | 126.9602
CID=154090848 | 15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7333 | 147.7132 | 23.2347 | 294.074 | 441.7436 | 410.9364 | 32682.7973 | 2.413 | 0.058111 | 2.6366 | 106.952 | 281.9863 | 15 | 69.99 | 4 | 63.99 | 488.3739 | 2116.3519 | 86.1618 | 4.3335 | 0.91658 | 110 | 177.2862 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 85.6595 | 126.9602
CID=-163679234 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-701478047 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=602483868 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1906445783 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1084559598 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2061163045 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-929842336 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=219403342 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523365257 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=154089823 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1432197094 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=355602921 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=254846372 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-766790541 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1941889838 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1176723283 | 18 | 32.5 | 0 | 4 | 26.5 | 5.3 | 1.7322 | 147.3721 | 25.5211 | 236.688 | 421.7412 | 412.6163 | 19386.8546 | 1.0059 | 0.0095754 | 11.4394 | 15.4702 | 176.97 | 18 | 32.5 | 4 | 26.5 | 537.1767 | 827.0396 | 42.1058 | 1.5396 | 0.74519 | 84.7446 | 31.5419 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.839 | 32.3325
CID=-1277479832 | 18 | 35 | 0 | 4 | 29 | 5.8 | 1.7322 | 147.3721 | 25.5211 | 240.2788 | 423.2242 | 412.6163 | 19749.7596 | 1.0612 | 0.010684 | 9.9416 | 18.3965 | 182.8897 | 18 | 35 | 4 | 29 | 537.1767 | 886.981 | 45.1169 | 1.6512 | 0.76585 | 107.1025 | 36.4959 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9999 | 13.112 | 38.233
CID=1275184455 | 18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7322 | 147.3721 | 25.5211 | 243.8959 | 424.6812 | 412.6163 | 20957.0104 | 1.1725 | 0.012233 | 8.7973 | 22.4873 | 197.8269 | 18 | 37.5 | 4 | 31.5 | 537.1767 | 950.1287 | 48.0667 | 1.7687 | 0.79072 | 106.123 | 43.2087 | 0 | 0 | 0 | 0 | 0 | 0 | 8.877 | 15.9579 | 46.2963
CID=-28777460 | 18 | 40 | 0 | 4 | 34 | 6.8 | 1.7322 | 147.3721 | 25.5211 | 247.5407 | 426.1123 | 412.6163 | 22109.6271 | 1.2836 | 0.013998 | 7.8564 | 26.9701 | 211.8877 | 18 | 40 | 4 | 34 | 537.1767 | 1016.593 | 51.0014 | 1.8925 | 0.81338 | 110 | 50.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0416 | 55.1907
CID=-411859011 | 18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7322 | 147.3721 | 25.5211 | 251.2145 | 427.5179 | 412.6163 | 23003.7877 | 1.3385 | 0.01552 | 7.089 | 30.4743 | 216.0324 | 18 | 42.5 | 4 | 36.5 | 537.1767 | 1086.4865 | 53.8456 | 2.0226 | 0.8283 | 109.3877 | 55.8989 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5309 | 21.9546 | 64.858
CID=-1715820926 | 18 | 45 | 0 | 4 | 39 | 7.8 | 1.7322 | 147.3721 | 25.5211 | 254.9187 | 428.8982 | 412.6163 | 23858.6595 | 1.3933 | 0.017161 | 6.4434 | 34.0987 | 219.7123 | 18 | 45 | 4 | 39 | 537.1767 | 1159.9242 | 56.6579 | 2.1593 | 0.84153 | 109 | 61.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.0409 | 72.3151
CID=-2098902477 | 18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7322 | 147.3721 | 25.5211 | 258.655 | 430.2533 | 412.6163 | 24873.6437 | 1.526 | 0.019686 | 5.8855 | 39.9202 | 234.9524 | 18 | 47.5 | 4 | 41.5 | 537.1767 | 1237.0237 | 59.4932 | 2.3028 | 0.85891 | 109.6371 | 70.6158 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8146 | 28.9027 | 83.3388
CID=892102904 | 18 | 50 | 0 | 4 | 44 | 8.8 | 1.7322 | 147.3721 | 25.5211 | 262.425 | 431.5835 | 412.6163 | 25888.406 | 1.6698 | 0.022654 | 5.3855 | 46.5686 | 250.7955 | 18 | 50 | 4 | 44 | 537.1767 | 1317.9055 | 62.3727 | 2.4534 | 0.8741 | 110 | 80.9448 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7506 | 95.4733
CID=509021353 | 18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7322 | 147.3721 | 25.5211 | 266.2308 | 432.8891 | 412.6163 | 26770.8967 | 1.7797 | 0.025605 | 4.9393 | 52.7455 | 260.5257 | 18 | 52.5 | 4 | 46.5 | 537.1767 | 1402.6932 | 65.2653 | 2.6112 | 0.88481 | 110 | 90.5718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.0197 | 107.8119
CID=-794940562 | 18 | 55 | 0 | 4 | 49 | 9.8 | 1.7322 | 147.3721 | 25.5211 | 270.0745 | 434.1702 | 412.6163 | 27596.9519 | 1.8893 | 0.028857 | 4.5444 | 59.2613 | 269.3047 | 18 | 55 | 4 | 49 | 537.1767 | 1491.5141 | 68.1522 | 2.7766 | 0.89341 | 110 | 100.7809 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9579 | 121.2507
CID=-1178022113 | 18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7322 | 147.3721 | 25.5211 | 273.9586 | 435.4273 | 412.6163 | 28351.0362 | 1.9986 | 0.032347 | 4.2058 | 65.8924 | 277.1278 | 18 | 57.5 | 4 | 51.5 | 537.1767 | 1584.4992 | 70.9511 | 2.9497 | 0.9 | 110 | 111.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.6837 | 126.9601
CID=1812983268 | 18 | 60 | 0 | 4 | 54 | 10.8 | 1.7322 | 147.3721 | 25.5211 | 277.8855 | 436.6604 | 412.6163 | 29048.6608 | 2.1077 | 0.03614 | 3.9041 | 72.737 | 283.9701 | 18 | 60 | 4 | 54 | 537.1767 | 1681.7842 | 73.7191 | 3.1308 | 0.9051 | 110 | 122.0995 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1459 | 126.9601
CID=1275183430 | 18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7322 | 147.3721 | 25.5211 | 281.8586 | 437.87 | 412.6163 | 29869.2642 | 2.2718 | 0.041319 | 3.612 | 82.2397 | 297.0498 | 18 | 62.5 | 4 | 56.5 | 537.1767 | 1783.5096 | 76.6213 | 3.3202 | 0.9101 | 110 | 137.293 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59.592 | 126.9601
CID=-28778485 | 18 | 65 | 0 | 4 | 59 | 11.8 | 1.7322 | 147.3721 | 25.5211 | 285.881 | 439.0563 | 412.6163 | 30337.1788 | 2.2688 | 0.044307 | 3.3425 | 86.0245 | 287.5331 | 18 | 65 | 4 | 59 | 537.1767 | 1889.8218 | 79.5282 | 3.5181 | 0.91159 | 110 | 143.3773 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.4574 | 126.9601
CID=-411860036 | 18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7322 | 147.3721 | 25.5211 | 289.9569 | 440.2196 | 412.6163 | 31086.2323 | 2.4319 | 0.050472 | 3.0984 | 96.2722 | 298.2897 | 18 | 67.5 | 4 | 61.5 | 537.1767 | 2000.8736 | 82.4393 | 3.7248 | 0.91458 | 110 | 159.931 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.1509 | 126.9602
CID=-1715821951 | 18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7322 | 147.3721 | 25.5211 | 294.074 | 441.3558 | 412.6163 | 31625.8189 | 2.4835 | 0.055241 | 2.8684 | 102.6361 | 294.3998 | 18 | 69.99 | 4 | 63.99 | 537.1767 | 2116.3519 | 85.3877 | 3.9398 | 0.91588 | 110 | 170.2616 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79.9236 | 126.9602
CID=574350247 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2134330132 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-548043215 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-447286666 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1495230611 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1213449768 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-346529096 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1239757821 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-411861057 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1715822972 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2098904523 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=892100858 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=509019307 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-794942608 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1178024159 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1812981222 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1275181384 | 21 | 35 | 0 | 4 | 29 | 5.8 | 1.7312 | 146.9698 | 27.9878 | 240.2788 | 422.8982 | 414.2684 | 19333.7604 | 1.0685 | 0.0097518 | 11.8418 | 15.6989 | 185.9026 | 21 | 35 | 4 | 29 | 589.5892 | 886.981 | 44.3525 | 1.5044 | 0.7469 | 76.3286 | 31.9348 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.5732 | 24.4855
CID=-28780531 | 21 | 37.5 | 0 | 4 | 31.5 | 6.3 | 1.7312 | 146.9698 | 27.9878 | 243.8959 | 424.3523 | 414.2684 | 19445.1691 | 1.1613 | 0.011058 | 10.3116 | 19.1867 | 197.8453 | 21 | 37.5 | 4 | 31.5 | 589.5892 | 950.1287 | 47.2926 | 1.6115 | 0.771 | 104.6847 | 37.8093 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.0444 | 38.7928
CID=-411862082 | 21 | 40 | 0 | 4 | 34 | 6.8 | 1.7312 | 146.9698 | 27.9878 | 247.5407 | 425.7807 | 414.2684 | 20446.3547 | 1.2216 | 0.012373 | 9.0651 | 22.4686 | 203.6807 | 21 | 40 | 4 | 34 | 589.5892 | 1016.593 | 50.2477 | 1.7242 | 0.79061 | 108.2695 | 43.1784 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.5838 | 47.2501
CID=-1715823997 | 21 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7312 | 146.9698 | 27.9878 | 251.2145 | 427.1835 | 414.2684 | 21580.0159 | 1.3432 | 0.014238 | 8.0618 | 27.1664 | 219.0096 | 21 | 42.5 | 4 | 36.5 | 589.5892 | 1086.4865 | 53.206 | 1.8428 | 0.81428 | 110 | 50.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8198 | 56.3689
CID=-2098905548 | 21 | 45 | 0 | 4 | 39 | 7.8 | 1.7312 | 146.9698 | 27.9878 | 254.9187 | 428.5609 | 414.2684 | 22484.6252 | 1.4033 | 0.015837 | 7.2573 | 30.812 | 223.6114 | 21 | 45 | 4 | 39 | 589.5892 | 1159.9242 | 56.0544 | 1.9673 | 0.82962 | 107.8312 | 56.4283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9995 | 66.3301
CID=892099833 | 21 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7312 | 146.9698 | 27.9878 | 258.655 | 429.9132 | 414.2684 | 23364.3983 | 1.4633 | 0.01755 | 6.5921 | 34.5419 | 227.7033 | 21 | 47.5 | 4 | 41.5 | 589.5892 | 1237.0237 | 58.8457 | 2.0981 | 0.84301 | 108.7852 | 62.254 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.2319 | 76.5263
CID=509018282 | 21 | 50 | 0 | 4 | 44 | 8.8 | 1.7312 | 146.9698 | 27.9878 | 262.425 | 431.2407 | 414.2684 | 24330.7172 | 1.5842 | 0.020001 | 6.0092 | 40.0304 | 240.5522 | 21 | 50 | 4 | 44 | 589.5892 | 1317.9055 | 61.6812 | 2.2353 | 0.8592 | 109 | 70.7869 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.9299 | 85.388
CID=-794943633 | 21 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7312 | 146.9698 | 27.9878 | 266.2308 | 432.5434 | 414.2684 | 25236.4823 | 1.7049 | 0.0227 | 5.5085 | 45.8181 | 252.3914 | 21 | 52.5 | 4 | 46.5 | 589.5892 | 1402.6932 | 64.4809 | 2.3791 | 0.87259 | 109.8485 | 79.7777 | 0 | 0 | 0 | 0 | 0 | 0 | 6.5154 | 34.5049 | 97.772
CID=-1178025184 | 21 | 55 | 0 | 4 | 49 | 9.8 | 1.7312 | 146.9698 | 27.9878 | 270.0745 | 433.8218 | 414.2684 | 26139.0871 | 1.8252 | 0.025793 | 5.0392 | 52.2281 | 263.1859 | 21 | 55 | 4 | 49 | 589.5892 | 1491.5141 | 67.397 | 2.5298 | 0.88401 | 110 | 89.7638 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.7568 | 110.8709
CID=1812980197 | 21 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7312 | 146.9698 | 27.9878 | 273.9586 | 435.076 | 414.2684 | 27125.9739 | 2.0062 | 0.029932 | 4.6294 | 60.8039 | 281.4874 | 21 | 57.5 | 4 | 51.5 | 589.5892 | 1584.4992 | 70.2985 | 2.6875 | 0.89511 | 110 | 103.2071 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.7196 | 124.4588
CID=1275188555 | 21 | 60 | 0 | 4 | 54 | 10.8 | 1.7312 | 146.9698 | 27.9878 | 277.8855 | 436.3063 | 414.2684 | 28003.4969 | 2.1868 | 0.034453 | 4.2789 | 69.6995 | 298.2373 | 21 | 60 | 4 | 54 | 589.5892 | 1681.7842 | 73.111 | 2.8525 | 0.90302 | 110 | 117.27 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.373 | 126.9601
CID=-28773360 | 21 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7312 | 146.9698 | 27.9878 | 281.8586 | 437.513 | 414.2684 | 28736.8153 | 2.3059 | 0.03868 | 3.9533 | 77.2337 | 305.329 | 21 | 62.5 | 4 | 56.5 | 589.5892 | 1783.5096 | 75.9679 | 3.025 | 0.90772 | 110 | 129.2737 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7306 | 126.9601
CID=-411854911 | 21 | 65 | 0 | 4 | 59 | 11.8 | 1.7312 | 146.9698 | 27.9878 | 285.881 | 438.6964 | 414.2684 | 29173.1925 | 2.3033 | 0.041366 | 3.6686 | 80.6048 | 295.7086 | 21 | 65 | 4 | 59 | 589.5892 | 1889.8218 | 78.7374 | 3.2053 | 0.90938 | 110 | 134.6704 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.4786 | 126.9602
CID=-1715816826 | 21 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7312 | 146.9698 | 27.9878 | 289.9569 | 439.8569 | 414.2684 | 29975.6749 | 2.4823 | 0.047439 | 3.3893 | 91.0434 | 308.5763 | 21 | 67.5 | 4 | 61.5 | 589.5892 | 2000.8736 | 81.6765 | 3.3937 | 0.91322 | 110 | 151.4709 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.0331 | 126.9602
CID=-2098898377 | 21 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7312 | 146.9698 | 27.9878 | 294.074 | 440.9902 | 414.2684 | 30727.6182 | 2.6607 | 0.054093 | 3.1414 | 101.8028 | 319.8046 | 21 | 69.99 | 4 | 63.99 | 589.5892 | 2116.3519 | 84.5509 | 3.5895 | 0.91573 | 110 | 168.9069 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.1546 | 126.9602
CID=-2134335257 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-548048340 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-447291791 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1495225486 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1213454893 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-346534217 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1239752700 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-411855936 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1715817851 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2098899402 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=892105979 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=509024428 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-794937487 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1178019038 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1812986343 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1275186509 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-28775406 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-411856957 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1715818872 | 24 | 40 | 0 | 4 | 34 | 6.8 | 1.7302 | 146.5045 | 30.6472 | 247.5407 | 425.4661 | 415.8906 | 19284.023 | 1.2681 | 0.011487 | 10.6186 | 20.1055 | 213.4925 | 24 | 40 | 4 | 34 | 645.7808 | 1016.593 | 49.5906 | 1.5742 | 0.77678 | 102.5553 | 39.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.4516 | 39.1373
CID=-2098900423 | 24 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7302 | 146.5045 | 30.6472 | 251.2145 | 426.8662 | 415.8906 | 20127.9748 | 1.3341 | 0.012861 | 9.3612 | 23.469 | 219.6982 | 24 | 42.5 | 4 | 36.5 | 645.7808 | 1086.4865 | 52.4519 | 1.6824 | 0.79606 | 108.864 | 44.7923 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8399 | 16.6006 | 48.1204
CID=892104958 | 24 | 45 | 0 | 4 | 39 | 7.8 | 1.7302 | 146.5045 | 30.6472 | 254.9187 | 428.241 | 415.8906 | 21278.1744 | 1.4668 | 0.014881 | 8.2851 | 28.4985 | 236.1138 | 24 | 45 | 4 | 39 | 645.7808 | 1159.9242 | 55.4321 | 1.7962 | 0.82017 | 110 | 52.793 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7334 | 57.4863
CID=509023407 | 24 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7302 | 146.5045 | 30.6472 | 258.655 | 429.5907 | 415.8906 | 22161.6415 | 1.5324 | 0.016594 | 7.4481 | 32.351 | 240.9539 | 24 | 47.5 | 4 | 41.5 | 645.7808 | 1237.0237 | 58.2632 | 1.9155 | 0.83541 | 110 | 58.8362 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.8929 | 67.8348
CID=-794938508 | 24 | 50 | 0 | 4 | 44 | 8.8 | 1.7302 | 146.5045 | 30.6472 | 262.425 | 430.9154 | 415.8906 | 23018.3221 | 1.5979 | 0.018449 | 6.7479 | 36.3415 | 245.2276 | 24 | 50 | 4 | 44 | 645.7808 | 1317.9055 | 61.0668 | 2.0408 | 0.84875 | 108.0006 | 65.0551 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.2397 | 79.0043
CID=-1178020059 | 24 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7302 | 146.5045 | 30.6472 | 266.2308 | 432.2155 | 415.8906 | 23831.8688 | 1.6632 | 0.020486 | 6.1388 | 40.5487 | 248.9207 | 24 | 52.5 | 4 | 46.5 | 645.7808 | 1402.6932 | 63.888 | 2.1721 | 0.86054 | 108.9708 | 71.5917 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.8629 | 87.3441
CID=1812985322 | 24 | 55 | 0 | 4 | 49 | 9.8 | 1.7302 | 146.5045 | 30.6472 | 270.0745 | 433.4912 | 415.8906 | 24741.6154 | 1.7951 | 0.023349 | 5.6159 | 46.6089 | 261.7515 | 24 | 55 | 4 | 49 | 645.7808 | 1491.5141 | 66.7008 | 2.3096 | 0.87418 | 108.9991 | 81.0073 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9999 | 34.4237 | 99.9239
CID=1275185484 | 24 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7302 | 146.5045 | 30.6472 | 273.9586 | 434.7427 | 415.8906 | 25786.8999 | 1.9932 | 0.027325 | 5.137 | 55.0693 | 282.892 | 24 | 57.5 | 4 | 51.5 | 645.7808 | 1584.4992 | 69.5995 | 2.4536 | 0.88815 | 110 | 94.2059 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.2609 | 113.6981
CID=-28776431 | 24 | 60 | 0 | 4 | 54 | 10.8 | 1.7302 | 146.5045 | 30.6472 | 277.8855 | 435.9703 | 415.8906 | 26771.2519 | 2.1907 | 0.031784 | 4.7143 | 64.1313 | 302.3331 | 24 | 60 | 4 | 54 | 645.7808 | 1681.7842 | 72.4903 | 2.6043 | 0.89843 | 110 | 108.4531 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.9849 | 126.9601
CID=-411857982 | 24 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7302 | 146.5045 | 30.6472 | 281.8586 | 437.1743 | 415.8906 | 27427.4582 | 2.2548 | 0.035064 | 4.335 | 69.7161 | 302.2167 | 24 | 62.5 | 4 | 56.5 | 645.7808 | 1783.5096 | 75.3724 | 2.7618 | 0.90303 | 110 | 117.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4735 | 126.9601
CID=-1715819897 | 24 | 65 | 0 | 4 | 59 | 11.8 | 1.7302 | 146.5045 | 30.6472 | 285.881 | 438.355 | 415.8906 | 28150.4531 | 2.3851 | 0.039437 | 4.0098 | 77.3333 | 310.0903 | 24 | 65 | 4 | 59 | 645.7808 | 1889.8218 | 78.1768 | 2.9264 | 0.90777 | 110 | 129.4329 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.832 | 126.9601
CID=-2098901448 | 24 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7302 | 146.5045 | 30.6472 | 289.9569 | 439.5127 | 415.8906 | 28828.8556 | 2.515 | 0.044243 | 3.7153 | 85.2483 | 316.7267 | 24 | 67.5 | 4 | 61.5 | 645.7808 | 2000.8736 | 80.9758 | 3.0984 | 0.9113 | 110 | 142.1281 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.542 | 126.9602
CID=892103933 | 24 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7302 | 146.5045 | 30.6472 | 294.074 | 440.6434 | 415.8906 | 29440.0046 | 2.6066 | 0.049056 | 3.4348 | 92.4436 | 317.5265 | 24 | 69.99 | 4 | 63.99 | 645.7808 | 2116.3519 | 83.8489 | 3.2772 | 0.91362 | 110 | 153.7338 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68.6833 | 126.9601
CID=-548045269 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-447288720 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1495228557 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1213451822 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-346539342 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1239747575 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-411850811 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1715812726 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2098894277 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=892111104 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=509029553 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-794932362 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1178013913 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1812991468 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1275191630 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-28770285 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-411851836 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1715813751 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2098895302 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=892110079 | 27 | 42.5 | 0 | 4 | 36.5 | 7.3 | 1.7292 | 145.9744 | 33.5123 | 251.2145 | 426.563 | 417.481 | 19203.0066 | 1.3093 | 0.01152 | 11.014 | 19.7651 | 217.6934 | 27 | 42.5 | 4 | 36.5 | 705.9244 | 1086.4865 | 51.7752 | 1.5391 | 0.77466 | 86.2897 | 38.7651 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.346 | 41.1277
CID=509028528 | 27 | 45 | 0 | 4 | 39 | 7.8 | 1.7292 | 145.9744 | 33.5123 | 254.9187 | 427.9352 | 417.481 | 19589.9641 | 1.3812 | 0.012986 | 9.6177 | 23.346 | 224.5338 | 27 | 45 | 4 | 39 | 705.9244 | 1159.9242 | 54.7205 | 1.6431 | 0.79541 | 107.3889 | 44.5943 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.5416 | 48.8753
CID=-794933387 | 27 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7292 | 145.9744 | 33.5123 | 258.655 | 429.2823 | 417.481 | 20741.8858 | 1.5259 | 0.015045 | 8.5359 | 28.3925 | 242.3552 | 27 | 47.5 | 4 | 41.5 | 705.9244 | 1237.0237 | 57.6154 | 1.7523 | 0.81971 | 106.5422 | 52.6259 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4578 | 20.0626 | 58.5775
CID=-1178014938 | 27 | 50 | 0 | 4 | 44 | 8.8 | 1.7292 | 145.9744 | 33.5123 | 262.425 | 430.6045 | 417.481 | 21625.7392 | 1.5975 | 0.016871 | 7.6277 | 32.4734 | 247.6972 | 27 | 50 | 4 | 44 | 705.9244 | 1317.9055 | 60.506 | 1.8669 | 0.83585 | 108.4119 | 59.0275 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9703 | 23.8529 | 69.1973
CID=1812990443 | 27 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7292 | 145.9744 | 33.5123 | 266.2308 | 431.902 | 417.481 | 22495.2241 | 1.6689 | 0.018822 | 6.8926 | 36.6221 | 252.4209 | 27 | 52.5 | 4 | 46.5 | 705.9244 | 1402.6932 | 63.325 | 1.987 | 0.8496 | 106.3227 | 65.4915 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.4146 | 80.6498
CID=193455276 | 27 | 55 | 0 | 4 | 49 | 9.8 | 1.7292 | 145.9744 | 33.5123 | 270.0745 | 433.1751 | 417.481 | 23336.3246 | 1.7401 | 0.020952 | 6.2638 | 40.951 | 256.5088 | 27 | 55 | 4 | 49 | 705.9244 | 1491.5141 | 66.138 | 2.1129 | 0.86156 | 108.174 | 72.2165 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.1505 | 89.9111
CID=92698727 | 27 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7292 | 145.9744 | 33.5123 | 273.9586 | 434.4241 | 417.481 | 24263.0867 | 1.8839 | 0.023995 | 5.715 | 47.31 | 270.3764 | 27 | 57.5 | 4 | 51.5 | 705.9244 | 1584.4992 | 68.9761 | 2.2446 | 0.87554 | 109 | 82.0981 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.5589 | 102.1624
CID=-1493588190 | 27 | 60 | 0 | 4 | 54 | 10.8 | 1.7292 | 145.9744 | 33.5123 | 277.8855 | 435.6491 | 417.481 | 25141.2628 | 2.0273 | 0.027364 | 5.2381 | 54.0258 | 282.995 | 27 | 60 | 4 | 54 | 705.9244 | 1681.7842 | 71.7941 | 2.3824 | 0.88669 | 109.6844 | 92.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1556 | 40.7067 | 116.2504
CID=1215092189 | 27 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7292 | 145.9744 | 33.5123 | 281.8586 | 436.8505 | 417.481 | 26137.3195 | 2.2427 | 0.032048 | 4.7961 | 63.418 | 304.1608 | 27 | 62.5 | 4 | 56.5 | 705.9244 | 1783.5096 | 74.7049 | 2.5265 | 0.89776 | 110 | 107.327 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5787 | 126.9601
CID=1114335640 | 27 | 65 | 0 | 4 | 59 | 11.8 | 1.7292 | 145.9744 | 33.5123 | 285.881 | 438.0286 | 417.481 | 26951.6955 | 2.3851 | 0.036372 | 4.4046 | 71.2628 | 313.8841 | 27 | 65 | 4 | 59 | 705.9244 | 1889.8218 | 77.5964 | 2.6771 | 0.90413 | 110 | 119.7538 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.2946 | 126.9601
CID=1013579091 | 27 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7292 | 145.9744 | 33.5123 | 289.9569 | 439.1838 | 417.481 | 27800.049 | 2.5996 | 0.042049 | 4.0666 | 81.5203 | 331.5113 | 27 | 67.5 | 4 | 61.5 | 705.9244 | 2000.8736 | 80.4259 | 2.8344 | 0.90979 | 110 | 136.1386 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.4575 | 126.9602
CID=-572707826 | 27 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7292 | 145.9744 | 33.5123 | 294.074 | 440.3118 | 417.481 | 28507.6844 | 2.741 | 0.047383 | 3.7519 | 90.1573 | 338.2612 | 27 | 69.99 | 4 | 63.99 | 705.9244 | 2116.3519 | 83.2929 | 2.998 | 0.91296 | 110 | 150.0399 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.2881 | 126.9602
CID=-1214742448 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-475430537 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=828531378 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1977777056 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1013228325 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1493589215 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1215091164 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1114334615 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1013578066 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-572708851 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2135971528 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2035214979 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1934458430 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=193453230 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=92696681 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1493590236 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1215090143 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1114333594 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1013577045 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-572709872 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2135970507 | 30 | 45 | 0 | 4 | 39 | 7.8 | 1.7283 | 145.3777 | 36.5977 | 254.9187 | 427.6403 | 419.0371 | 19124.479 | 1.4246 | 0.011913 | 11.4078 | 20.4954 | 233.8065 | 30 | 45 | 4 | 39 | 770.1963 | 1159.9242 | 54.0358 | 1.506 | 0.77916 | 82.5881 | 39.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.2285 | 35.2368
CID=2035213958 | 30 | 47.5 | 0 | 4 | 41.5 | 8.3 | 1.7283 | 145.3777 | 36.5977 | 258.655 | 428.9849 | 419.0371 | 19276.1377 | 1.5029 | 0.01345 | 9.9663 | 24.1852 | 241.0369 | 30 | 47.5 | 4 | 41.5 | 770.1963 | 1237.0237 | 56.9205 | 1.6061 | 0.79982 | 105.0687 | 45.9423 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.3626 | 49.4867
CID=1934457409 | 30 | 50 | 0 | 4 | 44 | 8.8 | 1.7283 | 145.3777 | 36.5977 | 262.425 | 430.3047 | 419.0371 | 20226.7646 | 1.581 | 0.015193 | 8.7764 | 28.2116 | 247.5968 | 30 | 50 | 4 | 44 | 770.1963 | 1317.9055 | 59.8529 | 1.7111 | 0.81893 | 108.2727 | 52.3406 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.758 | 59.6018
CID=193452205 | 30 | 52.5 | 0 | 4 | 46.5 | 9.3 | 1.7283 | 145.3777 | 36.5977 | 266.2308 | 431.5997 | 419.0371 | 21310.281 | 1.7381 | 0.017673 | 7.8125 | 33.9957 | 265.591 | 30 | 52.5 | 4 | 46.5 | 770.1963 | 1402.6932 | 62.7866 | 1.8212 | 0.84118 | 110 | 61.403 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.5286 | 70.4551
CID=92695656 | 30 | 55 | 0 | 4 | 49 | 9.8 | 1.7283 | 145.3777 | 36.5977 | 270.0745 | 432.8703 | 419.0371 | 22164.5073 | 1.8158 | 0.019784 | 7.0406 | 38.418 | 270.4844 | 30 | 55 | 4 | 49 | 770.1963 | 1491.5141 | 65.619 | 1.9365 | 0.85483 | 108.5473 | 68.2825 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6318 | 28.2091 | 82.2635
CID=-1493591261 | 30 | 57.5 | 0 | 4 | 51.5 | 10.3 | 1.7283 | 145.3777 | 36.5977 | 273.9586 | 434.1168 | 419.0371 | 22992.8075 | 1.8933 | 0.022055 | 6.3962 | 42.9446 | 274.6807 | 30 | 57.5 | 4 | 51.5 | 770.1963 | 1584.4992 | 68.4107 | 2.0573 | 0.86636 | 108.6752 | 75.3125 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.0207 | 95.0594
CID=1215089118 | 30 | 60 | 0 | 4 | 54 | 10.8 | 1.7283 | 145.3777 | 36.5977 | 277.8855 | 435.3393 | 419.0371 | 23918.6184 | 2.0497 | 0.025326 | 5.8272 | 49.6487 | 289.3137 | 30 | 60 | 4 | 54 | 770.1963 | 1681.7842 | 71.2468 | 2.1836 | 0.87979 | 109.4325 | 85.74 | 0 | 0 | 0 | 0 | 0 | 0 | 7.8373 | 36.1156 | 104.3567
CID=1114332569 | 30 | 62.5 | 0 | 4 | 56.5 | 11.3 | 1.7283 | 145.3777 | 36.5977 | 281.8586 | 436.5383 | 419.0371 | 24778.0014 | 2.2057 | 0.028939 | 5.3363 | 56.7008 | 302.5706 | 30 | 62.5 | 4 | 56.5 | 770.1963 | 1783.5096 | 74.0558 | 2.3157 | 0.89031 | 110 | 96.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2449 | 118.617
CID=1013576020 | 30 | 65 | 0 | 4 | 59 | 11.8 | 1.7283 | 145.3777 | 36.5977 | 285.881 | 437.7139 | 419.0371 | 25641.4003 | 2.3611 | 0.033081 | 4.8773 | 64.4625 | 314.4005 | 30 | 65 | 4 | 59 | 770.1963 | 1889.8218 | 76.9609 | 2.4537 | 0.89874 | 110 | 108.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.3217 | 126.9601
CID=-572710897 | 30 | 67.5 | 0 | 4 | 61.5 | 12.3 | 1.7283 | 145.3777 | 36.5977 | 289.9569 | 438.8665 | 419.0371 | 26589.8336 | 2.595 | 0.038642 | 4.4751 | 74.8513 | 334.9636 | 30 | 67.5 | 4 | 61.5 | 770.1963 | 2000.8736 | 79.8524 | 2.5979 | 0.9064 | 110 | 125.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.7777 | 126.9602
CID=2135969482 | 30 | 69.99 | 0 | 4 | 63.99 | 12.798 | 1.7283 | 145.3777 | 36.5977 | 294.074 | 439.9919 | 419.0371 | 27215.3843 | 2.6707 | 0.042767 | 4.1102 | 81.1982 | 333.7372 | 30 | 69.99 | 4 | 63.99 | 770.1963 | 2116.3519 | 82.746 | 2.7478 | 0.90965 | 110 | 135.6219 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 11.7699 | 32.0031
[37 empty] | 13.601 | 37.5469
[37 empty] | 15.8508 | 41.9673
[37 empty] | 18.3412 | 47.8386
[37 empty] | 21.1691 | 53.5948
[37 empty] | 24.0585 | 58.447
[37 empty] | 27.8402 | 58.803
[37 empty] | 31.3546 | 58.5759
[37 empty] | 36.422 | 57.9392
[37 empty] | 41.4958 | 58.3942
[37 empty] | 48.0343 | 58.9531
[37 empty] | 55.3815 | 56.5848
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.4538 | 12.3991
[37 empty] | 5.9439 | 15.6403
[37 empty] | 7.3298 | 19.5445
[37 empty] | 8.5649 | 23.9769
[37 empty] | 9.993 | 27.8065
[37 empty] | 12.1391 | 33.2299
[37 empty] | 14.0304 | 39.1019
[37 empty] | 16.4121 | 45.5079
[37 empty] | 19.032 | 50.1624
[37 empty] | 21.8538 | 56.7855
[37 empty] | 24.9272 | 62.9919
[37 empty] | 28.6206 | 65.6702
[37 empty] | 32.3085 | 65.9405
[37 empty] | 36.6126 | 65.8016
[37 empty] | 42.4028 | 65.639
[37 empty] | 47.9875 | 66.1098
[37 empty] | 55.8685 | 66.0993
[37 empty] | 63.1387 | 63.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.8776 | 10.3709
[37 empty] | 5.9672 | 16.0914
[37 empty] | 7.3549 | 20.1873
[37 empty] | 8.9222 | 24.8293
[37 empty] | 10.5321 | 29.3656
[37 empty] | 12.3102 | 34.4149
[37 empty] | 14.7558 | 40.7191
[37 empty] | 16.9978 | 47.3518
[37 empty] | 19.6774 | 52.6566
[37 empty] | 22.5308 | 59.4656
[37 empty] | 25.7566 | 66.4236
[37 empty] | 29.1758 | 73.3333
[37 empty] | 33.425 | 73.7137
[37 empty] | 37.4523 | 73.3536
[37 empty] | 42.9142 | 73.3866
[37 empty] | 49.0108 | 74.0486
[37 empty] | 55.1264 | 74.5178
[37 empty] | 64.4822 | 74.5276
[37 empty] | 71.7723 | 70.7774
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.453 | 16.4601
[37 empty] | 7.6696 | 20.8178
[37 empty] | 9.2176 | 25.6674
[37 empty] | 10.7286 | 31.091
[37 empty] | 12.814 | 35.6449
[37 empty] | 15.1569 | 42.1821
[37 empty] | 17.5255 | 49.1571
[37 empty] | 20.3432 | 56.7809
[37 empty] | 23.3062 | 62.1448
[37 empty] | 26.4924 | 69.9107
[37 empty] | 30.2611 | 77.2504
[37 empty] | 34.2819 | 82.4485
[37 empty] | 39.1102 | 82.9524
[37 empty] | 43.5036 | 82.5148
[37 empty] | 49.8837 | 81.3364
[37 empty] | 56.269 | 82.5395
[37 empty] | 63.1967 | 82.9402
[37 empty] | 73.7545 | 82.3271
[37 empty] | 81.6054 | 79.3179
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.2395 | 17.0303
[37 empty] | 7.8059 | 21.4254
[37 empty] | 9.5793 | 26.4523
[37 empty] | 11.3834 | 32.0983
[37 empty] | 13.1276 | 36.8384
[37 empty] | 15.3536 | 43.5534
[37 empty] | 18.2962 | 51.0495
[37 empty] | 20.9887 | 58.877
[37 empty] | 24.0589 | 65.4577
[37 empty] | 27.3282 | 72.9534
[37 empty] | 31.2318 | 81.2868
[37 empty] | 35.4207 | 89.2568
[37 empty] | 40.004 | 91.6597
[37 empty] | 44.8066 | 92.0158
[37 empty] | 50.0122 | 91.8833
[37 empty] | 57.2677 | 91.0918
[37 empty] | 64.1843 | 92.3763
[37 empty] | 72.1709 | 92.7477
[37 empty] | 83.791 | 92.0281
[37 empty] | 92.1977 | 88.544
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.6527 | 15.5267
[37 empty] | 7.8476 | 21.9668
[37 empty] | 9.6303 | 27.2198
[37 empty] | 11.4976 | 33.1226
[37 empty] | 13.7099 | 39.6483
[37 empty] | 16.0491 | 44.9885
[37 empty] | 18.7183 | 52.7648
[37 empty] | 21.6284 | 60.943
[37 empty] | 24.9262 | 69.8742
[37 empty] | 28.2143 | 76.0029
[37 empty] | 32.0433 | 84.9985
[37 empty] | 36.5584 | 93.5253
[37 empty] | 40.6283 | 101.9065
[37 empty] | 46.0942 | 101.9148
[37 empty] | 51.0502 | 101.2467
[37 empty] | 57.491 | 102.1367
[37 empty] | 65.2952 | 101.6651
[37 empty] | 72.7779 | 102.0387
[37 empty] | 82.0777 | 102.54
[37 empty] | 94.1756 | 100.8854
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.4251 | 11.1654
[37 empty] | 8.626 | 22.4048
[37 empty] | 10.0707 | 27.9674
[37 empty] | 12.1238 | 34.0823
[37 empty] | 14.0916 | 40.8543
[37 empty] | 16.1927 | 46.3828
[37 empty] | 19.1571 | 54.3477
[37 empty] | 22.4325 | 63.1245
[37 empty] | 25.6165 | 72.2476
[37 empty] | 29.0856 | 80.3364
[37 empty] | 32.953 | 88.4142
[37 empty] | 37.6354 | 98.2926
[37 empty] | 41.9298 | 107.3472
[37 empty] | 47.1667 | 112.8128
[37 empty] | 53.1496 | 113.4849
[37 empty] | 58.3888 | 112.6148
[37 empty] | 65.8924 | 112.3073
[37 empty] | 73.9935 | 113.0467
[37 empty] | 82.0539 | 113.39
[37 empty] | 92.802 | 113.8644
[37 empty] | 105.0584 | 111.9723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.5417 | 22.8585
[37 empty] | 10.1644 | 28.6739
[37 empty] | 12.3537 | 34.9853
[37 empty] | 14.739 | 42.0253
[37 empty] | 17.1012 | 49.1455
[37 empty] | 19.7427 | 55.9665
[37 empty] | 22.991 | 65.1
[37 empty] | 26.3835 | 74.5803
[37 empty] | 30.2032 | 84.9212
[37 empty] | 33.7881 | 91.8398
[37 empty] | 38.4962 | 102.1436
[37 empty] | 43.1636 | 112.1825
[37 empty] | 48.3056 | 122.2097
[37 empty] | 54.1646 | 124.2598
[37 empty] | 60.3101 | 124.6468
[37 empty] | 66.4309 | 124.7604
[37 empty] | 75.0155 | 124.137
[37 empty] | 83.3904 | 125.2286
[37 empty] | 92.0266 | 125.5368
[37 empty] | 104.302 | 124.8224
[37 empty] | 116.6406 | 123.8195
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.8546 | 22.6697
[37 empty] | 10.2198 | 29.301
[37 empty] | 12.4687 | 35.877
[37 empty] | 14.9305 | 43.1989
[37 empty] | 17.2579 | 51.2247
[37 empty] | 20.0505 | 57.5838
[37 empty] | 23.6818 | 66.9124
[37 empty] | 27.2008 | 77.061
[37 empty] | 30.9216 | 87.5743
[37 empty] | 34.7915 | 97.396
[37 empty] | 39.4856 | 105.939
[37 empty] | 44.3087 | 117.1977
[37 empty] | 49.6486 | 126.9601
[37 empty] | 54.9361 | 126.9601
[37 empty] | 61.5619 | 126.9602
[37 empty] | 67.5145 | 126.9601
[37 empty] | 74.8839 | 126.9602
[37 empty] | 84.545 | 126.9602
[37 empty] | 93.4753 | 126.9601
[37 empty] | 102.6563 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.795 | 16.7083
[37 empty] | 11.1128 | 29.8031
[37 empty] | 13.0293 | 36.7366
[37 empty] | 15.6766 | 44.2749
[37 empty] | 18.1723 | 52.5653
[37 empty] | 20.8063 | 59.3536
[37 empty] | 24.0173 | 68.7122
[37 empty] | 28.0083 | 79.3022
[37 empty] | 31.8335 | 90.1739
[37 empty] | 36.2059 | 102.0198
[37 empty] | 40.3372 | 109.7483
[37 empty] | 45.5194 | 121.423
[37 empty] | 50.8145 | 126.9602
[37 empty] | 56.5802 | 126.9601
[37 empty] | 62.8856 | 126.9602
[37 empty] | 70.1201 | 126.9601
[37 empty] | 76.1762 | 126.9602
[37 empty] | 84.6298 | 126.9602
[37 empty] | 94.7107 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.3198 | 30.1197
[37 empty] | 13.0742 | 37.5319
[37 empty] | 15.7101 | 45.2884
[37 empty] | 18.4587 | 53.9129
[37 empty] | 21.4735 | 63.3068
[37 empty] | 24.7682 | 70.5569
[37 empty] | 28.93 | 81.3534
[37 empty] | 32.6346 | 92.9494
[37 empty] | 36.943 | 104.9514
[37 empty] | 41.2093 | 116.6989
[37 empty] | 46.8297 | 125.5944
[37 empty] | 51.704 | 126.9601
[37 empty] | 58.1896 | 126.9601
[37 empty] | 63.9624 | 126.9602
[37 empty] | 71.2677 | 126.9602
[37 empty] | 78.9695 | 126.9602
[37 empty] | 85.6595 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.839 | 32.3325
[37 empty] | 13.112 | 38.233
[37 empty] | 15.9579 | 46.2963
[37 empty] | 19.0416 | 55.1907
[37 empty] | 21.9546 | 64.858
[37 empty] | 25.0409 | 72.3151
[37 empty] | 28.9027 | 83.3388
[37 empty] | 33.7506 | 95.4733
[37 empty] | 38.0197 | 107.8119
[37 empty] | 42.9579 | 121.2507
[37 empty] | 47.6837 | 126.9601
[37 empty] | 53.1459 | 126.9601
[37 empty] | 59.592 | 126.9601
[37 empty] | 65.4574 | 126.9601
[37 empty] | 72.1509 | 126.9602
[37 empty] | 79.9236 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 13.5732 | 24.4855
[37 empty] | 14.0444 | 38.7928
[37 empty] | 16.5838 | 47.2501
[37 empty] | 19.8198 | 56.3689
[37 empty] | 22.9995 | 66.3301
[37 empty] | 26.2319 | 76.5263
[37 empty] | 29.9299 | 85.388
[37 empty] | 34.5049 | 97.772
[37 empty] | 38.7568 | 110.8709
[37 empty] | 43.7196 | 124.4588
[37 empty] | 48.373 | 126.9601
[37 empty] | 54.7306 | 126.9601
[37 empty] | 60.4786 | 126.9602
[37 empty] | 67.0331 | 126.9602
[37 empty] | 74.1546 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 15.4516 | 39.1373
[37 empty] | 16.6006 | 48.1204
[37 empty] | 19.7334 | 57.4863
[37 empty] | 22.8929 | 67.8348
[37 empty] | 26.2397 | 79.0043
[37 empty] | 29.8629 | 87.3441
[37 empty] | 34.4237 | 99.9239
[37 empty] | 40.2609 | 113.6981
[37 empty] | 44.9849 | 126.9601
[37 empty] | 50.4735 | 126.9601
[37 empty] | 55.832 | 126.9601
[37 empty] | 61.542 | 126.9602
[37 empty] | 68.6833 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 16.346 | 41.1277
[37 empty] | 16.5416 | 48.8753
[37 empty] | 20.0626 | 58.5775
[37 empty] | 23.8529 | 69.1973
[37 empty] | 27.4146 | 80.6498
[37 empty] | 31.1505 | 89.9111
[37 empty] | 35.5589 | 102.1624
[37 empty] | 40.7067 | 116.2504
[37 empty] | 45.5787 | 126.9601
[37 empty] | 51.2946 | 126.9601
[37 empty] | 56.4575 | 126.9602
[37 empty] | 63.2881 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 17.2285 | 35.2368
[37 empty] | 17.3626 | 49.4867
[37 empty] | 20.758 | 59.6018
[37 empty] | 24.5286 | 70.4551
[37 empty] | 28.2091 | 82.2635
[37 empty] | 32.0207 | 95.0594
[37 empty] | 36.1156 | 104.3567
[37 empty] | 41.2449 | 118.617
[37 empty] | 47.3217 | 126.9601
[37 empty] | 52.7777 | 126.9602
[37 empty] | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 11.7699 | 32.0031
[37 empty] | 13.601 | 37.5469
[37 empty] | 15.8508 | 41.9673
[37 empty] | 18.3412 | 47.8386
[37 empty] | 21.1691 | 53.5948
[37 empty] | 24.0585 | 58.447
[37 empty] | 27.8402 | 58.803
[37 empty] | 31.3546 | 58.5759
[37 empty] | 36.422 | 57.9392
[37 empty] | 41.4958 | 58.3942
[37 empty] | 48.0343 | 58.9531
[37 empty] | 55.3815 | 56.5848
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.4538 | 12.3991
[37 empty] | 5.9439 | 15.6403
[37 empty] | 7.3298 | 19.5445
[37 empty] | 8.5649 | 23.9769
[37 empty] | 9.993 | 27.8065
[37 empty] | 12.1391 | 33.2299
[37 empty] | 14.0304 | 39.1019
[37 empty] | 16.4121 | 45.5079
[37 empty] | 19.032 | 50.1624
[37 empty] | 21.8538 | 56.7855
[37 empty] | 24.9272 | 62.9919
[37 empty] | 28.6206 | 65.6702
[37 empty] | 32.3085 | 65.9405
[37 empty] | 36.6126 | 65.8016
[37 empty] | 42.4028 | 65.639
[37 empty] | 47.9875 | 66.1098
[37 empty] | 55.8685 | 66.0993
[37 empty] | 63.1387 | 63.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.8776 | 10.3709
[37 empty] | 5.9672 | 16.0914
[37 empty] | 7.3549 | 20.1873
[37 empty] | 8.9222 | 24.8293
[37 empty] | 10.5321 | 29.3656
[37 empty] | 12.3102 | 34.4149
[37 empty] | 14.7558 | 40.7191
[37 empty] | 16.9978 | 47.3518
[37 empty] | 19.6774 | 52.6566
[37 empty] | 22.5308 | 59.4656
[37 empty] | 25.7566 | 66.4236
[37 empty] | 29.1758 | 73.3333
[37 empty] | 33.425 | 73.7137
[37 empty] | 37.4523 | 73.3536
[37 empty] | 42.9142 | 73.3866
[37 empty] | 49.0108 | 74.0486
[37 empty] | 55.1264 | 74.5178
[37 empty] | 64.4822 | 74.5276
[37 empty] | 71.7723 | 70.7774
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.453 | 16.4601
[37 empty] | 7.6696 | 20.8178
[37 empty] | 9.2176 | 25.6674
[37 empty] | 10.7286 | 31.091
[37 empty] | 12.814 | 35.6449
[37 empty] | 15.1569 | 42.1821
[37 empty] | 17.5255 | 49.1571
[37 empty] | 20.3432 | 56.7809
[37 empty] | 23.3062 | 62.1448
[37 empty] | 26.4924 | 69.9107
[37 empty] | 30.2611 | 77.2504
[37 empty] | 34.2819 | 82.4485
[37 empty] | 39.1102 | 82.9524
[37 empty] | 43.5036 | 82.5148
[37 empty] | 49.8837 | 81.3364
[37 empty] | 56.269 | 82.5395
[37 empty] | 63.1967 | 82.9402
[37 empty] | 73.7545 | 82.3271
[37 empty] | 81.6054 | 79.3179
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.2395 | 17.0303
[37 empty] | 7.8059 | 21.4254
[37 empty] | 9.5793 | 26.4523
[37 empty] | 11.3834 | 32.0983
[37 empty] | 13.1276 | 36.8384
[37 empty] | 15.3536 | 43.5534
[37 empty] | 18.2962 | 51.0495
[37 empty] | 20.9887 | 58.877
[37 empty] | 24.0589 | 65.4577
[37 empty] | 27.3282 | 72.9534
[37 empty] | 31.2318 | 81.2868
[37 empty] | 35.4207 | 89.2568
[37 empty] | 40.004 | 91.6597
[37 empty] | 44.8066 | 92.0158
[37 empty] | 50.0122 | 91.8833
[37 empty] | 57.2677 | 91.0918
[37 empty] | 64.1843 | 92.3763
[37 empty] | 72.1709 | 92.7477
[37 empty] | 83.791 | 92.0281
[37 empty] | 92.1977 | 88.544
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.6527 | 15.5267
[37 empty] | 7.8476 | 21.9668
[37 empty] | 9.6303 | 27.2198
[37 empty] | 11.4976 | 33.1226
[37 empty] | 13.7099 | 39.6483
[37 empty] | 16.0491 | 44.9885
[37 empty] | 18.7183 | 52.7648
[37 empty] | 21.6284 | 60.943
[37 empty] | 24.9262 | 69.8742
[37 empty] | 28.2143 | 76.0029
[37 empty] | 32.0433 | 84.9985
[37 empty] | 36.5584 | 93.5253
[37 empty] | 40.6283 | 101.9065
[37 empty] | 46.0942 | 101.9148
[37 empty] | 51.0502 | 101.2467
[37 empty] | 57.491 | 102.1367
[37 empty] | 65.2952 | 101.6651
[37 empty] | 72.7779 | 102.0387
[37 empty] | 82.0777 | 102.54
[37 empty] | 94.1756 | 100.8854
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.4251 | 11.1654
[37 empty] | 8.626 | 22.4048
[37 empty] | 10.0707 | 27.9674
[37 empty] | 12.1238 | 34.0823
[37 empty] | 14.0916 | 40.8543
[37 empty] | 16.1927 | 46.3828
[37 empty] | 19.1571 | 54.3477
[37 empty] | 22.4325 | 63.1245
[37 empty] | 25.6165 | 72.2476
[37 empty] | 29.0856 | 80.3364
[37 empty] | 32.953 | 88.4142
[37 empty] | 37.6354 | 98.2926
[37 empty] | 41.9298 | 107.3472
[37 empty] | 47.1667 | 112.8128
[37 empty] | 53.1496 | 113.4849
[37 empty] | 58.3888 | 112.6148
[37 empty] | 65.8924 | 112.3073
[37 empty] | 73.9935 | 113.0467
[37 empty] | 82.0539 | 113.39
[37 empty] | 92.802 | 113.8644
[37 empty] | 105.0584 | 111.9723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.5417 | 22.8585
[37 empty] | 10.1644 | 28.6739
[37 empty] | 12.3537 | 34.9853
[37 empty] | 14.739 | 42.0253
[37 empty] | 17.1012 | 49.1455
[37 empty] | 19.7427 | 55.9665
[37 empty] | 22.991 | 65.1
[37 empty] | 26.3835 | 74.5803
[37 empty] | 30.2032 | 84.9212
[37 empty] | 33.7881 | 91.8398
[37 empty] | 38.4962 | 102.1436
[37 empty] | 43.1636 | 112.1825
[37 empty] | 48.3056 | 122.2097
[37 empty] | 54.1646 | 124.2598
[37 empty] | 60.3101 | 124.6468
[37 empty] | 66.4309 | 124.7604
[37 empty] | 75.0155 | 124.137
[37 empty] | 83.3904 | 125.2286
[37 empty] | 92.0266 | 125.5368
[37 empty] | 104.302 | 124.8224
[37 empty] | 116.6406 | 123.8195
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.8546 | 22.6697
[37 empty] | 10.2198 | 29.301
[37 empty] | 12.4687 | 35.877
[37 empty] | 14.9305 | 43.1989
[37 empty] | 17.2579 | 51.2247
[37 empty] | 20.0505 | 57.5838
[37 empty] | 23.6818 | 66.9124
[37 empty] | 27.2008 | 77.061
[37 empty] | 30.9216 | 87.5743
[37 empty] | 34.7915 | 97.396
[37 empty] | 39.4856 | 105.939
[37 empty] | 44.3087 | 117.1977
[37 empty] | 49.6486 | 126.9601
[37 empty] | 54.9361 | 126.9601
[37 empty] | 61.5619 | 126.9602
[37 empty] | 67.5145 | 126.9601
[37 empty] | 74.8839 | 126.9602
[37 empty] | 84.545 | 126.9602
[37 empty] | 93.4753 | 126.9601
[37 empty] | 102.6563 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.795 | 16.7083
[37 empty] | 11.1128 | 29.8031
[37 empty] | 13.0293 | 36.7366
[37 empty] | 15.6766 | 44.2749
[37 empty] | 18.1723 | 52.5653
[37 empty] | 20.8063 | 59.3536
[37 empty] | 24.0173 | 68.7122
[37 empty] | 28.0083 | 79.3022
[37 empty] | 31.8335 | 90.1739
[37 empty] | 36.2059 | 102.0198
[37 empty] | 40.3372 | 109.7483
[37 empty] | 45.5194 | 121.423
[37 empty] | 50.8145 | 126.9602
[37 empty] | 56.5802 | 126.9601
[37 empty] | 62.8856 | 126.9602
[37 empty] | 70.1201 | 126.9601
[37 empty] | 76.1762 | 126.9602
[37 empty] | 84.6298 | 126.9602
[37 empty] | 94.7107 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.3198 | 30.1197
[37 empty] | 13.0742 | 37.5319
[37 empty] | 15.7101 | 45.2884
[37 empty] | 18.4587 | 53.9129
[37 empty] | 21.4735 | 63.3068
[37 empty] | 24.7682 | 70.5569
[37 empty] | 28.93 | 81.3534
[37 empty] | 32.6346 | 92.9494
[37 empty] | 36.943 | 104.9514
[37 empty] | 41.2093 | 116.6989
[37 empty] | 46.8297 | 125.5944
[37 empty] | 51.704 | 126.9601
[37 empty] | 58.1896 | 126.9601
[37 empty] | 63.9624 | 126.9602
[37 empty] | 71.2677 | 126.9602
[37 empty] | 78.9695 | 126.9602
[37 empty] | 85.6595 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.839 | 32.3325
[37 empty] | 13.112 | 38.233
[37 empty] | 15.9579 | 46.2963
[37 empty] | 19.0416 | 55.1907
[37 empty] | 21.9546 | 64.858
[37 empty] | 25.0409 | 72.3151
[37 empty] | 28.9027 | 83.3388
[37 empty] | 33.7506 | 95.4733
[37 empty] | 38.0197 | 107.8119
[37 empty] | 42.9579 | 121.2507
[37 empty] | 47.6837 | 126.9601
[37 empty] | 53.1459 | 126.9601
[37 empty] | 59.592 | 126.9601
[37 empty] | 65.4574 | 126.9601
[37 empty] | 72.1509 | 126.9602
[37 empty] | 79.9236 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 13.5732 | 24.4855
[37 empty] | 14.0444 | 38.7928
[37 empty] | 16.5838 | 47.2501
[37 empty] | 19.8198 | 56.3689
[37 empty] | 22.9995 | 66.3301
[37 empty] | 26.2319 | 76.5263
[37 empty] | 29.9299 | 85.388
[37 empty] | 34.5049 | 97.772
[37 empty] | 38.7568 | 110.8709
[37 empty] | 43.7196 | 124.4588
[37 empty] | 48.373 | 126.9601
[37 empty] | 54.7306 | 126.9601
[37 empty] | 60.4786 | 126.9602
[37 empty] | 67.0331 | 126.9602
[37 empty] | 74.1546 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 15.4516 | 39.1373
[37 empty] | 16.6006 | 48.1204
[37 empty] | 19.7334 | 57.4863
[37 empty] | 22.8929 | 67.8348
[37 empty] | 26.2397 | 79.0043
[37 empty] | 29.8629 | 87.3441
[37 empty] | 34.4237 | 99.9239
[37 empty] | 40.2609 | 113.6981
[37 empty] | 44.9849 | 126.9601
[37 empty] | 50.4735 | 126.9601
[37 empty] | 55.832 | 126.9601
[37 empty] | 61.542 | 126.9602
[37 empty] | 68.6833 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 16.346 | 41.1277
[37 empty] | 16.5416 | 48.8753
[37 empty] | 20.0626 | 58.5775
[37 empty] | 23.8529 | 69.1973
[37 empty] | 27.4146 | 80.6498
[37 empty] | 31.1505 | 89.9111
[37 empty] | 35.5589 | 102.1624
[37 empty] | 40.7067 | 116.2504
[37 empty] | 45.5787 | 126.9601
[37 empty] | 51.2946 | 126.9601
[37 empty] | 56.4575 | 126.9602
[37 empty] | 63.2881 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 17.2285 | 35.2368
[37 empty] | 17.3626 | 49.4867
[37 empty] | 20.758 | 59.6018
[37 empty] | 24.5286 | 70.4551
[37 empty] | 28.2091 | 82.2635
[37 empty] | 32.0207 | 95.0594
[37 empty] | 36.1156 | 104.3567
[37 empty] | 41.2449 | 118.617
[37 empty] | 47.3217 | 126.9601
[37 empty] | 52.7777 | 126.9602
[37 empty] | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 11.7699 | 32.0031
[37 empty] | 13.601 | 37.5469
[37 empty] | 15.8508 | 41.9673
[37 empty] | 18.3412 | 47.8386
[37 empty] | 21.1691 | 53.5948
[37 empty] | 24.0585 | 58.447
[37 empty] | 27.8402 | 58.803
[37 empty] | 31.3546 | 58.5759
[37 empty] | 36.422 | 57.9392
[37 empty] | 41.4958 | 58.3942
[37 empty] | 48.0343 | 58.9531
[37 empty] | 55.3815 | 56.5848
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.4538 | 12.3991
[37 empty] | 5.9439 | 15.6403
[37 empty] | 7.3298 | 19.5445
[37 empty] | 8.5649 | 23.9769
[37 empty] | 9.993 | 27.8065
[37 empty] | 12.1391 | 33.2299
[37 empty] | 14.0304 | 39.1019
[37 empty] | 16.4121 | 45.5079
[37 empty] | 19.032 | 50.1624
[37 empty] | 21.8538 | 56.7855
[37 empty] | 24.9272 | 62.9919
[37 empty] | 28.6206 | 65.6702
[37 empty] | 32.3085 | 65.9405
[37 empty] | 36.6126 | 65.8016
[37 empty] | 42.4028 | 65.639
[37 empty] | 47.9875 | 66.1098
[37 empty] | 55.8685 | 66.0993
[37 empty] | 63.1387 | 63.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.8776 | 10.3709
[37 empty] | 5.9672 | 16.0914
[37 empty] | 7.3549 | 20.1873
[37 empty] | 8.9222 | 24.8293
[37 empty] | 10.5321 | 29.3656
[37 empty] | 12.3102 | 34.4149
[37 empty] | 14.7558 | 40.7191
[37 empty] | 16.9978 | 47.3518
[37 empty] | 19.6774 | 52.6566
[37 empty] | 22.5308 | 59.4656
[37 empty] | 25.7566 | 66.4236
[37 empty] | 29.1758 | 73.3333
[37 empty] | 33.425 | 73.7137
[37 empty] | 37.4523 | 73.3536
[37 empty] | 42.9142 | 73.3866
[37 empty] | 49.0108 | 74.0486
[37 empty] | 55.1264 | 74.5178
[37 empty] | 64.4822 | 74.5276
[37 empty] | 71.7723 | 70.7774
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.453 | 16.4601
[37 empty] | 7.6696 | 20.8178
[37 empty] | 9.2176 | 25.6674
[37 empty] | 10.7286 | 31.091
[37 empty] | 12.814 | 35.6449
[37 empty] | 15.1569 | 42.1821
[37 empty] | 17.5255 | 49.1571
[37 empty] | 20.3432 | 56.7809
[37 empty] | 23.3062 | 62.1448
[37 empty] | 26.4924 | 69.9107
[37 empty] | 30.2611 | 77.2504
[37 empty] | 34.2819 | 82.4485
[37 empty] | 39.1102 | 82.9524
[37 empty] | 43.5036 | 82.5148
[37 empty] | 49.8837 | 81.3364
[37 empty] | 56.269 | 82.5395
[37 empty] | 63.1967 | 82.9402
[37 empty] | 73.7545 | 82.3271
[37 empty] | 81.6054 | 79.3179
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.2395 | 17.0303
[37 empty] | 7.8059 | 21.4254
[37 empty] | 9.5793 | 26.4523
[37 empty] | 11.3834 | 32.0983
[37 empty] | 13.1276 | 36.8384
[37 empty] | 15.3536 | 43.5534
[37 empty] | 18.2962 | 51.0495
[37 empty] | 20.9887 | 58.877
[37 empty] | 24.0589 | 65.4577
[37 empty] | 27.3282 | 72.9534
[37 empty] | 31.2318 | 81.2868
[37 empty] | 35.4207 | 89.2568
[37 empty] | 40.004 | 91.6597
[37 empty] | 44.8066 | 92.0158
[37 empty] | 50.0122 | 91.8833
[37 empty] | 57.2677 | 91.0918
[37 empty] | 64.1843 | 92.3763
[37 empty] | 72.1709 | 92.7477
[37 empty] | 83.791 | 92.0281
[37 empty] | 92.1977 | 88.544
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.6527 | 15.5267
[37 empty] | 7.8476 | 21.9668
[37 empty] | 9.6303 | 27.2198
[37 empty] | 11.4976 | 33.1226
[37 empty] | 13.7099 | 39.6483
[37 empty] | 16.0491 | 44.9885
[37 empty] | 18.7183 | 52.7648
[37 empty] | 21.6284 | 60.943
[37 empty] | 24.9262 | 69.8742
[37 empty] | 28.2143 | 76.0029
[37 empty] | 32.0433 | 84.9985
[37 empty] | 36.5584 | 93.5253
[37 empty] | 40.6283 | 101.9065
[37 empty] | 46.0942 | 101.9148
[37 empty] | 51.0502 | 101.2467
[37 empty] | 57.491 | 102.1367
[37 empty] | 65.2952 | 101.6651
[37 empty] | 72.7779 | 102.0387
[37 empty] | 82.0777 | 102.54
[37 empty] | 94.1756 | 100.8854
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.4251 | 11.1654
[37 empty] | 8.626 | 22.4048
[37 empty] | 10.0707 | 27.9674
[37 empty] | 12.1238 | 34.0823
[37 empty] | 14.0916 | 40.8543
[37 empty] | 16.1927 | 46.3828
[37 empty] | 19.1571 | 54.3477
[37 empty] | 22.4325 | 63.1245
[37 empty] | 25.6165 | 72.2476
[37 empty] | 29.0856 | 80.3364
[37 empty] | 32.953 | 88.4142
[37 empty] | 37.6354 | 98.2926
[37 empty] | 41.9298 | 107.3472
[37 empty] | 47.1667 | 112.8128
[37 empty] | 53.1496 | 113.4849
[37 empty] | 58.3888 | 112.6148
[37 empty] | 65.8924 | 112.3073
[37 empty] | 73.9935 | 113.0467
[37 empty] | 82.0539 | 113.39
[37 empty] | 92.802 | 113.8644
[37 empty] | 105.0584 | 111.9723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.5417 | 22.8585
[37 empty] | 10.1644 | 28.6739
[37 empty] | 12.3537 | 34.9853
[37 empty] | 14.739 | 42.0253
[37 empty] | 17.1012 | 49.1455
[37 empty] | 19.7427 | 55.9665
[37 empty] | 22.991 | 65.1
[37 empty] | 26.3835 | 74.5803
[37 empty] | 30.2032 | 84.9212
[37 empty] | 33.7881 | 91.8398
[37 empty] | 38.4962 | 102.1436
[37 empty] | 43.1636 | 112.1825
[37 empty] | 48.3056 | 122.2097
[37 empty] | 54.1646 | 124.2598
[37 empty] | 60.3101 | 124.6468
[37 empty] | 66.4309 | 124.7604
[37 empty] | 75.0155 | 124.137
[37 empty] | 83.3904 | 125.2286
[37 empty] | 92.0266 | 125.5368
[37 empty] | 104.302 | 124.8224
[37 empty] | 116.6406 | 123.8195
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.8546 | 22.6697
[37 empty] | 10.2198 | 29.301
[37 empty] | 12.4687 | 35.877
[37 empty] | 14.9305 | 43.1989
[37 empty] | 17.2579 | 51.2247
[37 empty] | 20.0505 | 57.5838
[37 empty] | 23.6818 | 66.9124
[37 empty] | 27.2008 | 77.061
[37 empty] | 30.9216 | 87.5743
[37 empty] | 34.7915 | 97.396
[37 empty] | 39.4856 | 105.939
[37 empty] | 44.3087 | 117.1977
[37 empty] | 49.6486 | 126.9601
[37 empty] | 54.9361 | 126.9601
[37 empty] | 61.5619 | 126.9602
[37 empty] | 67.5145 | 126.9601
[37 empty] | 74.8839 | 126.9602
[37 empty] | 84.545 | 126.9602
[37 empty] | 93.4753 | 126.9601
[37 empty] | 102.6563 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.795 | 16.7083
[37 empty] | 11.1128 | 29.8031
[37 empty] | 13.0293 | 36.7366
[37 empty] | 15.6766 | 44.2749
[37 empty] | 18.1723 | 52.5653
[37 empty] | 20.8063 | 59.3536
[37 empty] | 24.0173 | 68.7122
[37 empty] | 28.0083 | 79.3022
[37 empty] | 31.8335 | 90.1739
[37 empty] | 36.2059 | 102.0198
[37 empty] | 40.3372 | 109.7483
[37 empty] | 45.5194 | 121.423
[37 empty] | 50.8145 | 126.9602
[37 empty] | 56.5802 | 126.9601
[37 empty] | 62.8856 | 126.9602
[37 empty] | 70.1201 | 126.9601
[37 empty] | 76.1762 | 126.9602
[37 empty] | 84.6298 | 126.9602
[37 empty] | 94.7107 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.3198 | 30.1197
[37 empty] | 13.0742 | 37.5319
[37 empty] | 15.7101 | 45.2884
[37 empty] | 18.4587 | 53.9129
[37 empty] | 21.4735 | 63.3068
[37 empty] | 24.7682 | 70.5569
[37 empty] | 28.93 | 81.3534
[37 empty] | 32.6346 | 92.9494
[37 empty] | 36.943 | 104.9514
[37 empty] | 41.2093 | 116.6989
[37 empty] | 46.8297 | 125.5944
[37 empty] | 51.704 | 126.9601
[37 empty] | 58.1896 | 126.9601
[37 empty] | 63.9624 | 126.9602
[37 empty] | 71.2677 | 126.9602
[37 empty] | 78.9695 | 126.9602
[37 empty] | 85.6595 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.839 | 32.3325
[37 empty] | 13.112 | 38.233
[37 empty] | 15.9579 | 46.2963
[37 empty] | 19.0416 | 55.1907
[37 empty] | 21.9546 | 64.858
[37 empty] | 25.0409 | 72.3151
[37 empty] | 28.9027 | 83.3388
[37 empty] | 33.7506 | 95.4733
[37 empty] | 38.0197 | 107.8119
[37 empty] | 42.9579 | 121.2507
[37 empty] | 47.6837 | 126.9601
[37 empty] | 53.1459 | 126.9601
[37 empty] | 59.592 | 126.9601
[37 empty] | 65.4574 | 126.9601
[37 empty] | 72.1509 | 126.9602
[37 empty] | 79.9236 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 13.5732 | 24.4855
[37 empty] | 14.0444 | 38.7928
[37 empty] | 16.5838 | 47.2501
[37 empty] | 19.8198 | 56.3689
[37 empty] | 22.9995 | 66.3301
[37 empty] | 26.2319 | 76.5263
[37 empty] | 29.9299 | 85.388
[37 empty] | 34.5049 | 97.772
[37 empty] | 38.7568 | 110.8709
[37 empty] | 43.7196 | 124.4588
[37 empty] | 48.373 | 126.9601
[37 empty] | 54.7306 | 126.9601
[37 empty] | 60.4786 | 126.9602
[37 empty] | 67.0331 | 126.9602
[37 empty] | 74.1546 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 15.4516 | 39.1373
[37 empty] | 16.6006 | 48.1204
[37 empty] | 19.7334 | 57.4863
[37 empty] | 22.8929 | 67.8348
[37 empty] | 26.2397 | 79.0043
[37 empty] | 29.8629 | 87.3441
[37 empty] | 34.4237 | 99.9239
[37 empty] | 40.2609 | 113.6981
[37 empty] | 44.9849 | 126.9601
[37 empty] | 50.4735 | 126.9601
[37 empty] | 55.832 | 126.9601
[37 empty] | 61.542 | 126.9602
[37 empty] | 68.6833 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 16.346 | 41.1277
[37 empty] | 16.5416 | 48.8753
[37 empty] | 20.0626 | 58.5775
[37 empty] | 23.8529 | 69.1973
[37 empty] | 27.4146 | 80.6498
[37 empty] | 31.1505 | 89.9111
[37 empty] | 35.5589 | 102.1624
[37 empty] | 40.7067 | 116.2504
[37 empty] | 45.5787 | 126.9601
[37 empty] | 51.2946 | 126.9601
[37 empty] | 56.4575 | 126.9602
[37 empty] | 63.2881 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 17.2285 | 35.2368
[37 empty] | 17.3626 | 49.4867
[37 empty] | 20.758 | 59.6018
[37 empty] | 24.5286 | 70.4551
[37 empty] | 28.2091 | 82.2635
[37 empty] | 32.0207 | 95.0594
[37 empty] | 36.1156 | 104.3567
[37 empty] | 41.2449 | 118.617
[37 empty] | 47.3217 | 126.9601
[37 empty] | 52.7777 | 126.9602
[37 empty] | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 11.7699 | 32.0031
[37 empty] | 13.601 | 37.5469
[37 empty] | 15.8508 | 41.9673
[37 empty] | 18.3412 | 47.8386
[37 empty] | 21.1691 | 53.5948
[37 empty] | 24.0585 | 58.447
[37 empty] | 27.8402 | 58.803
[37 empty] | 31.3546 | 58.5759
[37 empty] | 36.422 | 57.9392
[37 empty] | 41.4958 | 58.3942
[37 empty] | 48.0343 | 58.9531
[37 empty] | 55.3815 | 56.5848
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.4538 | 12.3991
[37 empty] | 5.9439 | 15.6403
[37 empty] | 7.3298 | 19.5445
[37 empty] | 8.5649 | 23.9769
[37 empty] | 9.993 | 27.8065
[37 empty] | 12.1391 | 33.2299
[37 empty] | 14.0304 | 39.1019
[37 empty] | 16.4121 | 45.5079
[37 empty] | 19.032 | 50.1624
[37 empty] | 21.8538 | 56.7855
[37 empty] | 24.9272 | 62.9919
[37 empty] | 28.6206 | 65.6702
[37 empty] | 32.3085 | 65.9405
[37 empty] | 36.6126 | 65.8016
[37 empty] | 42.4028 | 65.639
[37 empty] | 47.9875 | 66.1098
[37 empty] | 55.8685 | 66.0993
[37 empty] | 63.1387 | 63.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.8776 | 10.3709
[37 empty] | 5.9672 | 16.0914
[37 empty] | 7.3549 | 20.1873
[37 empty] | 8.9222 | 24.8293
[37 empty] | 10.5321 | 29.3656
[37 empty] | 12.3102 | 34.4149
[37 empty] | 14.7558 | 40.7191
[37 empty] | 16.9978 | 47.3518
[37 empty] | 19.6774 | 52.6566
[37 empty] | 22.5308 | 59.4656
[37 empty] | 25.7566 | 66.4236
[37 empty] | 29.1758 | 73.3333
[37 empty] | 33.425 | 73.7137
[37 empty] | 37.4523 | 73.3536
[37 empty] | 42.9142 | 73.3866
[37 empty] | 49.0108 | 74.0486
[37 empty] | 55.1264 | 74.5178
[37 empty] | 64.4822 | 74.5276
[37 empty] | 71.7723 | 70.7774
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.453 | 16.4601
[37 empty] | 7.6696 | 20.8178
[37 empty] | 9.2176 | 25.6674
[37 empty] | 10.7286 | 31.091
[37 empty] | 12.814 | 35.6449
[37 empty] | 15.1569 | 42.1821
[37 empty] | 17.5255 | 49.1571
[37 empty] | 20.3432 | 56.7809
[37 empty] | 23.3062 | 62.1448
[37 empty] | 26.4924 | 69.9107
[37 empty] | 30.2611 | 77.2504
[37 empty] | 34.2819 | 82.4485
[37 empty] | 39.1102 | 82.9524
[37 empty] | 43.5036 | 82.5148
[37 empty] | 49.8837 | 81.3364
[37 empty] | 56.269 | 82.5395
[37 empty] | 63.1967 | 82.9402
[37 empty] | 73.7545 | 82.3271
[37 empty] | 81.6054 | 79.3179
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.2395 | 17.0303
[37 empty] | 7.8059 | 21.4254
[37 empty] | 9.5793 | 26.4523
[37 empty] | 11.3834 | 32.0983
[37 empty] | 13.1276 | 36.8384
[37 empty] | 15.3536 | 43.5534
[37 empty] | 18.2962 | 51.0495
[37 empty] | 20.9887 | 58.877
[37 empty] | 24.0589 | 65.4577
[37 empty] | 27.3282 | 72.9534
[37 empty] | 31.2318 | 81.2868
[37 empty] | 35.4207 | 89.2568
[37 empty] | 40.004 | 91.6597
[37 empty] | 44.8066 | 92.0158
[37 empty] | 50.0122 | 91.8833
[37 empty] | 57.2677 | 91.0918
[37 empty] | 64.1843 | 92.3763
[37 empty] | 72.1709 | 92.7477
[37 empty] | 83.791 | 92.0281
[37 empty] | 92.1977 | 88.544
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.6527 | 15.5267
[37 empty] | 7.8476 | 21.9668
[37 empty] | 9.6303 | 27.2198
[37 empty] | 11.4976 | 33.1226
[37 empty] | 13.7099 | 39.6483
[37 empty] | 16.0491 | 44.9885
[37 empty] | 18.7183 | 52.7648
[37 empty] | 21.6284 | 60.943
[37 empty] | 24.9262 | 69.8742
[37 empty] | 28.2143 | 76.0029
[37 empty] | 32.0433 | 84.9985
[37 empty] | 36.5584 | 93.5253
[37 empty] | 40.6283 | 101.9065
[37 empty] | 46.0942 | 101.9148
[37 empty] | 51.0502 | 101.2467
[37 empty] | 57.491 | 102.1367
[37 empty] | 65.2952 | 101.6651
[37 empty] | 72.7779 | 102.0387
[37 empty] | 82.0777 | 102.54
[37 empty] | 94.1756 | 100.8854
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.4251 | 11.1654
[37 empty] | 8.626 | 22.4048
[37 empty] | 10.0707 | 27.9674
[37 empty] | 12.1238 | 34.0823
[37 empty] | 14.0916 | 40.8543
[37 empty] | 16.1927 | 46.3828
[37 empty] | 19.1571 | 54.3477
[37 empty] | 22.4325 | 63.1245
[37 empty] | 25.6165 | 72.2476
[37 empty] | 29.0856 | 80.3364
[37 empty] | 32.953 | 88.4142
[37 empty] | 37.6354 | 98.2926
[37 empty] | 41.9298 | 107.3472
[37 empty] | 47.1667 | 112.8128
[37 empty] | 53.1496 | 113.4849
[37 empty] | 58.3888 | 112.6148
[37 empty] | 65.8924 | 112.3073
[37 empty] | 73.9935 | 113.0467
[37 empty] | 82.0539 | 113.39
[37 empty] | 92.802 | 113.8644
[37 empty] | 105.0584 | 111.9723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.5417 | 22.8585
[37 empty] | 10.1644 | 28.6739
[37 empty] | 12.3537 | 34.9853
[37 empty] | 14.739 | 42.0253
[37 empty] | 17.1012 | 49.1455
[37 empty] | 19.7427 | 55.9665
[37 empty] | 22.991 | 65.1
[37 empty] | 26.3835 | 74.5803
[37 empty] | 30.2032 | 84.9212
[37 empty] | 33.7881 | 91.8398
[37 empty] | 38.4962 | 102.1436
[37 empty] | 43.1636 | 112.1825
[37 empty] | 48.3056 | 122.2097
[37 empty] | 54.1646 | 124.2598
[37 empty] | 60.3101 | 124.6468
[37 empty] | 66.4309 | 124.7604
[37 empty] | 75.0155 | 124.137
[37 empty] | 83.3904 | 125.2286
[37 empty] | 92.0266 | 125.5368
[37 empty] | 104.302 | 124.8224
[37 empty] | 116.6406 | 123.8195
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.8546 | 22.6697
[37 empty] | 10.2198 | 29.301
[37 empty] | 12.4687 | 35.877
[37 empty] | 14.9305 | 43.1989
[37 empty] | 17.2579 | 51.2247
[37 empty] | 20.0505 | 57.5838
[37 empty] | 23.6818 | 66.9124
[37 empty] | 27.2008 | 77.061
[37 empty] | 30.9216 | 87.5743
[37 empty] | 34.7915 | 97.396
[37 empty] | 39.4856 | 105.939
[37 empty] | 44.3087 | 117.1977
[37 empty] | 49.6486 | 126.9601
[37 empty] | 54.9361 | 126.9601
[37 empty] | 61.5619 | 126.9602
[37 empty] | 67.5145 | 126.9601
[37 empty] | 74.8839 | 126.9602
[37 empty] | 84.545 | 126.9602
[37 empty] | 93.4753 | 126.9601
[37 empty] | 102.6563 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.795 | 16.7083
[37 empty] | 11.1128 | 29.8031
[37 empty] | 13.0293 | 36.7366
[37 empty] | 15.6766 | 44.2749
[37 empty] | 18.1723 | 52.5653
[37 empty] | 20.8063 | 59.3536
[37 empty] | 24.0173 | 68.7122
[37 empty] | 28.0083 | 79.3022
[37 empty] | 31.8335 | 90.1739
[37 empty] | 36.2059 | 102.0198
[37 empty] | 40.3372 | 109.7483
[37 empty] | 45.5194 | 121.423
[37 empty] | 50.8145 | 126.9602
[37 empty] | 56.5802 | 126.9601
[37 empty] | 62.8856 | 126.9602
[37 empty] | 70.1201 | 126.9601
[37 empty] | 76.1762 | 126.9602
[37 empty] | 84.6298 | 126.9602
[37 empty] | 94.7107 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.3198 | 30.1197
[37 empty] | 13.0742 | 37.5319
[37 empty] | 15.7101 | 45.2884
[37 empty] | 18.4587 | 53.9129
[37 empty] | 21.4735 | 63.3068
[37 empty] | 24.7682 | 70.5569
[37 empty] | 28.93 | 81.3534
[37 empty] | 32.6346 | 92.9494
[37 empty] | 36.943 | 104.9514
[37 empty] | 41.2093 | 116.6989
[37 empty] | 46.8297 | 125.5944
[37 empty] | 51.704 | 126.9601
[37 empty] | 58.1896 | 126.9601
[37 empty] | 63.9624 | 126.9602
[37 empty] | 71.2677 | 126.9602
[37 empty] | 78.9695 | 126.9602
[37 empty] | 85.6595 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.839 | 32.3325
[37 empty] | 13.112 | 38.233
[37 empty] | 15.9579 | 46.2963
[37 empty] | 19.0416 | 55.1907
[37 empty] | 21.9546 | 64.858
[37 empty] | 25.0409 | 72.3151
[37 empty] | 28.9027 | 83.3388
[37 empty] | 33.7506 | 95.4733
[37 empty] | 38.0197 | 107.8119
[37 empty] | 42.9579 | 121.2507
[37 empty] | 47.6837 | 126.9601
[37 empty] | 53.1459 | 126.9601
[37 empty] | 59.592 | 126.9601
[37 empty] | 65.4574 | 126.9601
[37 empty] | 72.1509 | 126.9602
[37 empty] | 79.9236 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 13.5732 | 24.4855
[37 empty] | 14.0444 | 38.7928
[37 empty] | 16.5838 | 47.2501
[37 empty] | 19.8198 | 56.3689
[37 empty] | 22.9995 | 66.3301
[37 empty] | 26.2319 | 76.5263
[37 empty] | 29.9299 | 85.388
[37 empty] | 34.5049 | 97.772
[37 empty] | 38.7568 | 110.8709
[37 empty] | 43.7196 | 124.4588
[37 empty] | 48.373 | 126.9601
[37 empty] | 54.7306 | 126.9601
[37 empty] | 60.4786 | 126.9602
[37 empty] | 67.0331 | 126.9602
[37 empty] | 74.1546 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 15.4516 | 39.1373
[37 empty] | 16.6006 | 48.1204
[37 empty] | 19.7334 | 57.4863
[37 empty] | 22.8929 | 67.8348
[37 empty] | 26.2397 | 79.0043
[37 empty] | 29.8629 | 87.3441
[37 empty] | 34.4237 | 99.9239
[37 empty] | 40.2609 | 113.6981
[37 empty] | 44.9849 | 126.9601
[37 empty] | 50.4735 | 126.9601
[37 empty] | 55.832 | 126.9601
[37 empty] | 61.542 | 126.9602
[37 empty] | 68.6833 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 16.346 | 41.1277
[37 empty] | 16.5416 | 48.8753
[37 empty] | 20.0626 | 58.5775
[37 empty] | 23.8529 | 69.1973
[37 empty] | 27.4146 | 80.6498
[37 empty] | 31.1505 | 89.9111
[37 empty] | 35.5589 | 102.1624
[37 empty] | 40.7067 | 116.2504
[37 empty] | 45.5787 | 126.9601
[37 empty] | 51.2946 | 126.9601
[37 empty] | 56.4575 | 126.9602
[37 empty] | 63.2881 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 17.2285 | 35.2368
[37 empty] | 17.3626 | 49.4867
[37 empty] | 20.758 | 59.6018
[37 empty] | 24.5286 | 70.4551
[37 empty] | 28.2091 | 82.2635
[37 empty] | 32.0207 | 95.0594
[37 empty] | 36.1156 | 104.3567
[37 empty] | 41.2449 | 118.617
[37 empty] | 47.3217 | 126.9601
[37 empty] | 52.7777 | 126.9602
[37 empty] | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 11.7699 | 32.0031
[37 empty] | 13.601 | 37.5469
[37 empty] | 15.8508 | 41.9673
[37 empty] | 18.3412 | 47.8386
[37 empty] | 21.1691 | 53.5948
[37 empty] | 24.0585 | 58.447
[37 empty] | 27.8402 | 58.803
[37 empty] | 31.3546 | 58.5759
[37 empty] | 36.422 | 57.9392
[37 empty] | 41.4958 | 58.3942
[37 empty] | 48.0343 | 58.9531
[37 empty] | 55.3815 | 56.5848
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.4538 | 12.3991
[37 empty] | 5.9439 | 15.6403
[37 empty] | 7.3298 | 19.5445
[37 empty] | 8.5649 | 23.9769
[37 empty] | 9.993 | 27.8065
[37 empty] | 12.1391 | 33.2299
[37 empty] | 14.0304 | 39.1019
[37 empty] | 16.4121 | 45.5079
[37 empty] | 19.032 | 50.1624
[37 empty] | 21.8538 | 56.7855
[37 empty] | 24.9272 | 62.9919
[37 empty] | 28.6206 | 65.6702
[37 empty] | 32.3085 | 65.9405
[37 empty] | 36.6126 | 65.8016
[37 empty] | 42.4028 | 65.639
[37 empty] | 47.9875 | 66.1098
[37 empty] | 55.8685 | 66.0993
[37 empty] | 63.1387 | 63.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.8776 | 10.3709
[37 empty] | 5.9672 | 16.0914
[37 empty] | 7.3549 | 20.1873
[37 empty] | 8.9222 | 24.8293
[37 empty] | 10.5321 | 29.3656
[37 empty] | 12.3102 | 34.4149
[37 empty] | 14.7558 | 40.7191
[37 empty] | 16.9978 | 47.3518
[37 empty] | 19.6774 | 52.6566
[37 empty] | 22.5308 | 59.4656
[37 empty] | 25.7566 | 66.4236
[37 empty] | 29.1758 | 73.3333
[37 empty] | 33.425 | 73.7137
[37 empty] | 37.4523 | 73.3536
[37 empty] | 42.9142 | 73.3866
[37 empty] | 49.0108 | 74.0486
[37 empty] | 55.1264 | 74.5178
[37 empty] | 64.4822 | 74.5276
[37 empty] | 71.7723 | 70.7774
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.453 | 16.4601
[37 empty] | 7.6696 | 20.8178
[37 empty] | 9.2176 | 25.6674
[37 empty] | 10.7286 | 31.091
[37 empty] | 12.814 | 35.6449
[37 empty] | 15.1569 | 42.1821
[37 empty] | 17.5255 | 49.1571
[37 empty] | 20.3432 | 56.7809
[37 empty] | 23.3062 | 62.1448
[37 empty] | 26.4924 | 69.9107
[37 empty] | 30.2611 | 77.2504
[37 empty] | 34.2819 | 82.4485
[37 empty] | 39.1102 | 82.9524
[37 empty] | 43.5036 | 82.5148
[37 empty] | 49.8837 | 81.3364
[37 empty] | 56.269 | 82.5395
[37 empty] | 63.1967 | 82.9402
[37 empty] | 73.7545 | 82.3271
[37 empty] | 81.6054 | 79.3179
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.2395 | 17.0303
[37 empty] | 7.8059 | 21.4254
[37 empty] | 9.5793 | 26.4523
[37 empty] | 11.3834 | 32.0983
[37 empty] | 13.1276 | 36.8384
[37 empty] | 15.3536 | 43.5534
[37 empty] | 18.2962 | 51.0495
[37 empty] | 20.9887 | 58.877
[37 empty] | 24.0589 | 65.4577
[37 empty] | 27.3282 | 72.9534
[37 empty] | 31.2318 | 81.2868
[37 empty] | 35.4207 | 89.2568
[37 empty] | 40.004 | 91.6597
[37 empty] | 44.8066 | 92.0158
[37 empty] | 50.0122 | 91.8833
[37 empty] | 57.2677 | 91.0918
[37 empty] | 64.1843 | 92.3763
[37 empty] | 72.1709 | 92.7477
[37 empty] | 83.791 | 92.0281
[37 empty] | 92.1977 | 88.544
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.6527 | 15.5267
[37 empty] | 7.8476 | 21.9668
[37 empty] | 9.6303 | 27.2198
[37 empty] | 11.4976 | 33.1226
[37 empty] | 13.7099 | 39.6483
[37 empty] | 16.0491 | 44.9885
[37 empty] | 18.7183 | 52.7648
[37 empty] | 21.6284 | 60.943
[37 empty] | 24.9262 | 69.8742
[37 empty] | 28.2143 | 76.0029
[37 empty] | 32.0433 | 84.9985
[37 empty] | 36.5584 | 93.5253
[37 empty] | 40.6283 | 101.9065
[37 empty] | 46.0942 | 101.9148
[37 empty] | 51.0502 | 101.2467
[37 empty] | 57.491 | 102.1367
[37 empty] | 65.2952 | 101.6651
[37 empty] | 72.7779 | 102.0387
[37 empty] | 82.0777 | 102.54
[37 empty] | 94.1756 | 100.8854
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.4251 | 11.1654
[37 empty] | 8.626 | 22.4048
[37 empty] | 10.0707 | 27.9674
[37 empty] | 12.1238 | 34.0823
[37 empty] | 14.0916 | 40.8543
[37 empty] | 16.1927 | 46.3828
[37 empty] | 19.1571 | 54.3477
[37 empty] | 22.4325 | 63.1245
[37 empty] | 25.6165 | 72.2476
[37 empty] | 29.0856 | 80.3364
[37 empty] | 32.953 | 88.4142
[37 empty] | 37.6354 | 98.2926
[37 empty] | 41.9298 | 107.3472
[37 empty] | 47.1667 | 112.8128
[37 empty] | 53.1496 | 113.4849
[37 empty] | 58.3888 | 112.6148
[37 empty] | 65.8924 | 112.3073
[37 empty] | 73.9935 | 113.0467
[37 empty] | 82.0539 | 113.39
[37 empty] | 92.802 | 113.8644
[37 empty] | 105.0584 | 111.9723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.5417 | 22.8585
[37 empty] | 10.1644 | 28.6739
[37 empty] | 12.3537 | 34.9853
[37 empty] | 14.739 | 42.0253
[37 empty] | 17.1012 | 49.1455
[37 empty] | 19.7427 | 55.9665
[37 empty] | 22.991 | 65.1
[37 empty] | 26.3835 | 74.5803
[37 empty] | 30.2032 | 84.9212
[37 empty] | 33.7881 | 91.8398
[37 empty] | 38.4962 | 102.1436
[37 empty] | 43.1636 | 112.1825
[37 empty] | 48.3056 | 122.2097
[37 empty] | 54.1646 | 124.2598
[37 empty] | 60.3101 | 124.6468
[37 empty] | 66.4309 | 124.7604
[37 empty] | 75.0155 | 124.137
[37 empty] | 83.3904 | 125.2286
[37 empty] | 92.0266 | 125.5368
[37 empty] | 104.302 | 124.8224
[37 empty] | 116.6406 | 123.8195
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.8546 | 22.6697
[37 empty] | 10.2198 | 29.301
[37 empty] | 12.4687 | 35.877
[37 empty] | 14.9305 | 43.1989
[37 empty] | 17.2579 | 51.2247
[37 empty] | 20.0505 | 57.5838
[37 empty] | 23.6818 | 66.9124
[37 empty] | 27.2008 | 77.061
[37 empty] | 30.9216 | 87.5743
[37 empty] | 34.7915 | 97.396
[37 empty] | 39.4856 | 105.939
[37 empty] | 44.3087 | 117.1977
[37 empty] | 49.6486 | 126.9601
[37 empty] | 54.9361 | 126.9601
[37 empty] | 61.5619 | 126.9602
[37 empty] | 67.5145 | 126.9601
[37 empty] | 74.8839 | 126.9602
[37 empty] | 84.545 | 126.9602
[37 empty] | 93.4753 | 126.9601
[37 empty] | 102.6563 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.795 | 16.7083
[37 empty] | 11.1128 | 29.8031
[37 empty] | 13.0293 | 36.7366
[37 empty] | 15.6766 | 44.2749
[37 empty] | 18.1723 | 52.5653
[37 empty] | 20.8063 | 59.3536
[37 empty] | 24.0173 | 68.7122
[37 empty] | 28.0083 | 79.3022
[37 empty] | 31.8335 | 90.1739
[37 empty] | 36.2059 | 102.0198
[37 empty] | 40.3372 | 109.7483
[37 empty] | 45.5194 | 121.423
[37 empty] | 50.8145 | 126.9602
[37 empty] | 56.5802 | 126.9601
[37 empty] | 62.8856 | 126.9602
[37 empty] | 70.1201 | 126.9601
[37 empty] | 76.1762 | 126.9602
[37 empty] | 84.6298 | 126.9602
[37 empty] | 94.7107 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.3198 | 30.1197
[37 empty] | 13.0742 | 37.5319
[37 empty] | 15.7101 | 45.2884
[37 empty] | 18.4587 | 53.9129
[37 empty] | 21.4735 | 63.3068
[37 empty] | 24.7682 | 70.5569
[37 empty] | 28.93 | 81.3534
[37 empty] | 32.6346 | 92.9494
[37 empty] | 36.943 | 104.9514
[37 empty] | 41.2093 | 116.6989
[37 empty] | 46.8297 | 125.5944
[37 empty] | 51.704 | 126.9601
[37 empty] | 58.1896 | 126.9601
[37 empty] | 63.9624 | 126.9602
[37 empty] | 71.2677 | 126.9602
[37 empty] | 78.9695 | 126.9602
[37 empty] | 85.6595 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.839 | 32.3325
[37 empty] | 13.112 | 38.233
[37 empty] | 15.9579 | 46.2963
[37 empty] | 19.0416 | 55.1907
[37 empty] | 21.9546 | 64.858
[37 empty] | 25.0409 | 72.3151
[37 empty] | 28.9027 | 83.3388
[37 empty] | 33.7506 | 95.4733
[37 empty] | 38.0197 | 107.8119
[37 empty] | 42.9579 | 121.2507
[37 empty] | 47.6837 | 126.9601
[37 empty] | 53.1459 | 126.9601
[37 empty] | 59.592 | 126.9601
[37 empty] | 65.4574 | 126.9601
[37 empty] | 72.1509 | 126.9602
[37 empty] | 79.9236 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 13.5732 | 24.4855
[37 empty] | 14.0444 | 38.7928
[37 empty] | 16.5838 | 47.2501
[37 empty] | 19.8198 | 56.3689
[37 empty] | 22.9995 | 66.3301
[37 empty] | 26.2319 | 76.5263
[37 empty] | 29.9299 | 85.388
[37 empty] | 34.5049 | 97.772
[37 empty] | 38.7568 | 110.8709
[37 empty] | 43.7196 | 124.4588
[37 empty] | 48.373 | 126.9601
[37 empty] | 54.7306 | 126.9601
[37 empty] | 60.4786 | 126.9602
[37 empty] | 67.0331 | 126.9602
[37 empty] | 74.1546 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 15.4516 | 39.1373
[37 empty] | 16.6006 | 48.1204
[37 empty] | 19.7334 | 57.4863
[37 empty] | 22.8929 | 67.8348
[37 empty] | 26.2397 | 79.0043
[37 empty] | 29.8629 | 87.3441
[37 empty] | 34.4237 | 99.9239
[37 empty] | 40.2609 | 113.6981
[37 empty] | 44.9849 | 126.9601
[37 empty] | 50.4735 | 126.9601
[37 empty] | 55.832 | 126.9601
[37 empty] | 61.542 | 126.9602
[37 empty] | 68.6833 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 16.346 | 41.1277
[37 empty] | 16.5416 | 48.8753
[37 empty] | 20.0626 | 58.5775
[37 empty] | 23.8529 | 69.1973
[37 empty] | 27.4146 | 80.6498
[37 empty] | 31.1505 | 89.9111
[37 empty] | 35.5589 | 102.1624
[37 empty] | 40.7067 | 116.2504
[37 empty] | 45.5787 | 126.9601
[37 empty] | 51.2946 | 126.9601
[37 empty] | 56.4575 | 126.9602
[37 empty] | 63.2881 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 17.2285 | 35.2368
[37 empty] | 17.3626 | 49.4867
[37 empty] | 20.758 | 59.6018
[37 empty] | 24.5286 | 70.4551
[37 empty] | 28.2091 | 82.2635
[37 empty] | 32.0207 | 95.0594
[37 empty] | 36.1156 | 104.3567
[37 empty] | 41.2449 | 118.617
[37 empty] | 47.3217 | 126.9601
[37 empty] | 52.7777 | 126.9602
[37 empty] | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 11.7699 | 32.0031
[37 empty] | 13.601 | 37.5469
[37 empty] | 15.8508 | 41.9673
[37 empty] | 18.3412 | 47.8386
[37 empty] | 21.1691 | 53.5948
[37 empty] | 24.0585 | 58.447
[37 empty] | 27.8402 | 58.803
[37 empty] | 31.3546 | 58.5759
[37 empty] | 36.422 | 57.9392
[37 empty] | 41.4958 | 58.3942
[37 empty] | 48.0343 | 58.9531
[37 empty] | 55.3815 | 56.5848
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.4538 | 12.3991
[37 empty] | 5.9439 | 15.6403
[37 empty] | 7.3298 | 19.5445
[37 empty] | 8.5649 | 23.9769
[37 empty] | 9.993 | 27.8065
[37 empty] | 12.1391 | 33.2299
[37 empty] | 14.0304 | 39.1019
[37 empty] | 16.4121 | 45.5079
[37 empty] | 19.032 | 50.1624
[37 empty] | 21.8538 | 56.7855
[37 empty] | 24.9272 | 62.9919
[37 empty] | 28.6206 | 65.6702
[37 empty] | 32.3085 | 65.9405
[37 empty] | 36.6126 | 65.8016
[37 empty] | 42.4028 | 65.639
[37 empty] | 47.9875 | 66.1098
[37 empty] | 55.8685 | 66.0993
[37 empty] | 63.1387 | 63.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.8776 | 10.3709
[37 empty] | 5.9672 | 16.0914
[37 empty] | 7.3549 | 20.1873
[37 empty] | 8.9222 | 24.8293
[37 empty] | 10.5321 | 29.3656
[37 empty] | 12.3102 | 34.4149
[37 empty] | 14.7558 | 40.7191
[37 empty] | 16.9978 | 47.3518
[37 empty] | 19.6774 | 52.6566
[37 empty] | 22.5308 | 59.4656
[37 empty] | 25.7566 | 66.4236
[37 empty] | 29.1758 | 73.3333
[37 empty] | 33.425 | 73.7137
[37 empty] | 37.4523 | 73.3536
[37 empty] | 42.9142 | 73.3866
[37 empty] | 49.0108 | 74.0486
[37 empty] | 55.1264 | 74.5178
[37 empty] | 64.4822 | 74.5276
[37 empty] | 71.7723 | 70.7774
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.453 | 16.4601
[37 empty] | 7.6696 | 20.8178
[37 empty] | 9.2176 | 25.6674
[37 empty] | 10.7286 | 31.091
[37 empty] | 12.814 | 35.6449
[37 empty] | 15.1569 | 42.1821
[37 empty] | 17.5255 | 49.1571
[37 empty] | 20.3432 | 56.7809
[37 empty] | 23.3062 | 62.1448
[37 empty] | 26.4924 | 69.9107
[37 empty] | 30.2611 | 77.2504
[37 empty] | 34.2819 | 82.4485
[37 empty] | 39.1102 | 82.9524
[37 empty] | 43.5036 | 82.5148
[37 empty] | 49.8837 | 81.3364
[37 empty] | 56.269 | 82.5395
[37 empty] | 63.1967 | 82.9402
[37 empty] | 73.7545 | 82.3271
[37 empty] | 81.6054 | 79.3179
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.2395 | 17.0303
[37 empty] | 7.8059 | 21.4254
[37 empty] | 9.5793 | 26.4523
[37 empty] | 11.3834 | 32.0983
[37 empty] | 13.1276 | 36.8384
[37 empty] | 15.3536 | 43.5534
[37 empty] | 18.2962 | 51.0495
[37 empty] | 20.9887 | 58.877
[37 empty] | 24.0589 | 65.4577
[37 empty] | 27.3282 | 72.9534
[37 empty] | 31.2318 | 81.2868
[37 empty] | 35.4207 | 89.2568
[37 empty] | 40.004 | 91.6597
[37 empty] | 44.8066 | 92.0158
[37 empty] | 50.0122 | 91.8833
[37 empty] | 57.2677 | 91.0918
[37 empty] | 64.1843 | 92.3763
[37 empty] | 72.1709 | 92.7477
[37 empty] | 83.791 | 92.0281
[37 empty] | 92.1977 | 88.544
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.6527 | 15.5267
[37 empty] | 7.8476 | 21.9668
[37 empty] | 9.6303 | 27.2198
[37 empty] | 11.4976 | 33.1226
[37 empty] | 13.7099 | 39.6483
[37 empty] | 16.0491 | 44.9885
[37 empty] | 18.7183 | 52.7648
[37 empty] | 21.6284 | 60.943
[37 empty] | 24.9262 | 69.8742
[37 empty] | 28.2143 | 76.0029
[37 empty] | 32.0433 | 84.9985
[37 empty] | 36.5584 | 93.5253
[37 empty] | 40.6283 | 101.9065
[37 empty] | 46.0942 | 101.9148
[37 empty] | 51.0502 | 101.2467
[37 empty] | 57.491 | 102.1367
[37 empty] | 65.2952 | 101.6651
[37 empty] | 72.7779 | 102.0387
[37 empty] | 82.0777 | 102.54
[37 empty] | 94.1756 | 100.8854
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.4251 | 11.1654
[37 empty] | 8.626 | 22.4048
[37 empty] | 10.0707 | 27.9674
[37 empty] | 12.1238 | 34.0823
[37 empty] | 14.0916 | 40.8543
[37 empty] | 16.1927 | 46.3828
[37 empty] | 19.1571 | 54.3477
[37 empty] | 22.4325 | 63.1245
[37 empty] | 25.6165 | 72.2476
[37 empty] | 29.0856 | 80.3364
[37 empty] | 32.953 | 88.4142
[37 empty] | 37.6354 | 98.2926
[37 empty] | 41.9298 | 107.3472
[37 empty] | 47.1667 | 112.8128
[37 empty] | 53.1496 | 113.4849
[37 empty] | 58.3888 | 112.6148
[37 empty] | 65.8924 | 112.3073
[37 empty] | 73.9935 | 113.0467
[37 empty] | 82.0539 | 113.39
[37 empty] | 92.802 | 113.8644
[37 empty] | 105.0584 | 111.9723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.5417 | 22.8585
[37 empty] | 10.1644 | 28.6739
[37 empty] | 12.3537 | 34.9853
[37 empty] | 14.739 | 42.0253
[37 empty] | 17.1012 | 49.1455
[37 empty] | 19.7427 | 55.9665
[37 empty] | 22.991 | 65.1
[37 empty] | 26.3835 | 74.5803
[37 empty] | 30.2032 | 84.9212
[37 empty] | 33.7881 | 91.8398
[37 empty] | 38.4962 | 102.1436
[37 empty] | 43.1636 | 112.1825
[37 empty] | 48.3056 | 122.2097
[37 empty] | 54.1646 | 124.2598
[37 empty] | 60.3101 | 124.6468
[37 empty] | 66.4309 | 124.7604
[37 empty] | 75.0155 | 124.137
[37 empty] | 83.3904 | 125.2286
[37 empty] | 92.0266 | 125.5368
[37 empty] | 104.302 | 124.8224
[37 empty] | 116.6406 | 123.8195
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.8546 | 22.6697
[37 empty] | 10.2198 | 29.301
[37 empty] | 12.4687 | 35.877
[37 empty] | 14.9305 | 43.1989
[37 empty] | 17.2579 | 51.2247
[37 empty] | 20.0505 | 57.5838
[37 empty] | 23.6818 | 66.9124
[37 empty] | 27.2008 | 77.061
[37 empty] | 30.9216 | 87.5743
[37 empty] | 34.7915 | 97.396
[37 empty] | 39.4856 | 105.939
[37 empty] | 44.3087 | 117.1977
[37 empty] | 49.6486 | 126.9601
[37 empty] | 54.9361 | 126.9601
[37 empty] | 61.5619 | 126.9602
[37 empty] | 67.5145 | 126.9601
[37 empty] | 74.8839 | 126.9602
[37 empty] | 84.545 | 126.9602
[37 empty] | 93.4753 | 126.9601
[37 empty] | 102.6563 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.795 | 16.7083
[37 empty] | 11.1128 | 29.8031
[37 empty] | 13.0293 | 36.7366
[37 empty] | 15.6766 | 44.2749
[37 empty] | 18.1723 | 52.5653
[37 empty] | 20.8063 | 59.3536
[37 empty] | 24.0173 | 68.7122
[37 empty] | 28.0083 | 79.3022
[37 empty] | 31.8335 | 90.1739
[37 empty] | 36.2059 | 102.0198
[37 empty] | 40.3372 | 109.7483
[37 empty] | 45.5194 | 121.423
[37 empty] | 50.8145 | 126.9602
[37 empty] | 56.5802 | 126.9601
[37 empty] | 62.8856 | 126.9602
[37 empty] | 70.1201 | 126.9601
[37 empty] | 76.1762 | 126.9602
[37 empty] | 84.6298 | 126.9602
[37 empty] | 94.7107 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.3198 | 30.1197
[37 empty] | 13.0742 | 37.5319
[37 empty] | 15.7101 | 45.2884
[37 empty] | 18.4587 | 53.9129
[37 empty] | 21.4735 | 63.3068
[37 empty] | 24.7682 | 70.5569
[37 empty] | 28.93 | 81.3534
[37 empty] | 32.6346 | 92.9494
[37 empty] | 36.943 | 104.9514
[37 empty] | 41.2093 | 116.6989
[37 empty] | 46.8297 | 125.5944
[37 empty] | 51.704 | 126.9601
[37 empty] | 58.1896 | 126.9601
[37 empty] | 63.9624 | 126.9602
[37 empty] | 71.2677 | 126.9602
[37 empty] | 78.9695 | 126.9602
[37 empty] | 85.6595 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.839 | 32.3325
[37 empty] | 13.112 | 38.233
[37 empty] | 15.9579 | 46.2963
[37 empty] | 19.0416 | 55.1907
[37 empty] | 21.9546 | 64.858
[37 empty] | 25.0409 | 72.3151
[37 empty] | 28.9027 | 83.3388
[37 empty] | 33.7506 | 95.4733
[37 empty] | 38.0197 | 107.8119
[37 empty] | 42.9579 | 121.2507
[37 empty] | 47.6837 | 126.9601
[37 empty] | 53.1459 | 126.9601
[37 empty] | 59.592 | 126.9601
[37 empty] | 65.4574 | 126.9601
[37 empty] | 72.1509 | 126.9602
[37 empty] | 79.9236 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 13.5732 | 24.4855
[37 empty] | 14.0444 | 38.7928
[37 empty] | 16.5838 | 47.2501
[37 empty] | 19.8198 | 56.3689
[37 empty] | 22.9995 | 66.3301
[37 empty] | 26.2319 | 76.5263
[37 empty] | 29.9299 | 85.388
[37 empty] | 34.5049 | 97.772
[37 empty] | 38.7568 | 110.8709
[37 empty] | 43.7196 | 124.4588
[37 empty] | 48.373 | 126.9601
[37 empty] | 54.7306 | 126.9601
[37 empty] | 60.4786 | 126.9602
[37 empty] | 67.0331 | 126.9602
[37 empty] | 74.1546 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 15.4516 | 39.1373
[37 empty] | 16.6006 | 48.1204
[37 empty] | 19.7334 | 57.4863
[37 empty] | 22.8929 | 67.8348
[37 empty] | 26.2397 | 79.0043
[37 empty] | 29.8629 | 87.3441
[37 empty] | 34.4237 | 99.9239
[37 empty] | 40.2609 | 113.6981
[37 empty] | 44.9849 | 126.9601
[37 empty] | 50.4735 | 126.9601
[37 empty] | 55.832 | 126.9601
[37 empty] | 61.542 | 126.9602
[37 empty] | 68.6833 | 126.9601
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 16.346 | 41.1277
[37 empty] | 16.5416 | 48.8753
[37 empty] | 20.0626 | 58.5775
[37 empty] | 23.8529 | 69.1973
[37 empty] | 27.4146 | 80.6498
[37 empty] | 31.1505 | 89.9111
[37 empty] | 35.5589 | 102.1624
[37 empty] | 40.7067 | 116.2504
[37 empty] | 45.5787 | 126.9601
[37 empty] | 51.2946 | 126.9601
[37 empty] | 56.4575 | 126.9602
[37 empty] | 63.2881 | 126.9602
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 17.2285 | 35.2368
[37 empty] | 17.3626 | 49.4867
[37 empty] | 20.758 | 59.6018
[37 empty] | 24.5286 | 70.4551
[37 empty] | 28.2091 | 82.2635
[37 empty] | 32.0207 | 95.0594
[37 empty] | 36.1156 | 104.3567
[37 empty] | 41.2449 | 118.617
[37 empty] | 47.3217 | 126.9601
[37 empty] | 52.7777 | 126.9602
[37 empty] | 58.743 | 126.9602
[37 empty] | 4.5498 | 11.5167
[37 empty] | 5.577 | 14.6204
[37 empty] | 6.7893 | 18.1802
[37 empty] | 7.8511 | 21.3458
[37 empty] | 9.5588 | 25.7708
[37 empty] | 11.097 | 30.644
[37 empty] | 13.0916 | 35.9571
[37 empty] | 15.2624 | 39.94
[37 empty] | 17.7059 | 45.4484
[37 empty] | 20.3419 | 50.6552
[37 empty] | 23.3788 | 51.6444
[37 empty] | 26.5651 | 51.5068
[37 empty] | 30.9668 | 51.5623
[37 empty] | 35.6287 | 51.8719
[37 empty] | 40.9637 | 51.8934
[37 empty] | 48.2998 | 51.389
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.9292 | 11.8126
[37 empty] | 5.7776 | 15.1388
[37 empty] | 6.9172 | 18.8847
[37 empty] | 8.3095 | 23.1137
[37 empty] | 9.7669 | 26.7752
[37 empty] | 8.5747 | 23.0861
[37 empty] | 10.0921 | 27.0734
[37 empty] | 11.5676 | 30.0979
[37 empty] | 13.3575 | 34.2767
[37 empty] | 15.3391 | 38.2422
[37 empty] | 17.6718 | 39.9189
[37 empty] | 19.9411 | 40.1319
[37 empty] | 22.9327 | 40.079
[37 empty] | 26.5427 | 40.0954
[37 empty] | 30.1228 | 40.4314
[37 empty] | 35.7098 | 39.9119
[37 empty] | 40.2301 | 38.5874
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.1993 | 8.8682
[37 empty] | 4.6238 | 11.4069
[37 empty] | 5.4802 | 14.2089
[37 empty] | 6.3445 | 17.3877
[37 empty] | 7.5663 | 20.1421
[37 empty] | 8.9351 | 24.0547
[37 empty] | 10.4239 | 28.2107
[37 empty] | 11.959 | 32.2434
[37 empty] | 13.8048 | 36.0111
[37 empty] | 15.8745 | 40.4827
[37 empty] | 18.0705 | 44.884
[37 empty] | 20.8318 | 45.1309
[37 empty] | 23.4146 | 44.9448
[37 empty] | 27.064 | 44.9312
[37 empty] | 30.8778 | 45.1391
[37 empty] | 35.0704 | 45.4468
[37 empty] | 41.392 | 45.2292
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.3612 | 8.9771
[37 empty] | 4.5803 | 11.7505
[37 empty] | 5.6398 | 14.6838
[37 empty] | 6.707 | 18.0132
[37 empty] | 7.7039 | 20.8962
[37 empty] | 9.2107 | 24.9456
[37 empty] | 10.7125 | 29.4124
[37 empty] | 12.5811 | 34.2136
[37 empty] | 14.2865 | 37.7584
[37 empty] | 16.365 | 42.7201
[37 empty] | 18.8057 | 47.4545
[37 empty] | 21.4049 | 50.6676
[37 empty] | 24.4891 | 51.064
[37 empty] | 27.363 | 50.7666
[37 empty] | 31.5427 | 50.2122
[37 empty] | 35.6622 | 51.0088
[37 empty] | 40.6387 | 50.9152
[37 empty] | 47.1582 | 50.2672
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 4.7732 | 6.4786
[37 empty] | 4.779 | 12.0604
[37 empty] | 5.7257 | 15.1552
[37 empty] | 6.8046 | 18.649
[37 empty] | 8.1409 | 22.5502
[37 empty] | 9.4617 | 25.8429
[37 empty] | 11.2332 | 30.5791
[37 empty] | 12.9502 | 35.5459
[37 empty] | 14.7519 | 40.5021
[37 empty] | 16.9384 | 44.721
[37 empty] | 19.4722 | 50.1265
[37 empty] | 22.148 | 55.2599
[37 empty] | 25.0822 | 56.636
[37 empty] | 28.0639 | 56.9451
[37 empty] | 31.7052 | 56.788
[37 empty] | 36.4168 | 56.5732
[37 empty] | 40.914 | 56.8886
[37 empty] | 46.8283 | 57.2808
[37 empty] | 53.3934 | 56.521
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.3391 | 12.2784
[37 empty] | 5.9798 | 15.6157
[37 empty] | 7.1813 | 19.2479
[37 empty] | 8.3228 | 23.3226
[37 empty] | 9.6291 | 26.7511
[37 empty] | 11.6237 | 31.6404
[37 empty] | 13.2655 | 36.9411
[37 empty] | 15.5311 | 42.6405
[37 empty] | 17.4826 | 46.7387
[37 empty] | 20.0462 | 52.5507
[37 empty] | 22.9114 | 58.111
[37 empty] | 25.5999 | 63.3351
[37 empty] | 29.1961 | 63.4544
[37 empty] | 32.3922 | 63.0494
[37 empty] | 36.8219 | 63.027
[37 empty] | 41.7507 | 63.4939
[37 empty] | 46.6377 | 63.7961
[37 empty] | 53.5574 | 63.6127
[37 empty] | 60.1316 | 61.3723
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 5.6702 | 13.1874
[37 empty] | 5.883 | 16.0314
[37 empty] | 7.2692 | 19.8154
[37 empty] | 8.7353 | 24.0702
[37 empty] | 10.1199 | 28.0987
[37 empty] | 11.7385 | 32.6801
[37 empty] | 13.9765 | 38.3214
[37 empty] | 15.9309 | 44.1758
[37 empty] | 18.0018 | 50.2286
[37 empty] | 20.6907 | 54.8307
[37 empty] | 23.6252 | 61.2623
[37 empty] | 26.4682 | 67.1838
[37 empty] | 29.9202 | 70.4572
[37 empty] | 33.7902 | 71.0175
[37 empty] | 37.3283 | 70.5862
[37 empty] | 42.4342 | 70.2774
[37 empty] | 47.5636 | 70.9719
[37 empty] | 52.837 | 71.2608
[37 empty] | 60.8149 | 71.0549
[37 empty] | 67.3745 | 68.4511
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.0686 | 9.7556
[37 empty] | 6.1159 | 16.4081
[37 empty] | 7.4444 | 20.3842
[37 empty] | 8.8813 | 24.8225
[37 empty] | 10.3039 | 29.7346
[37 empty] | 12.151 | 33.7526
[37 empty] | 14.3139 | 39.5659
[37 empty] | 16.265 | 45.7721
[37 empty] | 18.9753 | 52.4501
[37 empty] | 21.2782 | 57.13
[37 empty] | 24.2945 | 63.85
[37 empty] | 27.2941 | 70.4485
[37 empty] | 30.628 | 77.0074
[37 empty] | 34.4646 | 78.0241
[37 empty] | 38.3198 | 78.3946
[37 empty] | 42.5765 | 78.2557
[37 empty] | 48.3691 | 77.4469
[37 empty] | 53.8459 | 78.4246
[37 empty] | 59.7005 | 78.6223
[37 empty] | 68.5754 | 77.8125
[37 empty] | 75.117 | 76.0577
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 6.8403 | 16.6703
[37 empty] | 7.7456 | 20.9315
[37 empty] | 9.3478 | 25.5163
[37 empty] | 10.8391 | 30.6162
[37 empty] | 12.4236 | 34.7884
[37 empty] | 14.4257 | 40.7528
[37 empty] | 17.097 | 47.374
[37 empty] | 19.3967 | 54.193
[37 empty] | 21.7901 | 61.371
[37 empty] | 25.0078 | 66.415
[37 empty] | 28.0513 | 73.8077
[37 empty] | 31.5834 | 80.6463
[37 empty] | 35.1297 | 86.4588
[37 empty] | 39.549 | 86.5615
[37 empty] | 43.4253 | 85.8853
[37 empty] | 48.4863 | 86.5751
[37 empty] | 54.7344 | 86.0097
[37 empty] | 60.5946 | 87.0244
[37 empty] | 67.1624 | 87.1744
[37 empty] | 76.7476 | 86.2309
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.3644 | 17.597
[37 empty] | 7.5779 | 21.4167
[37 empty] | 9.3386 | 26.1844
[37 empty] | 11.0478 | 31.5026
[37 empty] | 12.9917 | 37.3388
[37 empty] | 15.0271 | 41.988
[37 empty] | 17.4302 | 48.8161
[37 empty] | 19.739 | 55.9939
[37 empty] | 22.9419 | 63.7251
[37 empty] | 25.6277 | 69.0029
[37 empty] | 28.871 | 76.6845
[37 empty] | 32.4252 | 84.4459
[37 empty] | 36.2376 | 90.1325
[37 empty] | 40.4435 | 90.1325
[37 empty] | 45.1717 | 90.1326
[37 empty] | 49.2777 | 90.1326
[37 empty] | 55.0994 | 90.1325
[37 empty] | 61.5516 | 90.1325
[37 empty] | 67.8089 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 7.9035 | 14.4449
[37 empty] | 7.806 | 21.8594
[37 empty] | 9.6007 | 26.8405
[37 empty] | 11.4509 | 32.3474
[37 empty] | 13.2216 | 38.3861
[37 empty] | 15.1077 | 43.1811
[37 empty] | 17.6528 | 50.1588
[37 empty] | 20.6832 | 57.8258
[37 empty] | 23.3728 | 65.6764
[37 empty] | 26.1625 | 73.9419
[37 empty] | 29.7952 | 79.5389
[37 empty] | 33.0954 | 87.9361
[37 empty] | 37.3247 | 90.1325
[37 empty] | 41.1087 | 90.1325
[37 empty] | 45.939 | 90.1325
[37 empty] | 50.8496 | 90.1325
[37 empty] | 55.6734 | 90.1325
[37 empty] | 62.1983 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 8.5925 | 10.5456
[37 empty] | 8.6958 | 22.1642
[37 empty] | 9.9438 | 27.4707
[37 empty] | 11.8586 | 33.1342
[37 empty] | 13.9017 | 39.38
[37 empty] | 15.8898 | 45.3962
[37 empty] | 18.2373 | 51.5431
[37 empty] | 21.0094 | 59.4744
[37 empty] | 23.7775 | 67.6857
[37 empty] | 27.453 | 76.5318
[37 empty] | 30.551 | 82.4122
[37 empty] | 33.9713 | 90.1325
[37 empty] | 38.3346 | 90.1325
[37 empty] | 42.1963 | 90.1325
[37 empty] | 46.6943 | 90.1325
[37 empty] | 51.93 | 90.1325
[37 empty] | 56.5173 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.4876 | 22.9766
[37 empty] | 9.6985 | 28.0193
[37 empty] | 11.8592 | 33.8929
[37 empty] | 13.906 | 40.396
[37 empty] | 16.0656 | 47.4637
[37 empty] | 18.496 | 52.9123
[37 empty] | 21.5596 | 60.9897
[37 empty] | 24.7665 | 69.7483
[37 empty] | 27.8781 | 78.6886
[37 empty] | 31.0948 | 88.1043
[37 empty] | 35.0067 | 90.1325
[37 empty] | 39.0194 | 90.1325
[37 empty] | 43.2784 | 90.1325
[37 empty] | 48.0659 | 90.1326
[37 empty] | 53.0188 | 90.1325
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 9.9152 | 20.974
[37 empty] | 9.8342 | 28.5245
[37 empty] | 12.2151 | 34.6277
[37 empty] | 14.5417 | 41.3248
[37 empty] | 16.752 | 48.6019
[37 empty] | 19.0805 | 54.2307
[37 empty] | 21.9077 | 62.5046
[37 empty] | 25.2501 | 71.6014
[37 empty] | 28.3799 | 80.9026
[37 empty] | 32.5224 | 90.1325
[37 empty] | 36.0509 | 90.1326
[37 empty] | 39.8051 | 90.1326
[37 empty] | 44.3855 | 90.1326
[37 empty] | 49.2427 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 10.7318 | 15.7197
[37 empty] | 10.888 | 28.8692
[37 empty] | 12.5977 | 35.3309
[37 empty] | 14.8492 | 42.1901
[37 empty] | 17.2586 | 49.7239
[37 empty] | 19.8019 | 57.9119
[37 empty] | 22.5727 | 64.0509
[37 empty] | 26.0461 | 73.2965
[37 empty] | 29.3599 | 83.1958
[37 empty] | 32.9235 | 90.1325
[37 empty] | 36.5949 | 90.1326
[37 empty] | 40.7589 | 90.1326
[37 empty] | 45.532 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.0582 | 29.3459
[37 empty] | 12.2922 | 35.9335
[37 empty] | 14.8597 | 43.0269
[37 empty] | 17.4382 | 50.8249
[37 empty] | 19.9821 | 59.2263
[37 empty] | 22.6823 | 65.5153
[37 empty] | 26.0535 | 74.9452
[37 empty] | 30.1043 | 85.2525
[37 empty] | 33.5524 | 90.1325
[37 empty] | 38.1555 | 90.1326
[37 empty] | 41.9411 | 90.1326
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 0 | 0
[37 empty] | 12.2153 | 30.0035
[37 empty] | 12.6305 | 36.4854
[37 empty] | 15.2979 | 43.826
[37 empty] | 18.16 | 51.8244
[37 empty] | 20.8596 | 60.4554
[37 empty] | 23.677 | 68.5376
[37 empty] | 26.9058 | 76.6398
[37 empty] | 30.8512 | 87.1331
[37 empty] | 34.4695 | 90.1325
[37 empty] | 38.5113 | 90.1325
[37 empty] | 0 | 0

## TTH375-noEcon_APower
PN | 2718312
Calculation Type | FROM_POWER
Units | SI
Use Economizer? | FALSE
Compressor | TTH375-E-1-MT-SL
| Step SST | Step SDT | Percent Power |  | Subcooling
| 3 | 2.5 | 0 |  | 6 |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 11 | 11
| INPUT BLOCK | [5 empty] | 1: OUTPUT
CID | SST Verd. Temp | SDT Kond. Temperatur | Value Power | SSH Superheat | LLT Leaving Liquid Temp | tapp T approach Economizer | ENTROPY_SUCTION | SPEED_SOUND | DENSITY_SUCTION | ENTHALPY_LIQUID_CONDENSER_EXIT | ENTHALPY_DISCHARGE_ISENTROPIC | ENTHALPY_SUCTION | SPEED_COMPRESSOR | MASS_FLOW_RATE_EVAPORATOR | MASS_FLOW_RATE_MOTOR_COOLING | COEFFICIENT_OF_PERFORMANCE | POWER_INPUT_ELECTRICAL | CAPACITY_EVAPORATOR | TEMPERATURE_SUCT_SAT | TEMPERATURE_DISCH_SAT | TEMPERATURE_SUCT_SUPER_HEAT | TEMPERATURE_CONDENSER_LIQUID_LEAVING | PRESSURE_SUCT_ABSOLUTE | PRESSURE_DISCH_ABSOLUTE | TEMPERATURE_DISCH | PRESSURE_RATIO | POWER_FACTOR | IGV_ANGLE | INPUT_CURRENT | ECON_SAT_TEMP | ECON_INTERSTAGE_P | ECON_CAPACITY | ECON_MASS_FLOW | TEMPERATURE_ECO_LIQUID_LEAVING | ENTHALPY_LIQUID_ECO_EXIT | TOLERANCE | POWER_INPUT_ELECTRICAL | POWER_INPUT_ELECTRICAL
CID=390018774 | -18 | -5 | 4.5498 | 4 | -11 | 0 | 1.7524 | 147.8757 | 7.2169 | 185.3801 | 401.7246 | 391.078 | 19476.1011 | 0.18597 | 0.0061226 | 8.4079 | 4.5498 | 38.2544 | -18 | -5 | 4 | -11 | 144.6004 | 243.3424 | 9.4184 | 1.6829 | 0.64042 | 37.4524 | 10.7941 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 4.5498 | 11.5167
CID=390018739 | -18 | -2.5 | 5.577 | 4 | -8.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 188.676 | 403.6805 | 391.078 | 21189.7805 | 0.20193 | 0.0061699 | 7.3287 | 5.577 | 40.872 | -18 | -2.5 | 4 | -8.5 | 144.6004 | 267.1911 | 14.2519 | 1.8478 | 0.6525 | 24.2324 | 12.986 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.577 | 14.6204
CID=390018580 | -18 | 0 | 6.7893 | 4 | -6 | 0 | 1.7524 | 147.8757 | 7.2169 | 191.9873 | 405.6071 | 391.078 | 22339.2467 | 0.23371 | 0.0064065 | 6.8535 | 6.7893 | 46.5303 | -18 | 0 | 4 | -6 | 144.6004 | 292.8032 | 17.354 | 2.0249 | 0.66608 | 50.3801 | 15.4864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.7893 | 18.1802
CID=390018801 | -18 | 2.5 | 7.8511 | 4 | -3.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 195.3144 | 407.5045 | 391.078 | 23603.8497 | 0.24942 | 0.0067075 | 6.2192 | 7.8511 | 48.8276 | -18 | 2.5 | 4 | -3.5 | 144.6004 | 320.2635 | 20.8999 | 2.2148 | 0.67742 | 55.595 | 17.6089 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.8511 | 21.3458
CID=390018898 | -18 | 5 | 9.5588 | 4 | -1 | 0 | 1.7524 | 147.8757 | 7.2169 | 198.6579 | 409.3731 | 391.078 | 25099.9979 | 0.27825 | 0.0072057 | 5.6013 | 9.5588 | 53.5415 | -18 | 5 | 4 | -1 | 144.6004 | 349.6586 | 25.0301 | 2.4181 | 0.69459 | 51.2497 | 20.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.5588 | 25.7708
CID=390018863 | -18 | 7.5 | 11.097 | 4 | 1.5 | 0.3 | 1.7524 | 147.8757 | 7.2169 | 202.0183 | 411.2128 | 391.078 | 26024.5495 | 0.29705 | 0.0077216 | 5.0609 | 11.097 | 56.1609 | -18 | 7.5 | 4 | 1.5 | 144.6004 | 381.0767 | 29.018 | 2.6354 | 0.70902 | 66.5078 | 23.7795 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.097 | 30.644
CID=390018704 | -18 | 10 | 13.0916 | 4 | 4 | 0.8 | 1.7524 | 147.8757 | 7.2169 | 205.396 | 413.024 | 391.078 | 27215.0991 | 0.32777 | 0.0084031 | 4.6488 | 13.0916 | 60.8602 | -18 | 10 | 4 | 4 | 144.6004 | 414.6075 | 32.6528 | 2.8673 | 0.72636 | 91.826 | 27.3841 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.0916 | 35.9571
CID=390018429 | -18 | 12.5 | 15.2624 | 4 | 6.5 | 1.3 | 1.7524 | 147.8757 | 7.2169 | 208.7918 | 414.8068 | 391.078 | 28541.2048 | 0.359 | 0.0091812 | 4.2878 | 15.2624 | 65.4414 | -18 | 12.5 | 4 | 6.5 | 144.6004 | 450.3422 | 36.1951 | 3.1144 | 0.74362 | 60.8623 | 31.1838 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.2624 | 39.94
CID=390018526 | -18 | 15 | 17.7059 | 4 | 9 | 1.8 | 1.7524 | 147.8757 | 7.2169 | 212.2062 | 416.5615 | 391.078 | 29517.9144 | 0.39012 | 0.010085 | 3.9411 | 17.7059 | 69.7807 | -18 | 15 | 4 | 9 | 144.6004 | 488.3739 | 39.964 | 3.3774 | 0.76121 | 80.129 | 35.3403 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.7059 | 45.4484
CID=-143973562 | -18 | 17.5 | 20.3419 | 4 | 11.5 | 2.3 | 1.7524 | 147.8757 | 7.2169 | 215.6398 | 418.2881 | 391.078 | 30876.5743 | 0.42112 | 0.011096 | 3.6319 | 20.3419 | 73.8806 | -18 | 17.5 | 4 | 11.5 | 144.6004 | 528.7968 | 43.7182 | 3.657 | 0.77822 | 57.2816 | 39.714 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.3419 | 50.6552
CID=-143973465 | -18 | 20 | 23.3788 | 4 | 14 | 2.8 | 1.7524 | 147.8757 | 7.2169 | 219.0933 | 419.9871 | 391.078 | 31701.8631 | 0.45357 | 0.012285 | 3.3367 | 23.3788 | 78.0075 | -18 | 20 | 4 | 14 | 144.6004 | 571.7069 | 47.7339 | 3.9537 | 0.79558 | 59.0953 | 44.6471 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.3788 | 51.6444
CID=-143973500 | -18 | 22.5 | 26.5651 | 4 | 16.5 | 3.3 | 1.7524 | 147.8757 | 7.2169 | 222.5675 | 421.6585 | 391.078 | 32608.8076 | 0.49745 | 0.01358 | 3.1554 | 26.5651 | 83.825 | -18 | 22.5 | 4 | 16.5 | 144.6004 | 617.2019 | 50.4662 | 4.2683 | 0.81151 | 62.6996 | 49.7363 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.5651 | 51.5068
CID=-143973659 | -18 | 25 | 30.9668 | 4 | 19 | 3.8 | 1.7524 | 147.8757 | 7.2169 | 226.0633 | 423.3026 | 391.078 | 33199.9132 | 0.53985 | 0.015345 | 2.8767 | 30.9668 | 89.0835 | -18 | 25 | 4 | 19 | 144.6004 | 665.3809 | 55.0926 | 4.6015 | 0.83022 | 85.2528 | 56.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.9668 | 51.5623
CID=-143973438 | -18 | 27.5 | 35.6287 | 4 | 21.5 | 4.3 | 1.7524 | 147.8757 | 7.2169 | 229.5813 | 424.9196 | 391.078 | 34102.7332 | 0.5971 | 0.017285 | 2.7065 | 35.6287 | 96.4295 | -18 | 27.5 | 4 | 21.5 | 144.6004 | 716.3449 | 58.2019 | 4.954 | 0.84653 | 93.2703 | 63.9462 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.6287 | 51.8719
CID=-143973341 | -18 | 30 | 40.9637 | 4 | 24 | 4.8 | 1.7524 | 147.8757 | 7.2169 | 233.1226 | 426.5097 | 391.078 | 35013.8959 | 0.65303 | 0.019557 | 2.5181 | 40.9637 | 103.15 | -18 | 30 | 4 | 24 | 144.6004 | 770.1963 | 61.9438 | 5.3264 | 0.86159 | 88.7438 | 72.2363 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.9637 | 51.8934
CID=-143973376 | -18 | 32.5 | 48.2998 | 4 | 26.5 | 5.3 | 1.7524 | 147.8757 | 7.2169 | 236.688 | 428.0733 | 391.078 | 35720.965 | 0.8927 | 0.022665 | 2.8535 | 48.2998 | 137.8233 | -18 | 32.5 | 4 | 26.5 | 144.6004 | 827.0396 | 55.5814 | 5.7195 | 0.87739 | 108.6363 | 83.6387 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.2998 | 51.389
CID=-143973535 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-143973810 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-143973713 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702741 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702644 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702679 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702838 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702617 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702520 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702555 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702714 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702989 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1225702892 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1439798436 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1439798533 | -18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1439798498 | -15 | -5 | 0 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1439798339 | -15 | -2.5 | 4.9292 | 4 | -8.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 188.676 | 402.9994 | 392.9623 | 19280.4361 | 0.23081 | 0.0061158 | 9.5658 | 4.9292 | 47.152 | -15 | -2.5 | 4 | -8.5 | 163.9401 | 267.1911 | 10.4019 | 1.6298 | 0.64494 | 48.8461 | 11.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2767 | 4.9292 | 11.8126
CID=1439798560 | -15 | 0 | 5.7776 | 4 | -6 | 0 | 1.7499 | 148.1062 | 8.1279 | 191.9873 | 404.9188 | 392.9623 | 20633.4537 | 0.22851 | 0.0062263 | 7.949 | 5.7776 | 45.9257 | -15 | 0 | 4 | -6 | 163.9401 | 292.8032 | 15.3305 | 1.786 | 0.65479 | 25.4941 | 13.4059 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.7776 | 15.1388
CID=1439798657 | -15 | 2.5 | 6.9172 | 4 | -3.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 195.3144 | 406.8092 | 392.9623 | 21721.8633 | 0.24632 | 0.0064737 | 7.0383 | 6.9172 | 48.6855 | -15 | 2.5 | 4 | -3.5 | 163.9401 | 320.2635 | 19.4052 | 1.9535 | 0.66748 | 54.4416 | 15.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 6.9172 | 18.8847
CID=1439798622 | -15 | 5 | 8.3095 | 4 | -1 | 0 | 1.7499 | 148.1062 | 8.1279 | 198.6579 | 408.6707 | 392.9623 | 23390.8443 | 0.27855 | 0.0068532 | 6.5135 | 8.3095 | 54.1241 | -15 | 5 | 4 | -1 | 163.9401 | 349.6586 | 22.4971 | 2.1328 | 0.68215 | 33.7811 | 18.5076 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.3095 | 23.1137
CID=1439798463 | -15 | 7.5 | 9.7669 | 4 | 1.5 | 0.3 | 1.7499 | 148.1062 | 8.1279 | 202.0183 | 410.5034 | 392.9623 | 24395.4136 | 0.29966 | 0.0073118 | 5.8584 | 9.7669 | 57.2178 | -15 | 7.5 | 4 | 1.5 | 163.9401 | 381.0767 | 26.3235 | 2.3245 | 0.6966 | 58.2948 | 21.3024 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.7669 | 26.7752
CID=1439798188 | -15 | 10 | 11.7699 | 4 | 4 | 0.8 | 1.7499 | 148.1062 | 8.1279 | 205.396 | 412.3077 | 392.9623 | 25606.282 | 0.33512 | 0.007961 | 5.3405 | 11.7699 | 62.8576 | -15 | 10 | 4 | 4 | 163.9401 | 414.6075 | 29.9892 | 2.529 | 0.71504 | 62.2541 | 25.0093 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.7699 | 32.0031
CID=1439798285 | -15 | 12.5 | 13.601 | 4 | 6.5 | 1.3 | 1.7499 | 148.1062 | 8.1279 | 208.7918 | 414.0836 | 392.9623 | 26678.3161 | 0.35513 | 0.0086149 | 4.8088 | 13.601 | 65.4046 | -15 | 12.5 | 4 | 6.5 | 163.9401 | 450.3422 | 34.0619 | 2.747 | 0.73055 | 80.1564 | 28.2862 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.601 | 37.5469
CID=358069257 | -15 | 15 | 15.8508 | 4 | 9 | 1.8 | 1.7499 | 148.1062 | 8.1279 | 212.2062 | 415.8315 | 392.9623 | 27790.5727 | 0.38782 | 0.0094313 | 4.4226 | 15.8508 | 70.1013 | -15 | 15 | 4 | 9 | 163.9401 | 488.3739 | 37.5901 | 2.979 | 0.74802 | 73.8512 | 32.1952 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.8508 | 41.9673
CID=358069354 | -15 | 17.5 | 18.3412 | 4 | 11.5 | 2.3 | 1.7499 | 148.1062 | 8.1279 | 215.6398 | 417.5513 | 392.9623 | 29150.3034 | 0.423 | 0.010367 | 4.0896 | 18.3412 | 75.0077 | -15 | 17.5 | 4 | 11.5 | 163.9401 | 528.7968 | 40.9968 | 3.2255 | 0.76549 | 55.7862 | 36.4038 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.3412 | 47.8386
CID=358069319 | -15 | 20 | 21.1691 | 4 | 14 | 2.8 | 1.7499 | 148.1062 | 8.1279 | 219.0933 | 419.2435 | 392.9623 | 30364.4155 | 0.45633 | 0.011456 | 3.748 | 21.1691 | 79.3409 | -15 | 20 | 4 | 14 | 163.9401 | 571.7069 | 44.8596 | 3.4873 | 0.78318 | 70.3084 | 41.0674 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.1691 | 53.5948
CID=358069160 | -15 | 22.5 | 24.0585 | 4 | 16.5 | 3.3 | 1.7499 | 148.1062 | 8.1279 | 222.5675 | 420.9082 | 392.9623 | 31138.8779 | 0.48757 | 0.012619 | 3.4532 | 24.0585 | 83.0788 | -15 | 22.5 | 4 | 16.5 | 163.9401 | 617.2019 | 48.5943 | 3.7648 | 0.79916 | 56.9188 | 45.7392 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.0585 | 58.447
CID=358069381 | -15 | 25 | 27.8402 | 4 | 19 | 3.8 | 1.7499 | 148.1062 | 8.1279 | 226.0633 | 422.5457 | 392.9623 | 32077.4633 | 0.53539 | 0.014134 | 3.2096 | 27.8402 | 89.3561 | -15 | 25 | 4 | 19 | 163.9401 | 665.3809 | 52.0791 | 4.0587 | 0.8173 | 61.8259 | 51.7544 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.8402 | 58.803
CID=358069478 | -15 | 27.5 | 31.3546 | 4 | 21.5 | 4.3 | 1.7499 | 148.1062 | 8.1279 | 229.5813 | 424.156 | 392.9623 | 32919.6106 | 0.58025 | 0.015631 | 3.0235 | 31.3546 | 94.8019 | -15 | 27.5 | 4 | 21.5 | 163.9401 | 716.3449 | 54.9478 | 4.3696 | 0.8317 | 67.3895 | 57.2781 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.3546 | 58.5759
CID=358069443 | -15 | 30 | 36.422 | 4 | 24 | 4.8 | 1.7499 | 148.1062 | 8.1279 | 233.1226 | 425.7396 | 392.9623 | 33446.8947 | 0.62713 | 0.017741 | 2.7522 | 36.422 | 100.2402 | -15 | 30 | 4 | 24 | 163.9401 | 770.1963 | 59.604 | 4.698 | 0.84899 | 97.474 | 65.1803 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.422 | 57.9392
CID=358069284 | -15 | 32.5 | 41.4958 | 4 | 26.5 | 5.3 | 1.7499 | 148.1062 | 8.1279 | 236.688 | 427.2966 | 392.9623 | 34403.2055 | 0.689 | 0.019957 | 2.5948 | 41.4958 | 107.6726 | -15 | 32.5 | 4 | 26.5 | 163.9401 | 827.0396 | 62.5536 | 5.0448 | 0.86291 | 88.6685 | 73.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.4958 | 58.3942
CID=358069009 | -15 | 35 | 48.0343 | 4 | 29 | 5.8 | 1.7499 | 148.1062 | 8.1279 | 240.2788 | 428.8272 | 392.9623 | 35030.8743 | 0.91585 | 0.023113 | 2.8636 | 48.8316 | 139.8351 | -15 | 35 | 4 | 29 | 163.9401 | 886.981 | 57.7728 | 5.4104 | 0.87835 | 108.0498 | 84.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.0343 | 58.9531
CID=358069106 | -15 | 37.5 | 55.3815 | 4 | 31.5 | 6.3 | 1.7499 | 148.1062 | 8.1279 | 243.8959 | 430.3317 | 392.9623 | 35901.5738 | 1.0168 | 0.026135 | 2.7369 | 55.3815 | 151.5714 | -15 | 37.5 | 4 | 31.5 | 163.9401 | 950.1287 | 59.9214 | 5.7956 | 0.88858 | 108.6795 | 94.6947 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.3815 | 56.5848
CID=-175922982 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175922885 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175922920 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175923079 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175922858 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175922761 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175922796 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175922955 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175923230 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-175923133 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1257652161 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1257652064 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1257652099 | -15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1257652258 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1257652037 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1257651940 | -12 | 0 | 5.4538 | 4 | -6 | 0 | 1.7476 | 148.2918 | 9.1273 | 191.9873 | 404.2823 | 394.8346 | 19506.833 | 0.27809 | 0.0061513 | 10.3431 | 5.4538 | 56.4089 | -12 | 0 | 4 | -6 | 185.2442 | 292.8032 | 12.3867 | 1.5806 | 0.65107 | 48.2813 | 12.7269 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.4538 | 12.3991
CID=-1257651975 | -12 | 2.5 | 5.9439 | 4 | -3.5 | 0 | 1.7476 | 148.2918 | 9.1273 | 195.3144 | 406.166 | 394.8346 | 19961.5922 | 0.25286 | 0.0062857 | 8.4879 | 5.9439 | 50.4513 | -12 | 2.5 | 4 | -3.5 | 185.2442 | 320.2635 | 16.8044 | 1.7289 | 0.65668 | 39.5045 | 13.7523 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.9439 | 15.6403
CID=-1257652134 | -12 | 5 | 7.3298 | 4 | -1 | 0 | 1.7476 | 148.2918 | 9.1273 | 198.6579 | 408.021 | 394.8346 | 21495.4908 | 0.27728 | 0.0065937 | 7.421 | 7.3298 | 54.395 | -12 | 5 | 4 | -1 | 185.2442 | 349.6586 | 21.0488 | 1.8876 | 0.67192 | 23.1904 | 16.5743 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.3298 | 19.5445
CID=-1257652409 | -12 | 7.5 | 8.5649 | 4 | 1.5 | 0.3 | 1.7476 | 148.2918 | 9.1273 | 202.0183 | 409.8472 | 394.8346 | 22770.6834 | 0.29758 | 0.0069619 | 6.6992 | 8.5649 | 57.3778 | -12 | 7.5 | 4 | 1.5 | 185.2442 | 381.0767 | 24.4878 | 2.0572 | 0.68475 | 41.8588 | 19.0041 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.5649 | 23.9769
CID=-1257652312 | -12 | 10 | 9.993 | 4 | 4 | 0.8 | 1.7476 | 148.2918 | 9.1273 | 205.396 | 411.6451 | 394.8346 | 23790.5547 | 0.32193 | 0.0074257 | 6.1028 | 9.993 | 60.9851 | -12 | 10 | 4 | 4 | 185.2442 | 414.6075 | 27.8145 | 2.2382 | 0.69876 | 61.261 | 21.7283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.993 | 27.8065
CID=1407849016 | -12 | 12.5 | 12.1391 | 4 | 6.5 | 1.3 | 1.7476 | 148.2918 | 9.1273 | 208.7918 | 413.4146 | 394.8346 | 25308.532 | 0.35732 | 0.0081259 | 5.4763 | 12.1391 | 66.4771 | -12 | 12.5 | 4 | 6.5 | 185.2442 | 450.3422 | 31.8388 | 2.4311 | 0.71826 | 49.8893 | 25.6778 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.1391 | 33.2299
CID=1407849113 | -12 | 15 | 14.0304 | 4 | 9 | 1.8 | 1.7476 | 148.2918 | 9.1273 | 212.2062 | 415.1561 | 394.8346 | 26148.2509 | 0.38111 | 0.0088098 | 4.9607 | 14.0304 | 69.6008 | -12 | 15 | 4 | 9 | 185.2442 | 488.3739 | 35.598 | 2.6364 | 0.73402 | 66.5078 | 29.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.0304 | 39.1019
CID=1407849078 | -12 | 17.5 | 16.4121 | 4 | 11.5 | 2.3 | 1.7476 | 148.2918 | 9.1273 | 215.6398 | 416.8697 | 394.8346 | 27273.4437 | 0.41667 | 0.0096803 | 4.5494 | 16.4121 | 74.666 | -12 | 17.5 | 4 | 11.5 | 185.2442 | 528.7968 | 39.1271 | 2.8546 | 0.75212 | 92.6914 | 33.1537 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.4121 | 45.5079
CID=1407848919 | -12 | 20 | 19.032 | 4 | 14 | 2.8 | 1.7476 | 148.2918 | 9.1273 | 219.0933 | 418.5557 | 394.8346 | 28500.8573 | 0.45496 | 0.010672 | 4.2011 | 19.032 | 79.9559 | -12 | 20 | 4 | 14 | 185.2442 | 571.7069 | 42.4941 | 3.0862 | 0.77001 | 66.6215 | 37.5529 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.032 | 50.1624
CID=1407849140 | -12 | 22.5 | 21.8538 | 4 | 16.5 | 3.3 | 1.7476 | 148.2918 | 9.1273 | 222.5675 | 420.2141 | 394.8346 | 29439.1276 | 0.48981 | 0.01178 | 3.861 | 21.8538 | 84.3782 | -12 | 22.5 | 4 | 16.5 | 185.2442 | 617.2019 | 46.1233 | 3.3318 | 0.78715 | 62.5662 | 42.182 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.8538 | 56.7855
CID=1407849237 | -12 | 25 | 24.9272 | 4 | 19 | 3.8 | 1.7476 | 148.2918 | 9.1273 | 226.0633 | 421.8454 | 394.8346 | 30834.1602 | 0.52326 | 0.013024 | 3.5428 | 24.9272 | 88.3118 | -12 | 25 | 4 | 19 | 185.2442 | 665.3809 | 49.9275 | 3.5919 | 0.80359 | 54.2826 | 47.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.9272 | 62.9919
CID=1407849202 | -12 | 27.5 | 28.6206 | 4 | 21.5 | 4.3 | 1.7476 | 148.2918 | 9.1273 | 229.5813 | 423.4496 | 394.8346 | 31481.494 | 0.57424 | 0.014536 | 3.3156 | 28.6206 | 94.8951 | -12 | 27.5 | 4 | 21.5 | 185.2442 | 716.3449 | 53.0039 | 3.867 | 0.82069 | 61.2745 | 52.9853 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.6206 | 65.6702
CID=1407849043 | -12 | 30 | 32.3085 | 4 | 24 | 4.8 | 1.7476 | 148.2918 | 9.1273 | 233.1226 | 425.027 | 394.8346 | 32407.1128 | 0.61326 | 0.01612 | 3.0695 | 32.3085 | 99.1718 | -12 | 30 | 4 | 24 | 185.2442 | 770.1963 | 56.5951 | 4.1577 | 0.83525 | 63.4174 | 58.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.3085 | 65.9405
CID=1407848768 | -12 | 32.5 | 36.6126 | 4 | 26.5 | 5.3 | 1.7476 | 148.2918 | 9.1273 | 236.688 | 426.5779 | 394.8346 | 33130.2278 | 0.65554 | 0.017998 | 2.8316 | 36.6126 | 103.6717 | -12 | 32.5 | 4 | 26.5 | 185.2442 | 827.0396 | 60.4543 | 4.4646 | 0.84957 | 73.0304 | 65.4767 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.6126 | 65.8016
CID=1407848865 | -12 | 35 | 42.4028 | 4 | 29 | 5.8 | 1.7476 | 148.2918 | 9.1273 | 240.2788 | 428.1024 | 394.8346 | 33711.6849 | 0.72341 | 0.020507 | 2.6368 | 42.4029 | 111.807 | -12 | 35 | 4 | 29 | 185.2442 | 886.981 | 63.975 | 4.7882 | 0.86509 | 98.6211 | 74.4711 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.4028 | 65.639
CID=326119837 | -12 | 37.5 | 47.9875 | 4 | 31.5 | 6.3 | 1.7476 | 148.2918 | 9.1273 | 243.8959 | 429.6009 | 394.8346 | 34650.3662 | 0.79002 | 0.023068 | 2.4849 | 47.9875 | 119.2445 | -12 | 37.5 | 4 | 31.5 | 185.2442 | 950.1287 | 66.9021 | 5.1291 | 0.87682 | 86.6769 | 83.1527 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.9875 | 66.1098
CID=326119934 | -12 | 40 | 55.8685 | 4 | 34 | 6.8 | 1.7476 | 148.2918 | 9.1273 | 247.5407 | 431.0734 | 394.8346 | 35230.9901 | 1.029 | 0.026688 | 2.7062 | 56.0088 | 151.5725 | -12 | 40 | 4 | 34 | 185.2442 | 1016.593 | 62.7765 | 5.4879 | 0.88941 | 107.8586 | 95.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.8685 | 66.0993
CID=326119899 | -12 | 42.5 | 63.1387 | 4 | 36.5 | 7.3 | 1.7476 | 148.2918 | 9.1273 | 251.2145 | 432.5204 | 394.8346 | 36054.428 | 1.1526 | 0.030154 | 2.6217 | 63.1387 | 165.5334 | -12 | 42.5 | 4 | 36.5 | 185.2442 | 1086.4865 | 64.2913 | 5.8652 | 0.89749 | 108.5764 | 106.8864 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1387 | 63.9602
CID=326119740 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=326119961 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=326120058 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=326120023 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=326119864 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=326119589 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=326119686 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-740968703 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2044930618 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1866955127 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=562993212 | -12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=179911661 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1124050254 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1507131805 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1483873576 | -9 | 2.5 | 5.8776 | 4 | -3.5 | 0 | 1.7455 | 148.4312 | 10.2212 | 195.3144 | 405.5712 | 396.6938 | 19503.1117 | 0.33179 | 0.0062218 | 11.3679 | 5.8776 | 66.8166 | -9 | 2.5 | 4 | -3.5 | 208.6448 | 320.2635 | 13.9539 | 1.535 | 0.65593 | 53.136 | 13.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0754 | 5.8776 | 10.3709
CID=1100792025 | -9 | 5 | 5.9672 | 4 | -1 | 0 | 1.7455 | 148.4312 | 10.2212 | 198.6579 | 407.4201 | 396.6938 | 19549.1916 | 0.26675 | 0.006335 | 8.8527 | 5.9672 | 52.8262 | -9 | 5 | 4 | -1 | 208.6448 | 349.6586 | 18.6776 | 1.6759 | 0.65695 | 37.4487 | 13.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.9672 | 16.0914
CID=-203169890 | -9 | 7.5 | 7.3549 | 4 | 1.5 | 0.3 | 1.7455 | 148.4312 | 10.2212 | 202.0183 | 409.2404 | 396.6938 | 21131.5111 | 0.28919 | 0.0066491 | 7.6546 | 7.3549 | 56.299 | -9 | 7.5 | 4 | 1.5 | 208.6448 | 381.0767 | 22.9894 | 1.8264 | 0.67218 | 26.1857 | 16.6244 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.3549 | 20.1873
CID=-740965504 | -9 | 10 | 8.9222 | 4 | 4 | 0.8 | 1.7455 | 148.4312 | 10.2212 | 205.396 | 411.0322 | 396.6938 | 22130.5667 | 0.3238 | 0.0070981 | 6.9424 | 8.9222 | 61.9417 | -9 | 10 | 4 | 4 | 208.6448 | 414.6075 | 26.3539 | 1.9871 | 0.68834 | 54.3169 | 19.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.9222 | 24.8293
CID=-2044927419 | -9 | 12.5 | 10.5321 | 4 | 6.5 | 1.3 | 1.7455 | 148.4312 | 10.2212 | 208.7918 | 412.7959 | 396.6938 | 23577.0041 | 0.35649 | 0.007623 | 6.3601 | 10.5322 | 66.9855 | -9 | 12.5 | 4 | 6.5 | 208.6448 | 450.3422 | 29.453 | 2.1584 | 0.70383 | 42.6137 | 22.7355 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.5321 | 29.3656
CID=1866958326 | -9 | 15 | 12.3102 | 4 | 9 | 1.8 | 1.7455 | 148.4312 | 10.2212 | 212.2062 | 414.5315 | 396.6938 | 24645.2872 | 0.37863 | 0.0082413 | 5.6744 | 12.3102 | 69.8526 | -9 | 15 | 4 | 9 | 208.6448 | 488.3739 | 33.3655 | 2.3407 | 0.71974 | 54.8427 | 25.9863 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.3102 | 34.4149
CID=562996411 | -9 | 17.5 | 14.7558 | 4 | 11.5 | 2.3 | 1.7455 | 148.4312 | 10.2212 | 215.6398 | 416.2392 | 396.6938 | 25710.6567 | 0.42329 | 0.0090962 | 5.1938 | 14.7558 | 76.6383 | -9 | 17.5 | 4 | 11.5 | 208.6448 | 528.7968 | 36.7697 | 2.5344 | 0.73973 | 63.0036 | 30.3071 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.7558 | 40.7191
CID=179914860 | -9 | 20 | 16.9978 | 4 | 14 | 2.8 | 1.7455 | 148.4312 | 10.2212 | 219.0933 | 417.9194 | 396.6938 | 26744.7514 | 0.44907 | 0.0099435 | 4.6921 | 16.9978 | 79.7558 | -9 | 20 | 4 | 14 | 208.6448 | 571.7069 | 40.6239 | 2.7401 | 0.7563 | 80.1564 | 34.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.9978 | 47.3518
CID=-1124047055 | -9 | 22.5 | 19.6774 | 4 | 16.5 | 3.3 | 1.7455 | 148.4312 | 10.2212 | 222.5675 | 419.5721 | 396.6938 | 27779.9693 | 0.48789 | 0.010973 | 4.3173 | 19.6774 | 84.9539 | -9 | 22.5 | 4 | 16.5 | 208.6448 | 617.2019 | 44.0184 | 2.9581 | 0.77412 | 82.824 | 38.6205 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.6774 | 52.6566
CID=-1507128606 | -9 | 25 | 22.5308 | 4 | 19 | 3.8 | 1.7455 | 148.4312 | 10.2212 | 226.0633 | 421.1976 | 396.6938 | 29096.9848 | 0.52519 | 0.01211 | 3.9773 | 22.5308 | 89.6127 | -9 | 25 | 4 | 19 | 208.6448 | 665.3809 | 47.4516 | 3.1891 | 0.79096 | 54.6982 | 43.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.5308 | 59.4656
CID=1483876775 | -9 | 27.5 | 25.7566 | 4 | 21.5 | 4.3 | 1.7455 | 148.4312 | 10.2212 | 229.5813 | 422.7961 | 396.6938 | 30101.9203 | 0.56091 | 0.013427 | 3.6393 | 25.7566 | 93.7354 | -9 | 27.5 | 4 | 21.5 | 208.6448 | 716.3449 | 51.2608 | 3.4333 | 0.80767 | 70.3102 | 48.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.7566 | 66.4236
CID=1100795224 | -9 | 30 | 29.1758 | 4 | 24 | 4.8 | 1.7455 | 148.4312 | 10.2212 | 233.1226 | 424.3678 | 396.6938 | 31056.9588 | 0.59957 | 0.014873 | 3.3614 | 29.1759 | 98.0724 | -9 | 30 | 4 | 24 | 208.6448 | 770.1963 | 54.7933 | 3.6914 | 0.82303 | 57.0093 | 53.8596 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.1758 | 73.3333
CID=-203166691 | -9 | 32.5 | 33.425 | 4 | 26.5 | 5.3 | 1.7455 | 148.4312 | 10.2212 | 236.688 | 425.913 | 396.6938 | 31874.845 | 0.65036 | 0.01668 | 3.1133 | 33.425 | 104.0621 | -9 | 32.5 | 4 | 26.5 | 208.6448 | 827.0396 | 58.3193 | 3.9639 | 0.83922 | 59.0954 | 60.5131 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.425 | 73.7137
CID=-740966657 | -9 | 35 | 37.4523 | 4 | 29 | 5.8 | 1.7455 | 148.4312 | 10.2212 | 240.2788 | 427.4319 | 396.6938 | 32694.6943 | 0.70423 | 0.018497 | 2.9412 | 37.4523 | 110.1528 | -9 | 35 | 4 | 29 | 208.6448 | 886.981 | 60.9867 | 4.2512 | 0.85207 | 62.6993 | 66.782 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 37.4523 | 73.3536
CID=-2044928572 | -9 | 37.5 | 42.9142 | 4 | 31.5 | 6.3 | 1.7455 | 148.4312 | 10.2212 | 243.8959 | 428.9247 | 396.6938 | 33266.5719 | 0.75614 | 0.02093 | 2.6923 | 42.9142 | 115.5367 | -9 | 37.5 | 4 | 31.5 | 208.6448 | 950.1287 | 65.1947 | 4.5538 | 0.86629 | 85.2522 | 75.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.9142 | 73.3866
CID=1866957173 | -9 | 40 | 49.0108 | 4 | 34 | 6.8 | 1.7455 | 148.4312 | 10.2212 | 247.5407 | 430.3916 | 396.6938 | 33969.3119 | 0.8291 | 0.023728 | 2.5232 | 49.0108 | 123.6635 | -9 | 40 | 4 | 34 | 208.6448 | 1016.593 | 68.3481 | 4.8724 | 0.87867 | 97.8722 | 84.746 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.0108 | 74.0486
CID=562995258 | -9 | 42.5 | 55.1264 | 4 | 36.5 | 7.3 | 1.7455 | 148.4312 | 10.2212 | 251.2145 | 431.833 | 396.6938 | 34847.7227 | 0.90059 | 0.026681 | 2.3767 | 55.1264 | 131.0173 | -9 | 42.5 | 4 | 36.5 | 208.6448 | 1086.4865 | 71.2562 | 5.2074 | 0.88823 | 86.6769 | 94.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.1264 | 74.5178
CID=179913707 | -9 | 45 | 64.4822 | 4 | 39 | 7.8 | 1.7455 | 148.4312 | 10.2212 | 254.9187 | 433.2489 | 396.6938 | 35484.7536 | 1.0794 | 0.031078 | 2.3732 | 64.4822 | 153.0301 | -9 | 45 | 4 | 39 | 208.6448 | 1159.9242 | 71.271 | 5.5593 | 0.89875 | 102.7168 | 109.0072 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.4822 | 74.5276
CID=-1124048208 | -9 | 47.5 | 71.7723 | 4 | 41.5 | 8.3 | 1.7455 | 148.4312 | 10.2212 | 258.655 | 434.6398 | 396.6938 | 36119.6991 | 1.3082 | 0.034478 | 2.5514 | 70.7774 | 180.5813 | -9 | 47.5 | 4 | 41.5 | 208.6448 | 1237.0237 | 67.9309 | 5.9289 | 0.90379 | 109.5196 | 118.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.7723 | 70.7774
CID=-1507129759 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1483875622 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1100794071 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-203167844 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-740971906 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2044933821 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1866951924 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=562990009 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=179908458 | -9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1124053457 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1507135008 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1483870373 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1100788822 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-203173093 | -6 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-740964603 | -6 | 7.5 | 6.453 | 4 | 1.5 | 0.3 | 1.7436 | 148.523 | 11.416 | 202.0183 | 408.6791 | 398.5385 | 19308.8299 | 0.32457 | 0.006441 | 9.8845 | 6.453 | 63.7848 | -6 | 7.5 | 4 | 1.5 | 234.2779 | 381.0767 | 19.7464 | 1.6266 | 0.66239 | 48.8177 | 14.8016 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3081 | 6.453 | 16.4601
CID=-2044926518 | -6 | 10 | 7.6696 | 4 | 4 | 0.8 | 1.7436 | 148.523 | 11.416 | 205.396 | 410.4654 | 398.5385 | 20614.2797 | 0.32387 | 0.0067622 | 8.1559 | 7.6696 | 62.5527 | -6 | 10 | 4 | 4 | 234.2779 | 414.6075 | 24.4421 | 1.7697 | 0.67552 | 24.4933 | 17.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.6696 | 20.8178
CID=1866959227 | -6 | 12.5 | 9.2176 | 4 | 6.5 | 1.3 | 1.7436 | 148.523 | 11.416 | 208.7918 | 412.2236 | 398.5385 | 21631.0228 | 0.34884 | 0.0072254 | 7.1809 | 9.2176 | 66.1909 | -6 | 12.5 | 4 | 6.5 | 234.2779 | 450.3422 | 28.2662 | 1.9223 | 0.69126 | 54.5966 | 20.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.2176 | 25.6674
CID=562997312 | -6 | 15 | 10.7286 | 4 | 9 | 1.8 | 1.7436 | 148.523 | 11.416 | 212.2062 | 413.9537 | 398.5385 | 23132.1282 | 0.37376 | 0.0077381 | 6.4914 | 10.7286 | 69.6433 | -6 | 15 | 4 | 9 | 234.2779 | 488.3739 | 31.5636 | 2.0846 | 0.70565 | 34.3344 | 23.0999 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.7286 | 31.091
CID=179915761 | -6 | 17.5 | 12.814 | 4 | 11.5 | 2.3 | 1.7436 | 148.523 | 11.416 | 215.6398 | 415.6561 | 398.5385 | 24012.0397 | 0.41881 | 0.0084532 | 5.9777 | 12.814 | 76.5991 | -6 | 17.5 | 4 | 11.5 | 234.2779 | 528.7968 | 34.5698 | 2.2571 | 0.72403 | 61.2612 | 26.8895 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.814 | 35.6449
CID=-1124046154 | -6 | 20 | 15.1569 | 4 | 14 | 2.8 | 1.7436 | 148.523 | 11.416 | 219.0933 | 417.3308 | 398.5385 | 25445.666 | 0.4485 | 0.0092955 | 5.3099 | 15.1569 | 80.4813 | -6 | 20 | 4 | 14 | 234.2779 | 571.7069 | 38.6807 | 2.4403 | 0.74281 | 48.8275 | 31.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.1569 | 42.1821
CID=-1507127705 | -6 | 22.5 | 17.5255 | 4 | 16.5 | 3.3 | 1.7436 | 148.523 | 11.416 | 222.5675 | 418.9782 | 398.5385 | 26226.7475 | 0.48141 | 0.010197 | 4.8338 | 17.5255 | 84.714 | -6 | 22.5 | 4 | 16.5 | 234.2779 | 617.2019 | 42.2015 | 2.6345 | 0.75997 | 66.5078 | 35.0371 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.5255 | 49.1571
CID=1483877676 | -6 | 25 | 20.3432 | 4 | 19 | 3.8 | 1.7436 | 148.523 | 11.416 | 226.0633 | 420.5983 | 398.5385 | 27292.834 | 0.52281 | 0.011288 | 4.4325 | 20.3432 | 90.1714 | -6 | 25 | 4 | 19 | 234.2779 | 665.3809 | 45.6245 | 2.8401 | 0.77823 | 93.7863 | 39.7161 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.3432 | 56.7809
CID=1100796125 | -6 | 27.5 | 23.3062 | 4 | 21.5 | 4.3 | 1.7436 | 148.523 | 11.416 | 229.5813 | 422.1916 | 398.5385 | 28425.2306 | 0.56264 | 0.012482 | 4.0788 | 23.3062 | 95.0613 | -6 | 27.5 | 4 | 21.5 | 234.2779 | 716.3449 | 49.0122 | 3.0577 | 0.79519 | 66.6222 | 44.5303 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.3062 | 62.1448
CID=-203165790 | -6 | 30 | 26.4924 | 4 | 24 | 4.8 | 1.7436 | 148.523 | 11.416 | 233.1226 | 423.758 | 398.5385 | 29427.5449 | 0.60074 | 0.01381 | 3.751 | 26.4924 | 99.3727 | -6 | 30 | 4 | 24 | 234.2779 | 770.1963 | 52.517 | 3.2875 | 0.81117 | 62.5654 | 49.6209 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.4924 | 69.9107
CID=-740961404 | -6 | 32.5 | 30.2611 | 4 | 26.5 | 5.3 | 1.7436 | 148.523 | 11.416 | 236.688 | 425.298 | 398.5385 | 30699.7058 | 0.64586 | 0.015403 | 3.4543 | 30.2612 | 104.5323 | -6 | 32.5 | 4 | 26.5 | 234.2779 | 827.0396 | 56.0833 | 3.5302 | 0.82745 | 55.9169 | 55.5646 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.2611 | 77.2504
CID=-2044923319 | -6 | 35 | 34.2819 | 4 | 29 | 5.8 | 1.7436 | 148.523 | 11.416 | 240.2788 | 426.8116 | 398.5385 | 31301.2074 | 0.69712 | 0.017165 | 3.2182 | 34.2819 | 110.3262 | -6 | 35 | 4 | 29 | 234.2779 | 886.981 | 59.2516 | 3.786 | 0.84215 | 59.3723 | 61.849 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.2819 | 82.4485
CID=1866962426 | -6 | 37.5 | 39.1102 | 4 | 31.5 | 6.3 | 1.7436 | 148.523 | 11.416 | 243.8959 | 428.2991 | 398.5385 | 32173.062 | 0.7553 | 0.019307 | 2.9865 | 39.1102 | 116.8016 | -6 | 37.5 | 4 | 31.5 | 234.2779 | 950.1287 | 62.6591 | 4.0556 | 0.85674 | 61.8259 | 69.3578 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.1102 | 82.9524
CID=563000511 | -6 | 40 | 43.5036 | 4 | 34 | 6.8 | 1.7436 | 148.523 | 11.416 | 247.5407 | 429.7609 | 398.5385 | 32942.8051 | 0.81204 | 0.021398 | 2.8185 | 43.5036 | 122.6164 | -6 | 40 | 4 | 34 | 234.2779 | 1016.593 | 65.3408 | 4.3393 | 0.86763 | 64.603 | 76.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.5036 | 82.5148
CID=179918960 | -6 | 42.5 | 49.8837 | 4 | 36.5 | 7.3 | 1.7436 | 148.523 | 11.416 | 251.2145 | 431.197 | 398.5385 | 33385.3299 | 0.86644 | 0.024354 | 2.5589 | 49.8837 | 127.6474 | -6 | 42.5 | 4 | 36.5 | 234.2779 | 1086.4865 | 69.8888 | 4.6376 | 0.8802 | 97.4739 | 86.1062 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.8837 | 81.3364
CID=-1124042955 | -6 | 45 | 56.269 | 4 | 39 | 7.8 | 1.7436 | 148.523 | 11.416 | 254.9187 | 432.6077 | 398.5385 | 34206.5574 | 0.94465 | 0.027472 | 2.4111 | 56.269 | 135.6701 | -6 | 45 | 4 | 39 | 234.2779 | 1159.9242 | 72.7335 | 4.9511 | 0.88975 | 93.2704 | 96.0849 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.269 | 82.5395
CID=-1507124506 | -6 | 47.5 | 63.1967 | 4 | 41.5 | 8.3 | 1.7436 | 148.523 | 11.416 | 258.655 | 433.9933 | 398.5385 | 35014.3211 | 1.021 | 0.030983 | 2.26 | 63.1968 | 142.8232 | -6 | 47.5 | 4 | 41.5 | 234.2779 | 1237.0237 | 75.8442 | 5.2802 | 0.89755 | 87.0428 | 106.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1967 | 82.9402
CID=1483880875 | -6 | 50 | 73.7545 | 4 | 44 | 8.8 | 1.7436 | 148.523 | 11.416 | 262.425 | 435.3541 | 398.5385 | 35681.4579 | 1.1515 | 0.036193 | 2.125 | 73.7545 | 156.729 | -6 | 50 | 4 | 44 | 234.2779 | 1317.9055 | 78.8416 | 5.6254 | 0.90574 | 98.7658 | 123.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.7545 | 82.3271
CID=1100799324 | -6 | 52.5 | 81.6054 | 4 | 46.5 | 9.3 | 1.7436 | 148.523 | 11.416 | 266.2308 | 436.6902 | 398.5385 | 36189.9086 | 1.461 | 0.039595 | 2.437 | 79.3179 | 193.2958 | -6 | 52.5 | 4 | 46.5 | 234.2779 | 1402.6932 | 72.3832 | 5.9873 | 0.90877 | 109.5619 | 132.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 81.6054 | 79.3179
CID=-203162591 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-740962557 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2044924472 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1866961273 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=562999358 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=179917807 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1124044108 | -6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1507125659 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1483879722 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1100798171 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-203163744 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-740967806 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2044929721 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1866956024 | -3 | 10 | 7.2395 | 4 | 4 | 0.8 | 1.7418 | 148.5658 | 12.7186 | 205.396 | 409.9411 | 400.3675 | 19542.8754 | 0.39019 | 0.0066181 | 10.5083 | 7.2396 | 76.0756 | -3 | 10 | 4 | 4 | 262.283 | 414.6075 | 21.8236 | 1.5808 | 0.67095 | 48.7413 | 16.3937 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.2395 | 17.0303
CID=562994109 | -3 | 12.5 | 7.8059 | 4 | 6.5 | 1.3 | 1.7418 | 148.5658 | 12.7186 | 208.7918 | 411.6941 | 400.3675 | 19945.2242 | 0.35194 | 0.0068449 | 8.6374 | 7.8059 | 67.4228 | -3 | 12.5 | 4 | 6.5 | 262.283 | 450.3422 | 26.0147 | 1.717 | 0.67694 | 39.5045 | 17.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.8059 | 21.4254
CID=179912558 | -3 | 15 | 9.5793 | 4 | 9 | 1.8 | 1.7418 | 148.5658 | 12.7186 | 212.2062 | 413.4192 | 400.3675 | 21462.2875 | 0.37714 | 0.0073738 | 7.4081 | 9.5793 | 70.9637 | -3 | 15 | 4 | 9 | 262.283 | 488.3739 | 30.284 | 1.862 | 0.69479 | 23.1822 | 20.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.5793 | 26.4523
CID=-1124049357 | -3 | 17.5 | 11.3834 | 4 | 11.5 | 2.3 | 1.7418 | 148.5658 | 12.7186 | 215.6398 | 415.1165 | 400.3675 | 22520.4442 | 0.41717 | 0.0079791 | 6.7698 | 11.3834 | 77.063 | -3 | 17.5 | 4 | 11.5 | 262.283 | 528.7968 | 33.2767 | 2.0161 | 0.7116 | 48.6046 | 24.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.3834 | 32.0983
CID=-1507130908 | -3 | 20 | 13.1276 | 4 | 14 | 2.8 | 1.7418 | 148.5658 | 12.7186 | 219.0933 | 416.7863 | 400.3675 | 23672.8683 | 0.44488 | 0.0086177 | 6.1431 | 13.1276 | 80.6445 | -3 | 20 | 4 | 14 | 262.283 | 571.7069 | 36.4717 | 2.1797 | 0.72666 | 50.8872 | 27.448 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.1276 | 36.8384
CID=1483874473 | -3 | 22.5 | 15.3536 | 4 | 16.5 | 3.3 | 1.7418 | 148.5658 | 12.7186 | 222.5675 | 418.4287 | 400.3675 | 24838.4446 | 0.4724 | 0.0094399 | 5.4705 | 15.3536 | 83.992 | -3 | 22.5 | 4 | 16.5 | 262.283 | 617.2019 | 40.3675 | 2.3532 | 0.74431 | 51.8419 | 31.3411 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.3536 | 43.5534
CID=1100792922 | -3 | 25 | 18.2962 | 4 | 19 | 3.8 | 1.7418 | 148.5658 | 12.7186 | 226.0633 | 420.0439 | 400.3675 | 25773.9195 | 0.52799 | 0.010532 | 5.0301 | 18.2962 | 92.0311 | -3 | 25 | 4 | 19 | 262.283 | 665.3809 | 43.5459 | 2.5369 | 0.76519 | 63.6246 | 36.3285 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.2962 | 51.0495
CID=-203168993 | -3 | 27.5 | 20.9887 | 4 | 21.5 | 4.3 | 1.7418 | 148.5658 | 12.7186 | 229.5813 | 421.6322 | 400.3675 | 26769.4168 | 0.56013 | 0.011605 | 4.5578 | 20.9887 | 95.6618 | -3 | 27.5 | 4 | 21.5 | 262.283 | 716.3449 | 47.2213 | 2.7312 | 0.78211 | 80.1564 | 40.773 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.9887 | 58.877
CID=-740976903 | -3 | 30 | 24.0589 | 4 | 24 | 4.8 | 1.7418 | 148.5658 | 12.7186 | 233.1226 | 423.1938 | 400.3675 | 27742.3806 | 0.60245 | 0.012857 | 4.1879 | 24.0589 | 100.7569 | -3 | 30 | 4 | 24 | 262.283 | 770.1963 | 50.574 | 2.9365 | 0.79917 | 82.8252 | 45.7398 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.0589 | 65.4577
CID=-2044938818 | -3 | 32.5 | 27.3282 | 4 | 26.5 | 5.3 | 1.7418 | 148.5658 | 12.7186 | 236.688 | 424.7289 | 400.3675 | 29005.7773 | 0.64294 | 0.014239 | 3.8508 | 27.3282 | 105.2367 | -3 | 32.5 | 4 | 26.5 | 262.283 | 827.0396 | 53.9935 | 3.1532 | 0.81501 | 54.6982 | 50.9451 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.3282 | 72.9534
CID=1866946927 | -3 | 35 | 31.2318 | 4 | 29 | 5.8 | 1.7418 | 148.5658 | 12.7186 | 240.2788 | 426.2376 | 400.3675 | 29819.2244 | 0.69267 | 0.01591 | 3.5505 | 31.2318 | 110.8892 | -3 | 35 | 4 | 29 | 262.283 | 886.981 | 57.4228 | 3.3818 | 0.83124 | 75.6225 | 57.0858 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.2318 | 81.2868
CID=562985012 | -3 | 37.5 | 35.4207 | 4 | 31.5 | 6.3 | 1.7418 | 148.5658 | 12.7186 | 243.8959 | 427.7203 | 400.3675 | 30990.2622 | 0.74646 | 0.017766 | 3.2975 | 35.4207 | 116.7997 | -3 | 37.5 | 4 | 31.5 | 262.283 | 950.1287 | 60.6422 | 3.6225 | 0.84587 | 54.2839 | 63.6224 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.4207 | 89.2568
CID=179903461 | -3 | 40 | 40.004 | 4 | 34 | 6.8 | 1.7418 | 148.5658 | 12.7186 | 247.5407 | 429.1772 | 400.3675 | 31600.6372 | 0.80209 | 0.019862 | 3.0642 | 40.004 | 122.5814 | -3 | 40 | 4 | 34 | 262.283 | 1016.593 | 63.8983 | 3.8759 | 0.85913 | 60.8068 | 70.7459 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.004 | 91.6597
CID=-1124058454 | -3 | 42.5 | 44.8066 | 4 | 36.5 | 7.3 | 1.7418 | 148.5658 | 12.7186 | 251.2145 | 430.6085 | 400.3675 | 32430.9193 | 0.85649 | 0.022151 | 2.8511 | 44.8066 | 127.7484 | -3 | 42.5 | 4 | 36.5 | 262.283 | 1086.4865 | 67.1498 | 4.1424 | 0.87049 | 63.7098 | 78.2053 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44.8066 | 92.0158
CID=-1507140005 | -3 | 45 | 50.0122 | 4 | 39 | 7.8 | 1.7418 | 148.5658 | 12.7186 | 254.9187 | 432.0144 | 400.3675 | 33120.4591 | 0.91061 | 0.024717 | 2.6483 | 50.0122 | 132.4475 | -3 | 45 | 4 | 39 | 262.283 | 1159.9242 | 70.5265 | 4.4224 | 0.88042 | 71.0838 | 86.3065 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50.0122 | 91.8833
CID=1483865376 | -3 | 47.5 | 57.2677 | 4 | 41.5 | 8.3 | 1.7418 | 148.5658 | 12.7186 | 258.655 | 433.3951 | 400.3675 | 33574.5655 | 0.98698 | 0.028237 | 2.4423 | 57.2678 | 139.8674 | -3 | 47.5 | 4 | 41.5 | 262.283 | 1237.0237 | 74.3169 | 4.7164 | 0.89103 | 97.474 | 97.6509 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 57.2677 | 91.0918
CID=1100783825 | -3 | 50 | 64.1843 | 4 | 44 | 8.8 | 1.7418 | 148.5658 | 12.7186 | 262.425 | 434.7511 | 400.3675 | 34409.6351 | 1.0705 | 0.03182 | 2.3006 | 64.1843 | 147.6612 | -3 | 50 | 4 | 44 | 262.283 | 1317.9055 | 77.1305 | 5.0247 | 0.89848 | 93.2697 | 108.5367 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.1843 | 92.3763
CID=-203178090 | -3 | 52.5 | 72.1709 | 4 | 46.5 | 9.3 | 1.7418 | 148.5658 | 12.7186 | 266.2308 | 436.0824 | 400.3675 | 35151.6034 | 1.1517 | 0.036064 | 2.1405 | 72.1709 | 154.4839 | -3 | 52.5 | 4 | 46.5 | 262.283 | 1402.6932 | 80.5539 | 5.348 | 0.90473 | 87.0432 | 121.1984 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72.1709 | 92.7477
CID=-740973704 | -3 | 55 | 83.791 | 4 | 49 | 9.8 | 1.7418 | 148.5658 | 12.7186 | 270.0745 | 437.3893 | 400.3675 | 35833.1525 | 1.2403 | 0.042135 | 1.9287 | 83.791 | 161.6057 | -3 | 55 | 4 | 49 | 262.283 | 1491.5141 | 85.6917 | 5.6867 | 0.91074 | 95.8683 | 139.7847 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.791 | 92.0281
CID=-2044935619 | -3 | 57.5 | 92.1977 | 4 | 51.5 | 10.3 | 1.7418 | 148.5658 | 12.7186 | 273.9586 | 438.6721 | 400.3675 | 36239.4688 | 1.6267 | 0.045541 | 2.3224 | 88.544 | 205.6311 | -3 | 57.5 | 4 | 51.5 | 262.283 | 1584.4992 | 76.8958 | 6.0412 | 0.91245 | 109.5992 | 147.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.1977 | 88.544
CID=1866950126 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=562988211 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=179906660 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1124055255 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1507136806 | -3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1483868575 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1100787024 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-203174891 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1745478940 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1644722391 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=623085478 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-963201439 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1628607992 | 0 | 12.5 | 7.6527 | 4 | 6.5 | 1.3 | 1.7401 | 148.5582 | 14.1363 | 208.7918 | 411.2041 | 402.1796 | 19459.5579 | 0.45172 | 0.0067503 | 11.4153 | 7.6527 | 87.358 | 0 | 12.5 | 4 | 6.5 | 292.8032 | 450.3422 | 23.4053 | 1.538 | 0.67534 | 52.4823 | 17.2167 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1984 | 7.6527 | 15.5267
CID=-1729364541 | 0 | 15 | 7.8476 | 4 | 9 | 1.8 | 1.7401 | 148.5582 | 14.1363 | 212.2062 | 412.9246 | 402.1796 | 19565.9611 | 0.3711 | 0.0069112 | 8.9835 | 7.8476 | 70.4991 | 0 | 15 | 4 | 9 | 292.8032 | 488.3739 | 27.954 | 1.6679 | 0.67738 | 37.4507 | 17.602 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.8476 | 21.9668
CID=1543965842 | 0 | 17.5 | 9.6303 | 4 | 11.5 | 2.3 | 1.7401 | 148.5582 | 14.1363 | 215.6398 | 414.6172 | 402.1796 | 21030.4263 | 0.40206 | 0.0074505 | 7.7879 | 9.6303 | 75.0005 | 0 | 17.5 | 4 | 11.5 | 292.8032 | 528.7968 | 31.841 | 1.806 | 0.69528 | 27.8723 | 21.0444 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.6303 | 27.2198
CID=-42321075 | 0 | 20 | 11.4976 | 4 | 14 | 2.8 | 1.7401 | 148.5582 | 14.1363 | 219.0933 | 416.2824 | 402.1796 | 21896.6095 | 0.43293 | 0.0080816 | 6.8939 | 11.4976 | 79.2637 | 0 | 20 | 4 | 14 | 292.8032 | 571.7069 | 35.4631 | 1.9525 | 0.71262 | 54.331 | 24.5135 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11.4976 | 33.1226
CID=-707727628 | 0 | 22.5 | 13.7099 | 4 | 16.5 | 3.3 | 1.7401 | 148.5582 | 14.1363 | 222.5675 | 417.9202 | 402.1796 | 23408.2696 | 0.48448 | 0.0088649 | 6.3471 | 13.7099 | 87.018 | 0 | 22.5 | 4 | 16.5 | 292.8032 | 617.2019 | 38.3131 | 2.1079 | 0.73144 | 33.7811 | 28.4781 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.7099 | 39.6483
CID=-808484177 | 0 | 25 | 16.0491 | 4 | 19 | 3.8 | 1.7401 | 148.5582 | 14.1363 | 226.0633 | 419.5308 | 402.1796 | 24204.2575 | 0.52578 | 0.0097397 | 5.7696 | 16.0491 | 92.5977 | 0 | 25 | 4 | 19 | 292.8032 | 665.3809 | 41.5335 | 2.2725 | 0.74948 | 62.961 | 32.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.0491 | 44.9885
CID=1745482139 | 0 | 27.5 | 18.7183 | 4 | 21.5 | 4.3 | 1.7401 | 148.5582 | 14.1363 | 229.5813 | 421.1145 | 402.1796 | 25536.3018 | 0.55625 | 0.010768 | 5.1291 | 18.7183 | 96.0074 | 0 | 27.5 | 4 | 21.5 | 292.8032 | 716.3449 | 45.5193 | 2.4465 | 0.76797 | 47.908 | 37.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.7183 | 52.7648
CID=1644725590 | 0 | 30 | 21.6284 | 4 | 24 | 4.8 | 1.7401 | 148.5582 | 14.1363 | 233.1226 | 422.6716 | 402.1796 | 26262.2901 | 0.6 | 0.011931 | 4.6899 | 21.6284 | 101.4344 | 0 | 30 | 4 | 24 | 292.8032 | 770.1963 | 48.8431 | 2.6304 | 0.78585 | 66.5078 | 41.8156 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.6284 | 60.943
CID=623088677 | 0 | 32.5 | 24.9262 | 4 | 26.5 | 5.3 | 1.7401 | 148.5582 | 14.1363 | 236.688 | 424.2021 | 402.1796 | 27269.1381 | 0.64824 | 0.013282 | 4.3038 | 24.9263 | 107.2778 | 0 | 32.5 | 4 | 26.5 | 292.8032 | 827.0396 | 52.1611 | 2.8246 | 0.80359 | 93.3259 | 47.1279 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.9262 | 69.8742
CID=-963198240 | 0 | 35 | 28.2143 | 4 | 29 | 5.8 | 1.7401 | 148.5582 | 14.1363 | 240.2788 | 425.7063 | 402.1796 | 28315.6824 | 0.68781 | 0.014698 | 3.9469 | 28.2143 | 111.3576 | 0 | 35 | 4 | 29 | 292.8032 | 886.981 | 55.5832 | 3.0293 | 0.81894 | 66.6223 | 52.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.2143 | 76.0029
CID=-1628604793 | 0 | 37.5 | 32.0433 | 4 | 31.5 | 6.3 | 1.7401 | 148.5582 | 14.1363 | 243.8959 | 427.1845 | 402.1796 | 29351.7719 | 0.73965 | 0.016376 | 3.6536 | 32.0433 | 117.0739 | 0 | 37.5 | 4 | 31.5 | 292.8032 | 950.1287 | 58.7766 | 3.2449 | 0.83428 | 60.0732 | 58.3555 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.0433 | 84.9985
CID=-1729361342 | 0 | 40 | 36.5584 | 4 | 34 | 6.8 | 1.7401 | 148.5582 | 14.1363 | 247.5407 | 428.6369 | 402.1796 | 30474.266 | 0.79877 | 0.018387 | 3.3787 | 36.5584 | 123.5207 | 0 | 40 | 4 | 34 | 292.8032 | 1016.593 | 62.0891 | 3.4719 | 0.84941 | 70.3072 | 65.3924 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.5584 | 93.5253
CID=1543969041 | 0 | 42.5 | 40.6283 | 4 | 36.5 | 7.3 | 1.7401 | 148.5582 | 14.1363 | 251.2145 | 430.0637 | 402.1796 | 31136.8197 | 0.83564 | 0.020338 | 3.105 | 40.6283 | 126.1525 | 0 | 42.5 | 4 | 36.5 | 292.8032 | 1086.4865 | 65.6975 | 3.7106 | 0.86074 | 56.9187 | 71.7154 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.6283 | 101.9065
CID=-42317876 | 0 | 45 | 46.0942 | 4 | 39 | 7.8 | 1.7401 | 148.5582 | 14.1363 | 254.9187 | 431.4651 | 402.1796 | 31911.5406 | 0.90157 | 0.022924 | 2.8803 | 46.0942 | 132.7657 | 0 | 45 | 4 | 39 | 292.8032 | 1159.9242 | 69.033 | 3.9614 | 0.87315 | 59.0954 | 80.2069 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.0942 | 101.9148
CID=-707724429 | 0 | 47.5 | 51.0502 | 4 | 41.5 | 8.3 | 1.7401 | 148.5582 | 14.1363 | 258.655 | 432.8414 | 402.1796 | 32657.633 | 0.96576 | 0.025454 | 2.7152 | 51.0502 | 138.6103 | 0 | 47.5 | 4 | 41.5 | 292.8032 | 1237.0237 | 71.708 | 4.2248 | 0.88214 | 62.6993 | 87.9253 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51.0502 | 101.2467
CID=-808480978 | 0 | 50 | 57.491 | 4 | 44 | 8.8 | 1.7401 | 148.5582 | 14.1363 | 262.425 | 434.1928 | 402.1796 | 33227.9985 | 1.0274 | 0.028722 | 2.4976 | 57.4911 | 143.5891 | 0 | 50 | 4 | 44 | 292.8032 | 1317.9055 | 75.4931 | 4.501 | 0.8913 | 73.0307 | 98.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 57.491 | 102.1367
CID=1745480986 | 0 | 52.5 | 65.2952 | 4 | 46.5 | 9.3 | 1.7401 | 148.5582 | 14.1363 | 266.2308 | 435.5196 | 402.1796 | 33745.7022 | 1.1181 | 0.032745 | 2.328 | 65.2952 | 152.0048 | 0 | 52.5 | 4 | 46.5 | 292.8032 | 1402.6932 | 78.7476 | 4.7906 | 0.89948 | 98.6211 | 110.2921 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65.2952 | 101.6651
CID=1644724437 | 0 | 55 | 72.7779 | 4 | 49 | 9.8 | 1.7401 | 148.5582 | 14.1363 | 270.0745 | 436.822 | 402.1796 | 34566.3991 | 1.2069 | 0.036876 | 2.1908 | 72.778 | 159.4408 | 0 | 55 | 4 | 49 | 292.8032 | 1491.5141 | 81.5549 | 5.0939 | 0.90513 | 88.6685 | 122.1648 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72.7779 | 102.0387
CID=623087524 | 0 | 57.5 | 82.0777 | 4 | 51.5 | 10.3 | 1.7401 | 148.5582 | 14.1363 | 273.9586 | 438.1003 | 402.1796 | 35061.1842 | 1.5636 | 0.042946 | 2.3842 | 84.0892 | 200.4862 | 0 | 57.5 | 4 | 51.5 | 292.8032 | 1584.4992 | 77.9429 | 5.4115 | 0.91086 | 107.8072 | 140.264 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82.0777 | 102.54
CID=-963199393 | 0 | 60 | 94.1756 | 4 | 54 | 10.8 | 1.7401 | 148.5582 | 14.1363 | 277.8855 | 439.3549 | 402.1796 | 35914.8075 | 1.3827 | 0.048861 | 1.8249 | 94.1756 | 171.8654 | 0 | 60 | 4 | 54 | 292.8032 | 1681.7842 | 90.2396 | 5.7437 | 0.91407 | 95.3499 | 156.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.1756 | 100.8854
CID=-1628605946 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1729362495 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1543967888 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-42319029 | 0 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-707725582 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-808482131 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1745475737 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1644719188 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=623082275 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-963204642 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1628611195 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1729367744 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1543962639 | 3 | 15 | 8.4251 | 4 | 9 | 1.8 | 1.7385 | 148.4988 | 15.6766 | 212.2062 | 412.4664 | 403.9734 | 19516.2519 | 0.54277 | 0.0069691 | 12.3542 | 8.4251 | 104.0852 | 3 | 15 | 4 | 9 | 325.9849 | 488.3739 | 25.2141 | 1.4981 | 0.68333 | 59.0892 | 18.7327 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.4251 | 11.1654
CID=-42324278 | 3 | 17.5 | 8.626 | 4 | 11.5 | 2.3 | 1.7385 | 148.4988 | 15.6766 | 215.6398 | 414.1547 | 403.9734 | 19515.1741 | 0.44384 | 0.0071415 | 9.6905 | 8.626 | 83.59 | 3 | 17.5 | 4 | 11.5 | 325.9849 | 528.7968 | 29.5609 | 1.6222 | 0.68537 | 42.8476 | 19.1224 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0249 | 8.626 | 22.4048
CID=-707730831 | 3 | 20 | 10.0707 | 4 | 14 | 2.8 | 1.7385 | 148.4988 | 15.6766 | 219.0933 | 415.8156 | 403.9734 | 20525.7213 | 0.44632 | 0.0076286 | 8.1937 | 10.0707 | 82.5161 | 3 | 20 | 4 | 14 | 325.9849 | 571.7069 | 33.5574 | 1.7538 | 0.6995 | 26.4119 | 21.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.0707 | 27.9674
CID=-808487380 | 3 | 22.5 | 12.1238 | 4 | 16.5 | 3.3 | 1.7385 | 148.4988 | 15.6766 | 222.5675 | 417.4491 | 403.9734 | 21580.5198 | 0.48054 | 0.0083294 | 7.1902 | 12.1238 | 87.1729 | 3 | 22.5 | 4 | 16.5 | 325.9849 | 617.2019 | 37.2299 | 1.8933 | 0.71813 | 47.4851 | 25.6502 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.1238 | 34.0823
CID=1745483040 | 3 | 25 | 14.0916 | 4 | 19 | 3.8 | 1.7385 | 148.4988 | 15.6766 | 226.0633 | 419.0555 | 403.9734 | 22827.7463 | 0.51473 | 0.0090614 | 6.4986 | 14.0916 | 91.5754 | 3 | 25 | 4 | 19 | 325.9849 | 665.3809 | 40.3738 | 2.0411 | 0.73451 | 41.275 | 29.1487 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.0916 | 40.8543
CID=1644726491 | 3 | 27.5 | 16.1927 | 4 | 21.5 | 4.3 | 1.7385 | 148.4988 | 15.6766 | 229.5813 | 420.635 | 403.9734 | 23727.8808 | 0.54883 | 0.0098798 | 5.9108 | 16.1927 | 95.7115 | 3 | 27.5 | 4 | 21.5 | 325.9849 | 716.3449 | 43.477 | 2.1975 | 0.75053 | 58.4067 | 32.7797 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.1927 | 46.3828
CID=623089578 | 3 | 30 | 19.1571 | 4 | 24 | 4.8 | 1.7385 | 148.4988 | 15.6766 | 233.1226 | 422.1878 | 403.9734 | 24984.8289 | 0.59305 | 0.011018 | 5.2891 | 19.1571 | 101.3234 | 3 | 30 | 4 | 24 | 325.9849 | 770.1963 | 47.2028 | 2.3627 | 0.77081 | 51.2498 | 37.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.1571 | 54.3477
CID=-963197339 | 3 | 32.5 | 22.4325 | 4 | 26.5 | 5.3 | 1.7385 | 148.4988 | 15.6766 | 236.688 | 423.7141 | 403.9734 | 25796.6502 | 0.65115 | 0.01232 | 4.8558 | 22.4325 | 108.9273 | 3 | 32.5 | 4 | 26.5 | 325.9849 | 827.0396 | 50.3411 | 2.537 | 0.79041 | 64.1589 | 43.12 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.4325 | 63.1245
CID=-1628603892 | 3 | 35 | 25.6165 | 4 | 29 | 5.8 | 1.7385 | 148.4988 | 15.6766 | 240.2788 | 425.2142 | 403.9734 | 26754.0866 | 0.69035 | 0.01366 | 4.4114 | 25.6165 | 113.0059 | 3 | 35 | 4 | 29 | 325.9849 | 886.981 | 53.8687 | 2.7209 | 0.80699 | 80.1564 | 48.2287 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.6165 | 72.2476
CID=-1729360441 | 3 | 37.5 | 29.0856 | 4 | 31.5 | 6.3 | 1.7385 | 148.4988 | 15.6766 | 243.8959 | 426.6882 | 403.9734 | 27668.8573 | 0.73571 | 0.015167 | 4.0491 | 29.0856 | 117.7698 | 3 | 37.5 | 4 | 31.5 | 325.9849 | 950.1287 | 57.1871 | 2.9146 | 0.82265 | 82.8253 | 53.7176 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.0856 | 80.3364
CID=1543969942 | 3 | 40 | 32.953 | 4 | 34 | 6.8 | 1.7385 | 148.4988 | 15.6766 | 247.5407 | 428.1364 | 403.9734 | 28860.7166 | 0.78625 | 0.016893 | 3.7325 | 32.953 | 122.9954 | 3 | 40 | 4 | 34 | 325.9849 | 1016.593 | 60.4544 | 3.1185 | 0.83757 | 56.4675 | 59.7764 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.953 | 88.4142
CID=-42316975 | 3 | 42.5 | 37.6354 | 4 | 36.5 | 7.3 | 1.7385 | 148.4988 | 15.6766 | 251.2145 | 429.559 | 403.9734 | 29517.3658 | 0.85398 | 0.019006 | 3.4662 | 37.6354 | 130.4525 | 3 | 42.5 | 4 | 36.5 | 325.9849 | 1086.4865 | 63.5444 | 3.3329 | 0.8526 | 83.5733 | 67.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 37.6354 | 98.2926
CID=-707723528 | 3 | 45 | 41.9298 | 4 | 39 | 7.8 | 1.7385 | 148.4988 | 15.6766 | 254.9187 | 430.9562 | 403.9734 | 30834.8581 | 0.89311 | 0.021087 | 3.1749 | 41.9298 | 133.1223 | 3 | 45 | 4 | 39 | 325.9849 | 1159.9242 | 67.1918 | 3.5582 | 0.86397 | 54.2825 | 73.7365 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.9298 | 107.3472
CID=-808480077 | 3 | 47.5 | 47.1667 | 4 | 41.5 | 8.3 | 1.7385 | 148.4988 | 15.6766 | 258.655 | 432.3283 | 403.9734 | 31343.6018 | 0.96427 | 0.023644 | 2.9709 | 47.1667 | 140.1265 | 3 | 47.5 | 4 | 41.5 | 325.9849 | 1237.0237 | 70.0985 | 3.7947 | 0.87526 | 59.3723 | 81.8752 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.1667 | 112.8128
CID=1745486239 | 3 | 50 | 53.1496 | 4 | 44 | 8.8 | 1.7385 | 148.4988 | 15.6766 | 262.425 | 433.6755 | 403.9734 | 32143.1935 | 1.033 | 0.02664 | 2.7512 | 53.1496 | 146.2229 | 3 | 50 | 4 | 44 | 325.9849 | 1317.9055 | 73.4627 | 4.0428 | 0.88541 | 61.8259 | 91.2033 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.1496 | 113.4849
CID=1644729690 | 3 | 52.5 | 58.3888 | 4 | 46.5 | 9.3 | 1.7385 | 148.4988 | 15.6766 | 266.2308 | 434.9982 | 403.9734 | 32841.329 | 1.1 | 0.029507 | 2.5949 | 58.3888 | 151.5107 | 3 | 52.5 | 4 | 46.5 | 325.9849 | 1402.6932 | 76.0829 | 4.3029 | 0.89239 | 64.6029 | 99.4103 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58.3888 | 112.6148
CID=623092777 | 3 | 55 | 65.8924 | 4 | 49 | 9.8 | 1.7385 | 148.4988 | 15.6766 | 270.0745 | 436.2964 | 403.9734 | 33297.1334 | 1.1638 | 0.033497 | 2.365 | 65.8924 | 155.8362 | 3 | 55 | 4 | 49 | 325.9849 | 1491.5141 | 80.2133 | 4.5754 | 0.9 | 85.2523 | 111.2365 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65.8924 | 112.3073
CID=-963194140 | 3 | 57.5 | 73.9935 | 4 | 51.5 | 10.3 | 1.7385 | 148.4988 | 15.6766 | 273.9586 | 437.5705 | 403.9734 | 33898.5854 | 1.2602 | 0.037994 | 2.2143 | 73.9935 | 163.847 | 3 | 57.5 | 4 | 51.5 | 325.9849 | 1584.4992 | 83.2058 | 4.8607 | 0.90589 | 97.8722 | 124.1013 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.9935 | 113.0467
CID=-1628600693 | 3 | 60 | 82.0539 | 4 | 54 | 10.8 | 1.7385 | 148.4988 | 15.6766 | 277.8855 | 438.8208 | 403.9734 | 34690.2396 | 1.3544 | 0.042766 | 2.0813 | 82.0539 | 170.7784 | 3 | 60 | 4 | 54 | 325.9849 | 1681.7842 | 86.0114 | 5.1591 | 0.91002 | 86.6769 | 136.9949 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82.0539 | 113.39
CID=-1729357242 | 3 | 62.5 | 92.802 | 4 | 56.5 | 11.3 | 1.7385 | 148.4988 | 15.6766 | 281.8586 | 440.0476 | 403.9734 | 35133.4109 | 1.766 | 0.049768 | 2.2881 | 94.2516 | 215.6588 | 3 | 62.5 | 4 | 56.5 | 325.9849 | 1783.5096 | 82.1139 | 5.4711 | 0.91409 | 108.0412 | 156.6586 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.802 | 113.8644
CID=1543973141 | 3 | 65 | 105.0584 | 4 | 59 | 11.8 | 1.7385 | 148.4988 | 15.6766 | 285.881 | 441.2512 | 403.9734 | 35857.0289 | 1.9378 | 0.056604 | 2.1782 | 105.0584 | 228.8397 | 3 | 65 | 4 | 59 | 325.9849 | 1889.8218 | 84.298 | 5.7973 | 0.91629 | 108.623 | 174.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 105.0584 | 111.9723
CID=-42313776 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-707720329 | 3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-808476878 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1745485086 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1644728537 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=623091624 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-963195293 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1628601846 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1729358395 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1543971988 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-42314929 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-707721482 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-808478031 | 6 | 20 | 9.5417 | 4 | 14 | 2.8 | 1.7371 | 148.3861 | 17.3476 | 219.0933 | 415.3827 | 405.7474 | 19519.2357 | 0.53315 | 0.0074241 | 10.4294 | 9.5417 | 99.5143 | 6 | 20 | 4 | 14 | 361.9781 | 571.7069 | 31.2732 | 1.5794 | 0.69443 | 49.172 | 20.8765 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.5417 | 22.8585
CID=1745479837 | 6 | 22.5 | 10.1644 | 4 | 16.5 | 3.3 | 1.7371 | 148.3861 | 17.3476 | 222.5675 | 417.0123 | 405.7474 | 19881.9179 | 0.47804 | 0.0077236 | 8.6151 | 10.1644 | 87.5671 | 6 | 22.5 | 4 | 16.5 | 361.9781 | 617.2019 | 35.2682 | 1.7051 | 0.70038 | 39.5045 | 22.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.1644 | 28.6739
CID=1644723288 | 6 | 25 | 12.3537 | 4 | 19 | 3.8 | 1.7371 | 148.3861 | 17.3476 | 226.0633 | 418.6147 | 405.7474 | 21375.4989 | 0.50196 | 0.0084739 | 7.3009 | 12.3537 | 90.1937 | 6 | 25 | 4 | 19 | 361.9781 | 665.3809 | 39.5338 | 1.8382 | 0.72012 | 23.1821 | 26.0646 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.3537 | 34.9853
CID=623086375 | 6 | 27.5 | 14.739 | 4 | 21.5 | 4.3 | 1.7371 | 148.3861 | 17.3476 | 229.5813 | 420.1903 | 405.7474 | 22237.4062 | 0.56201 | 0.0093435 | 6.7174 | 14.739 | 99.0072 | 6 | 27.5 | 4 | 21.5 | 361.9781 | 716.3449 | 42.2704 | 1.979 | 0.7396 | 54.3168 | 30.2779 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.739 | 42.0253
CID=-963200542 | 6 | 30 | 17.1012 | 4 | 24 | 4.8 | 1.7371 | 148.3861 | 17.3476 | 233.1226 | 421.7392 | 405.7474 | 23543.5655 | 0.60753 | 0.010262 | 6.1326 | 17.1012 | 104.8755 | 6 | 30 | 4 | 24 | 361.9781 | 770.1963 | 45.2184 | 2.1277 | 0.75703 | 39.729 | 34.322 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.1012 | 49.1455
CID=-1628607095 | 6 | 32.5 | 19.7427 | 4 | 26.5 | 5.3 | 1.7371 | 148.3861 | 17.3476 | 236.688 | 423.2616 | 405.7474 | 24357.9842 | 0.64509 | 0.011322 | 5.524 | 19.7427 | 109.0579 | 6 | 32.5 | 4 | 26.5 | 361.9781 | 827.0396 | 48.6129 | 2.2848 | 0.77452 | 59.764 | 38.7283 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.7427 | 55.9665
CID=-1729363644 | 6 | 35 | 22.991 | 4 | 29 | 5.8 | 1.7371 | 148.3861 | 17.3476 | 240.2788 | 424.7577 | 405.7474 | 25552.2994 | 0.68891 | 0.01264 | 4.9581 | 22.991 | 113.9927 | 6 | 35 | 4 | 29 | 361.9781 | 886.981 | 52.2783 | 2.4504 | 0.79349 | 47.5993 | 44.0223 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.991 | 65.1
CID=1543966739 | 6 | 37.5 | 26.3835 | 4 | 31.5 | 6.3 | 1.7371 | 148.3861 | 17.3476 | 243.8959 | 426.2278 | 405.7474 | 26256.6313 | 0.73915 | 0.014077 | 4.5344 | 26.3836 | 119.6324 | 6 | 37.5 | 4 | 31.5 | 361.9781 | 950.1287 | 55.5383 | 2.6248 | 0.81066 | 66.5079 | 49.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.3835 | 74.5803
CID=-42320178 | 6 | 40 | 30.2032 | 4 | 34 | 6.8 | 1.7371 | 148.3861 | 17.3476 | 247.5407 | 427.6721 | 405.7474 | 27207.9521 | 0.79512 | 0.015738 | 4.1649 | 30.2032 | 125.7934 | 6 | 40 | 4 | 34 | 361.9781 | 1016.593 | 58.7654 | 2.8084 | 0.82722 | 92.8491 | 55.4736 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.2032 | 84.9212
CID=-707726731 | 6 | 42.5 | 33.7881 | 4 | 36.5 | 7.3 | 1.7371 | 148.3861 | 17.3476 | 251.2145 | 429.0909 | 405.7474 | 28173.8556 | 0.83241 | 0.017401 | 3.8071 | 33.7881 | 128.6348 | 6 | 42.5 | 4 | 36.5 | 361.9781 | 1086.4865 | 62.2216 | 3.0015 | 0.84048 | 66.6223 | 61.0793 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.7881 | 91.8398
CID=-808483280 | 6 | 45 | 38.4962 | 4 | 39 | 7.8 | 1.7371 | 148.3861 | 17.3476 | 254.9187 | 430.4842 | 405.7474 | 29228.6 | 0.90713 | 0.019568 | 3.5541 | 38.4962 | 136.8208 | 6 | 45 | 4 | 39 | 361.9781 | 1159.9242 | 65.071 | 3.2044 | 0.85505 | 56.6715 | 68.4041 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.4962 | 102.1436
CID=1745470740 | 6 | 47.5 | 43.1636 | 4 | 41.5 | 8.3 | 1.7371 | 148.3861 | 17.3476 | 258.655 | 431.8524 | 405.7474 | 30113.542 | 0.95428 | 0.021837 | 3.252 | 43.1636 | 140.3671 | 6 | 47.5 | 4 | 41.5 | 361.9781 | 1237.0237 | 68.6719 | 3.4174 | 0.86686 | 70.3101 | 75.6526 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.1636 | 112.1825
CID=1644714191 | 6 | 50 | 48.3056 | 4 | 44 | 8.8 | 1.7371 | 148.3861 | 17.3476 | 262.425 | 433.1958 | 405.7474 | 30995.5909 | 1.0181 | 0.024418 | 3.0207 | 48.3056 | 145.9186 | 6 | 50 | 4 | 44 | 361.9781 | 1317.9055 | 71.7964 | 3.6408 | 0.8774 | 57.229 | 83.6479 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.3056 | 122.2097
CID=623077278 | 6 | 52.5 | 54.1646 | 4 | 46.5 | 9.3 | 1.7371 | 148.3861 | 17.3476 | 266.2308 | 434.5145 | 405.7474 | 31581.0238 | 1.0923 | 0.027435 | 2.8136 | 54.1646 | 152.3969 | 6 | 52.5 | 4 | 46.5 | 361.9781 | 1402.6932 | 74.8619 | 3.8751 | 0.88689 | 60.6639 | 92.7902 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.1646 | 124.2598
CID=-963209639 | 6 | 55 | 60.3101 | 4 | 49 | 9.8 | 1.7371 | 148.3861 | 17.3476 | 270.0745 | 435.8088 | 405.7474 | 32330.8469 | 1.1662 | 0.030751 | 2.6235 | 60.3101 | 158.2257 | 6 | 55 | 4 | 49 | 361.9781 | 1491.5141 | 77.91 | 4.1205 | 0.89458 | 64.2036 | 102.4301 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.3101 | 124.6468
CID=-1628616192 | 6 | 57.5 | 66.4309 | 4 | 51.5 | 10.3 | 1.7371 | 148.3861 | 17.3476 | 273.9586 | 437.0791 | 405.7474 | 32989.4139 | 1.2399 | 0.034262 | 2.4599 | 66.431 | 163.4107 | 6 | 57.5 | 4 | 51.5 | 361.9781 | 1584.4992 | 80.7462 | 4.3773 | 0.90046 | 67.6739 | 112.0886 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 66.4309 | 124.7604
CID=-1729372741 | 6 | 60 | 75.0155 | 4 | 54 | 10.8 | 1.7371 | 148.3861 | 17.3476 | 277.8855 | 438.3255 | 405.7474 | 33346.6351 | 1.3115 | 0.039082 | 2.2355 | 75.0155 | 167.6958 | 6 | 60 | 4 | 54 | 361.9781 | 1681.7842 | 84.9337 | 4.6461 | 0.90649 | 85.265 | 125.7312 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 75.0155 | 124.137
CID=1543957642 | 6 | 62.5 | 83.3904 | 4 | 56.5 | 11.3 | 1.7371 | 148.3861 | 17.3476 | 281.8586 | 439.5483 | 405.7474 | 34040.0989 | 1.4137 | 0.044131 | 2.1003 | 83.3905 | 175.1432 | 6 | 62.5 | 4 | 56.5 | 361.9781 | 1783.5096 | 87.7116 | 4.9271 | 0.91058 | 97.872 | 139.1411 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.3904 | 125.2286
CID=-42329275 | 6 | 65 | 92.0266 | 4 | 59 | 11.8 | 1.7371 | 148.3861 | 17.3476 | 285.881 | 440.748 | 405.7474 | 34774.2829 | 1.5134 | 0.049659 | 1.9712 | 92.0266 | 181.4023 | 6 | 65 | 4 | 59 | 361.9781 | 1889.8218 | 90.5133 | 5.2208 | 0.9135 | 86.6769 | 153.0596 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.0266 | 125.5368
CID=-707735828 | 6 | 67.5 | 104.302 | 4 | 61.5 | 12.3 | 1.7371 | 148.3861 | 17.3476 | 289.9569 | 441.9247 | 405.7474 | 35191.5415 | 1.9501 | 0.057732 | 2.1492 | 105.0627 | 225.8036 | 6 | 67.5 | 4 | 61.5 | 361.9781 | 2000.8736 | 87.068 | 5.5276 | 0.91629 | 107.9457 | 174.2095 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 104.302 | 124.8224
CID=-808492377 | 6 | 69.99 | 116.6406 | 4 | 63.99 | 12.798 | 1.7371 | 148.3861 | 17.3476 | 294.074 | 443.0743 | 405.7474 | 35978.5316 | 1.7308 | 0.065687 | 1.6571 | 116.6407 | 193.2825 | 6 | 69.99 | 4 | 63.99 | 361.9781 | 2116.3519 | 98.2331 | 5.8466 | 0.91774 | 95.3502 | 193.1007 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 116.6406 | 123.8195
CID=1745473939 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1644717390 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=623080477 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-963206440 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1628612993 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1729369542 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1543960841 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-42326076 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-707732629 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-808489178 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1467759177 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523246204 | 9 | 22.5 | 9.8546 | 4 | 16.5 | 3.3 | 1.7357 | 148.2186 | 19.1581 | 222.5675 | 416.6065 | 407.5003 | 19346.0203 | 0.60044 | 0.0075715 | 11.268 | 9.8546 | 111.0415 | 9 | 22.5 | 4 | 16.5 | 400.9358 | 617.2019 | 32.8735 | 1.5394 | 0.69744 | 52.19 | 21.4678 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2872 | 9.8546 | 22.6697
CID=1704814657 | 9 | 25 | 10.2198 | 4 | 19 | 3.8 | 1.7357 | 148.2186 | 19.1581 | 226.0633 | 418.2053 | 407.5003 | 19522.7118 | 0.50331 | 0.0078123 | 8.9356 | 10.2198 | 91.3199 | 9 | 25 | 4 | 19 | 400.9358 | 665.3809 | 37.2717 | 1.6596 | 0.70091 | 37.5154 | 22.1532 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.2198 | 29.301
CID=400852742 | 9 | 27.5 | 12.4687 | 4 | 21.5 | 4.3 | 1.7357 | 148.2186 | 19.1581 | 229.5813 | 419.7772 | 407.5003 | 20890.1885 | 0.54513 | 0.0085908 | 7.7786 | 12.4688 | 96.989 | 9 | 27.5 | 4 | 21.5 | 400.9358 | 716.3449 | 40.8706 | 1.7867 | 0.7211 | 28.6239 | 26.2713 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.4687 | 35.877
CID=-546878813 | 9 | 30 | 14.9305 | 4 | 24 | 4.8 | 1.7357 | 148.2186 | 19.1581 | 233.1226 | 421.3224 | 407.5003 | 21709.2632 | 0.58682 | 0.0094971 | 6.8536 | 14.9305 | 102.3279 | 9 | 30 | 4 | 24 | 400.9358 | 770.1963 | 44.4303 | 1.921 | 0.74108 | 54.4713 | 30.61 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 14.9305 | 43.1989
CID=-1850840728 | 9 | 32.5 | 17.2579 | 4 | 26.5 | 5.3 | 1.7357 | 148.2186 | 19.1581 | 236.688 | 422.8412 | 407.5003 | 23074.4087 | 0.62849 | 0.01042 | 6.2205 | 17.258 | 107.3535 | 9 | 32.5 | 4 | 26.5 | 400.9358 | 827.0396 | 47.4613 | 2.0628 | 0.75812 | 34.5729 | 34.5865 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.2579 | 51.2247
CID=-1669272275 | 9 | 35 | 20.0505 | 4 | 29 | 5.8 | 1.7357 | 148.2186 | 19.1581 | 240.2788 | 424.3337 | 407.5003 | 23807.4871 | 0.68325 | 0.011547 | 5.6983 | 20.0505 | 114.2537 | 9 | 35 | 4 | 29 | 400.9358 | 886.981 | 50.3919 | 2.2123 | 0.77644 | 61.261 | 39.2352 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.0505 | 57.5838
CID=1321733106 | 9 | 37.5 | 23.6818 | 4 | 31.5 | 6.3 | 1.7357 | 148.2186 | 19.1581 | 243.8959 | 425.8002 | 407.5003 | 25082.743 | 0.73875 | 0.013016 | 5.1036 | 23.6818 | 120.8635 | 9 | 37.5 | 4 | 31.5 | 400.9358 | 950.1287 | 54.032 | 2.3698 | 0.79719 | 51.2497 | 45.1345 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.6818 | 66.9124
CID=374001551 | 9 | 40 | 27.2008 | 4 | 34 | 6.8 | 1.7357 | 148.2186 | 19.1581 | 247.5407 | 427.2409 | 407.5003 | 25779.1061 | 0.79476 | 0.014526 | 4.6737 | 27.2008 | 127.1293 | 9 | 40 | 4 | 34 | 400.9358 | 1016.593 | 57.1784 | 2.5356 | 0.81444 | 64.6439 | 50.7435 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.2008 | 77.061
CID=-929960364 | 9 | 42.5 | 30.9216 | 4 | 36.5 | 7.3 | 1.7357 | 148.2186 | 19.1581 | 251.2145 | 428.656 | 407.5003 | 26700.1076 | 0.84205 | 0.016186 | 4.256 | 30.9217 | 131.6011 | 9 | 42.5 | 4 | 36.5 | 400.9358 | 1086.4865 | 60.5817 | 2.7099 | 0.83004 | 80.1564 | 56.6001 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30.9216 | 87.5743
CID=-1467755978 | 9 | 45 | 34.7915 | 4 | 39 | 7.8 | 1.7357 | 148.2186 | 19.1581 | 254.9187 | 430.0457 | 407.5003 | 27560.2907 | 0.88979 | 0.01799 | 3.9022 | 34.7915 | 135.7652 | 9 | 45 | 4 | 39 | 400.9358 | 1159.9242 | 63.8733 | 2.893 | 0.84383 | 82.8254 | 62.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.7915 | 97.396
CID=1523249403 | 9 | 47.5 | 39.4856 | 4 | 41.5 | 8.3 | 1.7357 | 148.2186 | 19.1581 | 258.655 | 431.4103 | 407.5003 | 28667.9946 | 0.95946 | 0.020199 | 3.6168 | 39.4856 | 142.8112 | 9 | 47.5 | 4 | 41.5 | 400.9358 | 1237.0237 | 66.9071 | 3.0853 | 0.85776 | 59.5233 | 69.9409 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 39.4856 | 105.939
CID=1704817856 | 9 | 50 | 44.3087 | 4 | 44 | 8.8 | 1.7357 | 148.2186 | 19.1581 | 262.425 | 432.7501 | 407.5003 | 29399.3774 | 1.0196 | 0.022581 | 3.3383 | 44.3087 | 147.9156 | 9 | 50 | 4 | 44 | 400.9358 | 1317.9055 | 70.131 | 3.2871 | 0.86941 | 62.5657 | 77.4315 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44.3087 | 117.1977
CID=400855941 | 9 | 52.5 | 49.6486 | 4 | 46.5 | 9.3 | 1.7357 | 148.2186 | 19.1581 | 266.2308 | 434.0651 | 407.5003 | 30576.6993 | 1.0821 | 0.025304 | 3.0791 | 49.6486 | 152.8729 | 9 | 52.5 | 4 | 46.5 | 400.9358 | 1402.6932 | 73.4435 | 3.4985 | 0.87979 | 56.8313 | 85.7398 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.6486 | 126.9601
CID=-546875614 | 9 | 55 | 54.9361 | 4 | 49 | 9.8 | 1.7357 | 148.2186 | 19.1581 | 270.0745 | 435.3559 | 407.5003 | 31106.9679 | 1.1388 | 0.028167 | 2.8488 | 54.9361 | 156.5036 | 9 | 55 | 4 | 49 | 400.9358 | 1491.5141 | 76.6914 | 3.7201 | 0.88797 | 56.9188 | 93.9973 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.9361 | 126.9601
CID=-1850837529 | 9 | 57.5 | 61.5619 | 4 | 51.5 | 10.3 | 1.7357 | 148.2186 | 19.1581 | 273.9586 | 436.6225 | 407.5003 | 31821.3319 | 1.2154 | 0.031767 | 2.6365 | 61.562 | 162.3085 | 9 | 57.5 | 4 | 51.5 | 400.9358 | 1584.4992 | 79.9843 | 3.952 | 0.89591 | 59.0953 | 104.4007 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.5619 | 126.9602
CID=-1669269076 | 9 | 60 | 67.5145 | 4 | 54 | 10.8 | 1.7357 | 148.2186 | 19.1581 | 277.8855 | 437.8652 | 407.5003 | 32503.7181 | 1.2898 | 0.035306 | 2.4761 | 67.5145 | 167.1715 | 9 | 60 | 4 | 54 | 400.9358 | 1681.7842 | 82.7149 | 4.1946 | 0.90135 | 62.6993 | 113.8045 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.5145 | 126.9601
CID=1321736305 | 9 | 62.5 | 74.8839 | 4 | 56.5 | 11.3 | 1.7357 | 148.2186 | 19.1581 | 281.8586 | 439.0844 | 407.5003 | 33075.4971 | 1.3659 | 0.039714 | 2.2917 | 74.8839 | 171.6122 | 9 | 62.5 | 4 | 56.5 | 400.9358 | 1783.5096 | 86.0436 | 4.4484 | 0.90642 | 72.3009 | 125.5212 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 74.8839 | 126.9602
CID=374004750 | 9 | 65 | 84.545 | 4 | 59 | 11.8 | 1.7357 | 148.2186 | 19.1581 | 285.881 | 440.2804 | 407.5003 | 33448.1095 | 1.4711 | 0.045488 | 2.1162 | 84.545 | 178.9154 | 9 | 65 | 4 | 59 | 400.9358 | 1889.8218 | 89.497 | 4.7135 | 0.91103 | 97.4739 | 140.9969 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84.545 | 126.9602
CID=-929957165 | 9 | 67.5 | 93.4753 | 4 | 61.5 | 12.3 | 1.7357 | 148.2186 | 19.1581 | 289.9569 | 441.4534 | 407.5003 | 34151.8114 | 1.579 | 0.051332 | 1.9855 | 93.4754 | 185.5992 | 9 | 67.5 | 4 | 61.5 | 400.9358 | 2000.8736 | 92.2618 | 4.9905 | 0.91389 | 93.2703 | 155.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 93.4753 | 126.9601
CID=-1467757131 | 9 | 69.99 | 102.6563 | 4 | 63.99 | 12.798 | 1.7357 | 148.2186 | 19.1581 | 294.074 | 442.5993 | 407.5003 | 34830.226 | 1.6837 | 0.057743 | 1.8603 | 102.6563 | 190.9714 | 9 | 69.99 | 4 | 63.99 | 400.9358 | 2116.3519 | 95.0537 | 5.2785 | 0.91588 | 86.6769 | 170.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 102.6563 | 126.9602
CID=1523248250 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1704816703 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=400854788 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-546876767 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1850838682 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1669270229 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1321735152 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=374003597 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-929958318 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1467762380 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523243001 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1704811454 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=400849539 | 12 | 25 | 10.795 | 4 | 19 | 3.8 | 1.7345 | 147.9949 | 21.1172 | 226.0633 | 417.8241 | 409.2305 | 19394.2924 | 0.71321 | 0.0078895 | 12.1016 | 10.795 | 130.6368 | 12 | 25 | 4 | 19 | 443.0145 | 665.3809 | 34.7376 | 1.5019 | 0.70626 | 58.915 | 23.2227 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.795 | 16.7083
CID=-546882016 | 12 | 27.5 | 11.1128 | 4 | 21.5 | 4.3 | 1.7345 | 147.9949 | 21.1172 | 229.5813 | 419.3925 | 409.2305 | 19423.9295 | 0.592 | 0.0081304 | 9.5702 | 11.1128 | 106.3515 | 12 | 27.5 | 4 | 21.5 | 443.0145 | 716.3449 | 38.9391 | 1.617 | 0.70916 | 42.7764 | 23.8086 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0576 | 11.1128 | 29.8031
CID=-1850843931 | 12 | 30 | 13.0293 | 4 | 24 | 4.8 | 1.7345 | 147.9949 | 21.1172 | 233.1226 | 420.9344 | 409.2305 | 20391.1079 | 0.60058 | 0.0088418 | 8.1176 | 13.0293 | 105.7669 | 12 | 30 | 4 | 24 | 443.0145 | 770.1963 | 42.7533 | 1.7385 | 0.72584 | 28.2564 | 27.2732 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.0293 | 36.7366
CID=-1669275478 | 12 | 32.5 | 15.6766 | 4 | 26.5 | 5.3 | 1.7345 | 147.9949 | 21.1172 | 236.688 | 422.4497 | 409.2305 | 21472.1387 | 0.64647 | 0.0098267 | 7.1153 | 15.6766 | 111.5441 | 12 | 32.5 | 4 | 26.5 | 443.0145 | 827.0396 | 46.3018 | 1.8668 | 0.74673 | 41.458 | 31.8965 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.6766 | 44.2749
CID=1321729903 | 12 | 35 | 18.1723 | 4 | 29 | 5.8 | 1.7345 | 147.9949 | 21.1172 | 240.2788 | 423.9389 | 409.2305 | 22500.5275 | 0.69235 | 0.010826 | 6.4369 | 18.1723 | 116.9741 | 12 | 35 | 4 | 29 | 443.0145 | 886.981 | 49.3284 | 2.0021 | 0.76436 | 47.061 | 36.1216 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.1723 | 52.5653
CID=373998348 | 12 | 37.5 | 20.8063 | 4 | 31.5 | 6.3 | 1.7345 | 147.9949 | 21.1172 | 243.8959 | 425.402 | 409.2305 | 23550.6178 | 0.73813 | 0.011928 | 5.8655 | 20.8063 | 122.0384 | 12 | 37.5 | 4 | 31.5 | 443.0145 | 950.1287 | 52.2959 | 2.1447 | 0.78103 | 47.3406 | 40.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.8063 | 59.3536
CID=-929963567 | 12 | 40 | 24.0173 | 4 | 34 | 6.8 | 1.7345 | 147.9949 | 21.1172 | 247.5407 | 426.8393 | 409.2305 | 24461.3824 | 0.78365 | 0.013284 | 5.2757 | 24.0173 | 126.7085 | 12 | 40 | 4 | 34 | 443.0145 | 1016.593 | 55.7066 | 2.2947 | 0.79895 | 56.8081 | 45.6731 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.0173 | 68.7122
CID=-1467755077 | 12 | 42.5 | 28.0083 | 4 | 36.5 | 7.3 | 1.7345 | 147.9949 | 21.1172 | 251.2145 | 428.251 | 409.2305 | 25510.5023 | 0.84855 | 0.014987 | 4.7873 | 28.0083 | 134.0851 | 12 | 42.5 | 4 | 36.5 | 443.0145 | 1086.4865 | 59.0414 | 2.4525 | 0.81804 | 47.5994 | 52.0198 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.0083 | 79.3022
CID=1523250304 | 12 | 45 | 31.8335 | 4 | 39 | 7.8 | 1.7345 | 147.9949 | 21.1172 | 254.9187 | 429.6374 | 409.2305 | 26211.0939 | 0.90143 | 0.016722 | 4.3696 | 31.8335 | 139.1007 | 12 | 45 | 4 | 39 | 443.0145 | 1159.9242 | 62.3036 | 2.6183 | 0.8335 | 66.5079 | 58.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.8335 | 90.1739
CID=1704818757 | 12 | 47.5 | 36.2059 | 4 | 41.5 | 8.3 | 1.7345 | 147.9949 | 21.1172 | 258.655 | 430.9986 | 409.2305 | 27110.08 | 0.9657 | 0.018753 | 4.0162 | 36.2059 | 145.4105 | 12 | 47.5 | 4 | 41.5 | 443.0145 | 1237.0237 | 65.4601 | 2.7923 | 0.84833 | 92.4269 | 64.8443 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.2059 | 102.0198
CID=400856842 | 12 | 50 | 40.3372 | 4 | 44 | 8.8 | 1.7345 | 147.9949 | 21.1172 | 262.425 | 432.335 | 409.2305 | 28000.3215 | 1.0105 | 0.020804 | 3.6778 | 40.3372 | 148.3506 | 12 | 50 | 4 | 44 | 443.0145 | 1317.9055 | 68.7949 | 2.9749 | 0.85999 | 68.7465 | 71.2634 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.3372 | 109.7483
CID=-546874713 | 12 | 52.5 | 45.5194 | 4 | 46.5 | 9.3 | 1.7345 | 147.9949 | 21.1172 | 266.2308 | 433.6467 | 409.2305 | 29046.9374 | 1.0894 | 0.023383 | 3.4225 | 45.5194 | 155.7888 | 12 | 52.5 | 4 | 46.5 | 443.0145 | 1402.6932 | 71.6979 | 3.1662 | 0.87198 | 54.6982 | 79.3132 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.5194 | 121.423
CID=-1850836628 | 12 | 55 | 50.8145 | 4 | 49 | 9.8 | 1.7345 | 147.9949 | 21.1172 | 270.0745 | 434.934 | 409.2305 | 29739.9064 | 1.1458 | 0.026158 | 3.1378 | 50.8145 | 159.4458 | 12 | 55 | 4 | 49 | 443.0145 | 1491.5141 | 75.1397 | 3.3667 | 0.88176 | 74.6466 | 87.5576 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50.8145 | 126.9602
CID=-1669268175 | 12 | 57.5 | 56.5802 | 4 | 51.5 | 10.3 | 1.7345 | 147.9949 | 21.1172 | 273.9586 | 436.1972 | 409.2305 | 30798.7105 | 1.2158 | 0.029297 | 2.9068 | 56.5802 | 164.468 | 12 | 57.5 | 4 | 51.5 | 443.0145 | 1584.4992 | 78.283 | 3.5766 | 0.89016 | 54.2826 | 96.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.5802 | 126.9601
CID=1321737206 | 12 | 60 | 62.8856 | 4 | 54 | 10.8 | 1.7345 | 147.9949 | 21.1172 | 277.8855 | 437.4365 | 409.2305 | 31259.8333 | 1.298 | 0.032864 | 2.7111 | 62.8856 | 170.4879 | 12 | 60 | 4 | 54 | 443.0145 | 1681.7842 | 81.2159 | 3.7962 | 0.89724 | 59.3723 | 106.4871 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 62.8856 | 126.9602
CID=374005651 | 12 | 62.5 | 70.1201 | 4 | 56.5 | 11.3 | 1.7345 | 147.9949 | 21.1172 | 281.8586 | 438.6523 | 409.2305 | 31994.0157 | 1.377 | 0.037075 | 2.5014 | 70.1202 | 175.3957 | 12 | 62.5 | 4 | 56.5 | 443.0145 | 1783.5096 | 84.5725 | 4.0258 | 0.90333 | 61.8259 | 117.9379 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70.1201 | 126.9601
CID=-929956264 | 12 | 65 | 76.1762 | 4 | 59 | 11.8 | 1.7345 | 147.9949 | 21.1172 | 285.881 | 439.8448 | 409.2305 | 32627.2416 | 1.4538 | 0.04104 | 2.3541 | 76.1762 | 179.3269 | 12 | 65 | 4 | 59 | 443.0145 | 1889.8218 | 87.1765 | 4.2658 | 0.90715 | 62.6996 | 127.584 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.1762 | 126.9602
CID=-1467751878 | 12 | 67.5 | 84.6298 | 4 | 61.5 | 12.3 | 1.7345 | 147.9949 | 21.1172 | 289.9569 | 441.0144 | 409.2305 | 33105.2152 | 1.5267 | 0.046422 | 2.1517 | 84.6298 | 182.0971 | 12 | 67.5 | 4 | 61.5 | 443.0145 | 2000.8736 | 90.9282 | 4.5165 | 0.91107 | 73.0306 | 141.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84.6298 | 126.9602
CID=1523253503 | 12 | 69.99 | 94.7107 | 4 | 63.99 | 12.798 | 1.7345 | 147.9949 | 21.1172 | 294.074 | 442.1569 | 409.2305 | 33527.2348 | 1.6424 | 0.052999 | 1.997 | 94.7108 | 189.1335 | 12 | 69.99 | 4 | 63.99 | 443.0145 | 2116.3519 | 94.0874 | 4.7772 | 0.91421 | 98.6211 | 157.4019 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.7107 | 126.9601
CID=1704821956 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=400860041 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-546871514 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1850833429 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1669264976 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1321740405 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=374008850 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-929953065 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1467753031 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523252350 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1704820803 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=400858888 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-546872667 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1850834582 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1669266129 | 15 | 30 | 12.3198 | 4 | 24 | 4.8 | 1.7333 | 147.7132 | 23.2347 | 233.1226 | 420.5719 | 410.9364 | 19413.2367 | 0.70805 | 0.0085534 | 10.2194 | 12.3198 | 125.9012 | 15 | 30 | 4 | 24 | 488.3739 | 770.1963 | 40.746 | 1.5771 | 0.71982 | 49.3573 | 26.0035 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0266 | 12.3198 | 30.1197
CID=1321739252 | 15 | 32.5 | 13.0742 | 4 | 26.5 | 5.3 | 1.7333 | 147.7132 | 23.2347 | 236.688 | 422.0841 | 410.9364 | 19774.2581 | 0.63691 | 0.0089494 | 8.4885 | 13.0742 | 110.9801 | 15 | 32.5 | 4 | 26.5 | 488.3739 | 827.0396 | 44.588 | 1.6935 | 0.72621 | 39.5045 | 27.3531 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.0742 | 37.5319
CID=374007697 | 15 | 35 | 15.7101 | 4 | 29 | 5.8 | 1.7333 | 147.7132 | 23.2347 | 240.2788 | 423.5701 | 410.9364 | 21220.5183 | 0.65931 | 0.0099457 | 7.162 | 15.7101 | 112.5159 | 15 | 35 | 4 | 29 | 488.3739 | 886.981 | 48.7551 | 1.8162 | 0.74698 | 23.4635 | 31.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.7101 | 45.2884
CID=-929954218 | 15 | 37.5 | 18.4587 | 4 | 31.5 | 6.3 | 1.7333 | 147.7132 | 23.2347 | 243.8959 | 425.03 | 410.9364 | 21916.1257 | 0.72494 | 0.011043 | 6.5603 | 18.4587 | 121.0949 | 15 | 37.5 | 4 | 31.5 | 488.3739 | 950.1287 | 51.5094 | 1.9455 | 0.76627 | 54.3169 | 36.5996 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 18.4587 | 53.9129
CID=-1467758280 | 15 | 40 | 21.4735 | 4 | 34 | 6.8 | 1.7333 | 147.7132 | 23.2347 | 247.5407 | 426.4641 | 410.9364 | 23245.9851 | 0.78992 | 0.012292 | 6.0106 | 21.4735 | 129.0696 | 15 | 40 | 4 | 34 | 488.3739 | 1016.593 | 54.3297 | 2.0816 | 0.78496 | 33.7811 | 41.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.4735 | 63.3068
CID=1523247101 | 15 | 42.5 | 24.7682 | 4 | 36.5 | 7.3 | 1.7333 | 147.7132 | 23.2347 | 251.2145 | 427.8727 | 410.9364 | 23884.6605 | 0.85171 | 0.013707 | 5.4924 | 24.7682 | 136.0375 | 15 | 42.5 | 4 | 36.5 | 488.3739 | 1086.4865 | 57.2889 | 2.2247 | 0.8028 | 61.2612 | 46.8754 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.7682 | 70.5569
CID=1704815554 | 15 | 45 | 28.93 | 4 | 39 | 7.8 | 1.7333 | 147.7132 | 23.2347 | 254.9187 | 429.2559 | 410.9364 | 25133.4228 | 0.91013 | 0.015506 | 4.9083 | 28.93 | 141.9969 | 15 | 45 | 4 | 39 | 488.3739 | 1159.9242 | 60.9194 | 2.3751 | 0.822 | 51.2494 | 53.4727 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.93 | 81.3534
CID=400853639 | 15 | 47.5 | 32.6346 | 4 | 41.5 | 8.3 | 1.7333 | 147.7132 | 23.2347 | 258.655 | 430.614 | 410.9364 | 25730.1418 | 0.9609 | 0.017237 | 4.4838 | 32.6346 | 146.3278 | 15 | 47.5 | 4 | 41.5 | 488.3739 | 1237.0237 | 64.085 | 2.5329 | 0.83643 | 65.0018 | 59.2794 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.6346 | 92.9494
CID=-546877916 | 15 | 50 | 36.943 | 4 | 44 | 8.8 | 1.7333 | 147.7132 | 23.2347 | 262.425 | 431.9472 | 410.9364 | 26608.4709 | 1.0179 | 0.01929 | 4.0921 | 36.943 | 151.1728 | 15 | 50 | 4 | 44 | 488.3739 | 1317.9055 | 67.3775 | 2.6986 | 0.85056 | 80.1564 | 65.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.943 | 104.9514
CID=-1850839831 | 15 | 52.5 | 41.2093 | 4 | 46.5 | 9.3 | 1.7333 | 147.7132 | 23.2347 | 266.2308 | 433.2557 | 410.9364 | 27417.3166 | 1.0672 | 0.021442 | 3.7474 | 41.2093 | 154.4265 | 15 | 52.5 | 4 | 46.5 | 488.3739 | 1402.6932 | 70.6501 | 2.8722 | 0.8622 | 82.8254 | 72.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.2093 | 116.6989
CID=-1669271378 | 15 | 55 | 46.8297 | 4 | 49 | 9.8 | 1.7333 | 147.7132 | 23.2347 | 270.0745 | 434.5399 | 410.9364 | 28447.0363 | 1.1598 | 0.024258 | 3.4886 | 46.8298 | 163.3726 | 15 | 55 | 4 | 49 | 488.3739 | 1491.5141 | 73.5026 | 3.054 | 0.87461 | 62.2554 | 81.351 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46.8297 | 125.5944
CID=1321734003 | 15 | 57.5 | 51.704 | 4 | 51.5 | 10.3 | 1.7333 | 147.7132 | 23.2347 | 273.9586 | 435.7999 | 410.9364 | 29245.4066 | 1.2086 | 0.026937 | 3.2019 | 51.704 | 165.5526 | 15 | 57.5 | 4 | 51.5 | 488.3739 | 1584.4992 | 76.83 | 3.2444 | 0.88319 | 62.3952 | 88.9455 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51.704 | 126.9601
CID=374002448 | 15 | 60 | 58.1896 | 4 | 54 | 10.8 | 1.7333 | 147.7132 | 23.2347 | 277.8855 | 437.0361 | 410.9364 | 30236.2814 | 1.2982 | 0.030464 | 2.9683 | 58.1896 | 172.7269 | 15 | 60 | 4 | 54 | 488.3739 | 1681.7842 | 79.8967 | 3.4436 | 0.89215 | 70.3095 | 99.0975 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58.1896 | 126.9601
CID=-929959467 | 15 | 62.5 | 63.9624 | 4 | 56.5 | 11.3 | 1.7333 | 147.7132 | 23.2347 | 281.8586 | 438.2486 | 410.9364 | 30883.0579 | 1.3561 | 0.033909 | 2.7366 | 63.9624 | 175.0399 | 15 | 62.5 | 4 | 56.5 | 488.3739 | 1783.5096 | 83.1726 | 3.6519 | 0.89827 | 57.1099 | 108.1863 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.9624 | 126.9602
CID=-1467767377 | 15 | 65 | 71.2677 | 4 | 59 | 11.8 | 1.7333 | 147.7132 | 23.2347 | 285.881 | 439.4379 | 410.9364 | 31434.1691 | 1.4547 | 0.038277 | 2.5526 | 71.2678 | 181.9149 | 15 | 65 | 4 | 59 | 488.3739 | 1889.8218 | 86.0744 | 3.8696 | 0.90413 | 60.692 | 119.7617 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.2677 | 126.9602
CID=1523238004 | 15 | 67.5 | 78.9695 | 4 | 61.5 | 12.3 | 1.7333 | 147.7132 | 23.2347 | 289.9569 | 440.6043 | 410.9364 | 32114.8242 | 1.552 | 0.04314 | 2.3777 | 78.9696 | 187.7646 | 15 | 67.5 | 4 | 61.5 | 488.3739 | 2000.8736 | 89.0251 | 4.097 | 0.9086 | 61.8296 | 132.0507 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 78.9695 | 126.9602
CID=1704806457 | 15 | 69.99 | 85.6595 | 4 | 63.99 | 12.798 | 1.7333 | 147.7132 | 23.2347 | 294.074 | 441.7436 | 410.9364 | 32724.1573 | 1.6302 | 0.047875 | 2.2241 | 85.6595 | 190.5113 | 15 | 69.99 | 4 | 63.99 | 488.3739 | 2116.3519 | 91.8038 | 4.3335 | 0.91145 | 64.6028 | 142.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 85.6595 | 126.9602
CID=400844542 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-546887013 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1850848928 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1669280475 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1321724906 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=373993351 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-929968564 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1467764178 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1523241203 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1704809656 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=400847741 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-546883814 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1850845729 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1669277276 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1321728105 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=373996550 | 18 | 32.5 | 12.839 | 4 | 26.5 | 5.3 | 1.7322 | 147.3721 | 25.5211 | 236.688 | 421.7412 | 412.6163 | 19385.8401 | 0.78104 | 0.0087954 | 10.7023 | 12.839 | 137.4064 | 18 | 32.5 | 4 | 26.5 | 537.1767 | 827.0396 | 42.7996 | 1.5396 | 0.72424 | 47.2226 | 26.9341 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12.839 | 32.3325
CID=-929965365 | 18 | 35 | 13.112 | 4 | 29 | 5.8 | 1.7322 | 147.3721 | 25.5211 | 240.2788 | 423.2242 | 412.6163 | 19415.2605 | 0.66794 | 0.0090599 | 8.779 | 13.112 | 115.1109 | 18 | 35 | 4 | 29 | 537.1767 | 886.981 | 46.6554 | 1.6512 | 0.72653 | 37.6941 | 27.4204 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.112 | 38.233
CID=-12886574 | 18 | 37.5 | 15.9579 | 4 | 31.5 | 6.3 | 1.7322 | 147.3721 | 25.5211 | 243.8959 | 424.6812 | 412.6163 | 20712.945 | 0.72328 | 0.010138 | 7.6471 | 15.9579 | 122.0316 | 18 | 37.5 | 4 | 31.5 | 537.1767 | 950.1287 | 50.1231 | 1.7687 | 0.74881 | 27.8675 | 32.3786 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 15.9579 | 46.2963
CID=-113643123 | 18 | 40 | 19.0416 | 4 | 34 | 6.8 | 1.7322 | 147.3721 | 25.5211 | 247.5407 | 426.1123 | 412.6163 | 21477.5895 | 0.77847 | 0.011365 | 6.7487 | 19.0416 | 128.5058 | 18 | 40 | 4 | 34 | 537.1767 | 1016.593 | 53.5354 | 1.8925 | 0.77007 | 54.582 | 37.5688 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.0416 | 55.1907
CID=-1699930040 | 18 | 42.5 | 21.9546 | 4 | 36.5 | 7.3 | 1.7322 | 147.3721 | 25.5211 | 251.2145 | 427.5179 | 412.6163 | 22698.3678 | 0.83364 | 0.012607 | 6.1286 | 21.9546 | 134.5513 | 18 | 42.5 | 4 | 36.5 | 537.1767 | 1086.4865 | 56.4864 | 2.0226 | 0.78772 | 40.2554 | 42.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 21.9546 | 64.858
CID=1008750339 | 18 | 45 | 25.0409 | 4 | 39 | 7.8 | 1.7322 | 147.3721 | 25.5211 | 254.9187 | 428.8982 | 412.6163 | 23514.9888 | 0.88869 | 0.013978 | 5.5966 | 25.0409 | 140.1438 | 18 | 45 | 4 | 39 | 537.1767 | 1159.9242 | 59.4072 | 2.1593 | 0.80416 | 54.6166 | 47.311 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25.0409 | 72.3151
CID=-933766938 | 18 | 47.5 | 28.9027 | 4 | 41.5 | 8.3 | 1.7322 | 147.3721 | 25.5211 | 258.655 | 430.2533 | 412.6163 | 24517.1138 | 0.94338 | 0.015704 | 5.0253 | 28.9027 | 145.2438 | 18 | 47.5 | 4 | 41.5 | 537.1767 | 1237.0237 | 62.839 | 2.3028 | 0.82189 | 53.9981 | 53.4297 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.9027 | 83.3388
CID=-1034523487 | 18 | 50 | 33.7506 | 4 | 44 | 8.8 | 1.7322 | 147.3721 | 25.5211 | 262.425 | 431.5835 | 412.6163 | 25427.9404 | 1.0352 | 0.01789 | 4.6066 | 33.7506 | 155.4741 | 18 | 50 | 4 | 44 | 537.1767 | 1317.9055 | 65.8878 | 2.4534 | 0.84035 | 47.5996 | 61.0208 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 33.7506 | 95.4733
CID=1674156892 | 18 | 52.5 | 38.0197 | 4 | 46.5 | 9.3 | 1.7322 | 147.3721 | 25.5211 | 266.2308 | 432.8891 | 412.6163 | 26126.6859 | 1.0898 | 0.01998 | 4.1961 | 38.0198 | 159.5338 | 18 | 52.5 | 4 | 46.5 | 537.1767 | 1402.6932 | 69.1574 | 2.6112 | 0.85371 | 66.508 | 67.6638 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.0197 | 107.8119
CID=87869975 | 18 | 55 | 42.9579 | 4 | 49 | 9.8 | 1.7322 | 147.3721 | 25.5211 | 270.0745 | 434.1702 | 412.6163 | 26976.0193 | 1.1623 | 0.022453 | 3.8567 | 42.9579 | 165.6755 | 18 | 55 | 4 | 49 | 537.1767 | 1491.5141 | 72.268 | 2.7766 | 0.86639 | 92.1028 | 75.3331 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.9579 | 121.2507
CID=1828874154 | 18 | 57.5 | 47.6837 | 4 | 51.5 | 10.3 | 1.7322 | 147.3721 | 25.5211 | 273.9586 | 435.4273 | 412.6163 | 27797.0657 | 1.2162 | 0.024988 | 3.5365 | 47.6837 | 168.6323 | 18 | 57.5 | 4 | 51.5 | 537.1767 | 1584.4992 | 75.5022 | 2.9497 | 0.87625 | 70.6453 | 82.6797 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.6837 | 126.9601
CID=1728117605 | 18 | 60 | 53.1459 | 4 | 54 | 10.8 | 1.7322 | 147.3721 | 25.5211 | 277.8855 | 436.6604 | 412.6163 | 28818.802 | 1.2896 | 0.027986 | 3.2692 | 53.1459 | 173.7429 | 18 | 60 | 4 | 54 | 537.1767 | 1681.7842 | 78.5565 | 3.1308 | 0.88541 | 54.6982 | 91.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 53.1459 | 126.9601
CID=-12883375 | 18 | 62.5 | 59.592 | 4 | 56.5 | 11.3 | 1.7322 | 147.3721 | 25.5211 | 281.8586 | 437.87 | 412.6163 | 29354.4291 | 1.3788 | 0.031599 | 3.0254 | 59.592 | 180.2907 | 18 | 62.5 | 4 | 56.5 | 537.1767 | 1783.5096 | 81.6205 | 3.3202 | 0.89378 | 81.8782 | 101.3007 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 59.592 | 126.9601
CID=-113639924 | 18 | 65 | 65.4574 | 4 | 59 | 11.8 | 1.7322 | 147.3721 | 25.5211 | 285.881 | 439.0563 | 412.6163 | 30528.3091 | 1.4316 | 0.035197 | 2.7719 | 65.4574 | 181.4384 | 18 | 65 | 4 | 59 | 537.1767 | 1889.8218 | 85.0354 | 3.5181 | 0.89963 | 54.899 | 110.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65.4574 | 126.9601
CID=-1699926841 | 18 | 67.5 | 72.1509 | 4 | 61.5 | 12.3 | 1.7322 | 147.3721 | 25.5211 | 289.9569 | 440.2196 | 412.6163 | 30956.6401 | 1.5147 | 0.039429 | 2.5751 | 72.151 | 185.7944 | 18 | 67.5 | 4 | 61.5 | 537.1767 | 2000.8736 | 88.0217 | 3.7248 | 0.90472 | 56.9188 | 121.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72.1509 | 126.9602
CID=1008753538 | 18 | 69.99 | 79.9236 | 4 | 63.99 | 12.798 | 1.7322 | 147.3721 | 25.5211 | 294.074 | 441.3558 | 412.6163 | 31609.6995 | 1.6008 | 0.044479 | 2.3743 | 79.9236 | 189.7651 | 18 | 69.99 | 4 | 63.99 | 537.1767 | 2116.3519 | 91.278 | 3.9398 | 0.90906 | 59.0953 | 133.5788 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 79.9236 | 126.9602
CID=-933763739 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1034520288 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1674160091 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=87873174 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1828877353 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1728120804 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-12884528 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-113641077 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1699927994 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1008752385 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-933764892 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1034521441 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1674158938 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=87872021 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1828876200 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1728119651 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-12889777 | 21 | 35 | 13.5732 | 4 | 29 | 5.8 | 1.7312 | 146.9698 | 27.9878 | 240.2788 | 422.8982 | 414.2684 | 19191.7576 | 0.91786 | 0.0091107 | 11.7657 | 13.5732 | 159.6989 | 21 | 35 | 4 | 29 | 589.5892 | 886.981 | 44.3015 | 1.5044 | 0.73033 | 59.2922 | 28.2372 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.5732 | 24.4855
CID=-113646326 | 21 | 37.5 | 14.0444 | 4 | 31.5 | 6.3 | 1.7312 | 146.9698 | 27.9878 | 243.8959 | 424.3523 | 414.2684 | 19257.3733 | 0.77154 | 0.0094478 | 9.3595 | 14.0444 | 131.4487 | 21 | 37.5 | 4 | 31.5 | 589.5892 | 950.1287 | 48.3811 | 1.6115 | 0.73413 | 42.7008 | 29.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 10.0987 | 14.0444 | 38.7928
CID=-1699933243 | 21 | 40 | 16.5838 | 4 | 34 | 6.8 | 1.7312 | 146.9698 | 27.9878 | 247.5407 | 425.7807 | 414.2684 | 20216.1893 | 0.79165 | 0.010459 | 7.959 | 16.5838 | 131.9897 | 21 | 40 | 4 | 34 | 589.5892 | 1016.593 | 52.0661 | 1.7242 | 0.75336 | 29.2193 | 33.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.5838 | 47.2501
CID=1008747136 | 21 | 42.5 | 19.8198 | 4 | 36.5 | 7.3 | 1.7312 | 146.9698 | 27.9878 | 251.2145 | 427.1835 | 414.2684 | 21288.9235 | 0.84562 | 0.011765 | 6.9568 | 19.8198 | 137.8819 | 21 | 42.5 | 4 | 36.5 | 589.5892 | 1086.4865 | 55.5604 | 1.8428 | 0.77501 | 23.1834 | 38.8554 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.8198 | 56.3689
CID=-933770141 | 21 | 45 | 22.9995 | 4 | 39 | 7.8 | 1.7312 | 146.9698 | 27.9878 | 254.9187 | 428.5609 | 414.2684 | 22147.7036 | 0.91238 | 0.013129 | 6.3213 | 22.9995 | 145.3875 | 21 | 45 | 4 | 39 | 589.5892 | 1159.9242 | 58.4489 | 1.9673 | 0.79353 | 51.656 | 44.036 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.9995 | 66.3301
CID=-1034526690 | 21 | 47.5 | 26.2319 | 4 | 41.5 | 8.3 | 1.7312 | 146.9698 | 27.9878 | 258.655 | 429.9132 | 414.2684 | 23307.4841 | 0.97262 | 0.014587 | 5.7698 | 26.2319 | 151.3531 | 21 | 47.5 | 4 | 41.5 | 589.5892 | 1237.0237 | 61.3255 | 2.0981 | 0.80995 | 38.4697 | 49.2073 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.2319 | 76.5263
CID=1674153689 | 21 | 50 | 29.9299 | 4 | 44 | 8.8 | 1.7312 | 146.9698 | 27.9878 | 262.425 | 431.2407 | 414.2684 | 23936.5497 | 1.0326 | 0.016298 | 5.2388 | 29.9299 | 156.7954 | 21 | 50 | 4 | 44 | 589.5892 | 1317.9055 | 64.4111 | 2.2353 | 0.82613 | 63.1191 | 55.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.9299 | 85.388
CID=87866772 | 21 | 52.5 | 34.5049 | 4 | 46.5 | 9.3 | 1.7312 | 146.9698 | 27.9878 | 266.2308 | 432.5434 | 414.2684 | 25098.7871 | 1.0922 | 0.018434 | 4.6858 | 34.505 | 161.6832 | 21 | 52.5 | 4 | 46.5 | 589.5892 | 1402.6932 | 67.9707 | 2.3791 | 0.84289 | 49.7147 | 62.1966 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.5049 | 97.772
CID=1828870951 | 21 | 55 | 38.7568 | 4 | 49 | 9.8 | 1.7312 | 146.9698 | 27.9878 | 270.0745 | 433.8218 | 414.2684 | 25647.9495 | 1.1517 | 0.020569 | 4.285 | 38.7568 | 166.0742 | 21 | 55 | 4 | 49 | 589.5892 | 1491.5141 | 71.0831 | 2.5298 | 0.85577 | 65.2837 | 68.8088 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 38.7568 | 110.8709
CID=1728114402 | 21 | 57.5 | 43.7196 | 4 | 51.5 | 10.3 | 1.7312 | 146.9698 | 27.9878 | 273.9586 | 435.076 | 414.2684 | 26479.9612 | 1.2211 | 0.023114 | 3.9189 | 43.7197 | 171.333 | 21 | 57.5 | 4 | 51.5 | 589.5892 | 1584.4992 | 74.275 | 2.6875 | 0.86812 | 80.1564 | 76.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 43.7196 | 124.4588
CID=-12882474 | 21 | 60 | 48.373 | 4 | 54 | 10.8 | 1.7312 | 146.9698 | 27.9878 | 277.8855 | 436.3063 | 414.2684 | 27240.4414 | 1.2708 | 0.025688 | 3.583 | 48.373 | 173.322 | 21 | 60 | 4 | 54 | 589.5892 | 1681.7842 | 77.5364 | 2.8525 | 0.87753 | 82.8255 | 83.7528 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.373 | 126.9601
CID=-113639023 | 21 | 62.5 | 54.7306 | 4 | 56.5 | 11.3 | 1.7312 | 146.9698 | 27.9878 | 281.8586 | 437.513 | 414.2684 | 28199.4785 | 1.378 | 0.029147 | 3.3339 | 54.7307 | 182.4658 | 21 | 62.5 | 4 | 56.5 | 589.5892 | 1783.5096 | 80.3648 | 3.025 | 0.88769 | 66.6221 | 93.6758 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 54.7306 | 126.9601
CID=-1699925940 | 21 | 65 | 60.4786 | 4 | 59 | 11.8 | 1.7312 | 146.9698 | 27.9878 | 285.881 | 438.6964 | 414.2684 | 29018.6529 | 1.4482 | 0.03257 | 3.0744 | 60.4787 | 185.9363 | 21 | 65 | 4 | 59 | 589.5892 | 1889.8218 | 83.4738 | 3.2053 | 0.89476 | 59.3308 | 102.6953 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 60.4786 | 126.9602
CID=1008754439 | 21 | 67.5 | 67.0331 | 4 | 61.5 | 12.3 | 1.7312 | 146.9698 | 27.9878 | 289.9569 | 439.8569 | 414.2684 | 29802.8992 | 1.5203 | 0.036595 | 2.8193 | 67.0332 | 188.985 | 21 | 67.5 | 4 | 61.5 | 589.5892 | 2000.8736 | 86.7942 | 3.3937 | 0.90096 | 70.3102 | 113.042 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.0331 | 126.9602
CID=-933762838 | 21 | 69.99 | 74.1546 | 4 | 63.99 | 12.798 | 1.7312 | 146.9698 | 27.9878 | 294.074 | 440.9902 | 414.2684 | 30638.1245 | 1.6158 | 0.041173 | 2.6191 | 74.1547 | 194.2153 | 21 | 69.99 | 4 | 63.99 | 589.5892 | 2116.3519 | 89.728 | 3.5895 | 0.90598 | 54.2829 | 124.3582 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 74.1546 | 126.9602
CID=-1034519387 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1674160992 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=87874075 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1828878254 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1728121705 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-12879275 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-113635824 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1699922741 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1008757638 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-933759639 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1034516188 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1674164191 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=87877274 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1828881453 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1728124904 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-12880428 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-113636977 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1699923894 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1008756485 | 24 | 40 | 15.4516 | 4 | 34 | 6.8 | 1.7302 | 146.5045 | 30.6472 | 247.5407 | 425.4661 | 415.8906 | 19204.4925 | 0.91226 | 0.010001 | 9.9393 | 15.4516 | 153.5785 | 24 | 40 | 4 | 34 | 645.7808 | 1016.593 | 50.2614 | 1.5742 | 0.74505 | 49.1569 | 31.5099 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1001 | 15.4516 | 39.1373
CID=-933760792 | 24 | 42.5 | 16.6006 | 4 | 36.5 | 7.3 | 1.7302 | 146.5045 | 30.6472 | 251.2145 | 426.8662 | 415.8906 | 19623.5845 | 0.83585 | 0.010595 | 8.2915 | 16.6006 | 137.6444 | 24 | 42.5 | 4 | 36.5 | 645.7808 | 1086.4865 | 53.9992 | 1.6824 | 0.75348 | 39.5045 | 33.4741 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.6006 | 48.1204
CID=-1034517341 | 24 | 45 | 19.7334 | 4 | 39 | 7.8 | 1.7302 | 146.5045 | 30.6472 | 254.9187 | 428.241 | 415.8906 | 20975.235 | 0.86365 | 0.011888 | 7.0451 | 19.7335 | 139.0238 | 24 | 45 | 4 | 39 | 645.7808 | 1159.9242 | 57.8927 | 1.7962 | 0.77447 | 24.4916 | 38.713 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 19.7334 | 57.4863
CID=1674163038 | 24 | 47.5 | 22.8929 | 4 | 41.5 | 8.3 | 1.7302 | 146.5045 | 30.6472 | 258.655 | 429.5907 | 415.8906 | 21583.9476 | 0.92962 | 0.013268 | 6.3849 | 22.893 | 146.1697 | 24 | 47.5 | 4 | 41.5 | 645.7808 | 1237.0237 | 60.8054 | 1.9155 | 0.79295 | 54.3412 | 43.8641 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 22.8929 | 67.8348
CID=87876121 | 24 | 50 | 26.2397 | 4 | 44 | 8.8 | 1.7302 | 146.5045 | 30.6472 | 262.425 | 430.9154 | 415.8906 | 22841.6202 | 0.99549 | 0.014794 | 5.8222 | 26.2397 | 152.7731 | 24 | 50 | 4 | 44 | 645.7808 | 1317.9055 | 63.683 | 2.0408 | 0.80998 | 33.781 | 49.2197 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 26.2397 | 79.0043
CID=1828880300 | 24 | 52.5 | 29.8629 | 4 | 46.5 | 9.3 | 1.7302 | 146.5045 | 30.6472 | 266.2308 | 432.2155 | 415.8906 | 23443.0267 | 1.063 | 0.016511 | 5.3275 | 29.8629 | 159.0953 | 24 | 52.5 | 4 | 46.5 | 645.7808 | 1402.6932 | 66.5671 | 2.1721 | 0.82585 | 61.261 | 54.9394 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29.8629 | 87.3441
CID=1728123751 | 24 | 55 | 34.4237 | 4 | 49 | 9.8 | 1.7302 | 146.5045 | 30.6472 | 270.0745 | 433.4912 | 415.8906 | 24527.4315 | 1.1263 | 0.018684 | 4.771 | 34.4237 | 164.235 | 24 | 55 | 4 | 49 | 645.7808 | 1491.5141 | 70.0343 | 2.3096 | 0.84262 | 51.2497 | 62.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 34.4237 | 99.9239
CID=-12885677 | 24 | 57.5 | 40.2609 | 4 | 51.5 | 10.3 | 1.7302 | 146.5045 | 30.6472 | 273.9586 | 434.7427 | 415.8906 | 25303.4282 | 1.2525 | 0.021488 | 4.4155 | 40.261 | 177.7721 | 24 | 57.5 | 4 | 51.5 | 645.7808 | 1584.4992 | 72.8365 | 2.4536 | 0.8598 | 47.6014 | 71.145 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.2609 | 113.6981
CID=-113642226 | 24 | 60 | 44.9849 | 4 | 54 | 10.8 | 1.7302 | 146.5045 | 30.6472 | 277.8855 | 435.9703 | 415.8906 | 26004.2304 | 1.3079 | 0.024012 | 4.0124 | 44.985 | 180.4964 | 24 | 60 | 4 | 54 | 645.7808 | 1681.7842 | 76.1194 | 2.6043 | 0.87086 | 66.5082 | 78.4825 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 44.9849 | 126.9601
CID=-1699929143 | 24 | 62.5 | 50.4735 | 4 | 56.5 | 11.3 | 1.7302 | 146.5045 | 30.6472 | 281.8586 | 437.1743 | 415.8906 | 26806.1774 | 1.3873 | 0.027015 | 3.684 | 50.4735 | 185.9453 | 24 | 62.5 | 4 | 56.5 | 645.7808 | 1783.5096 | 79.2123 | 2.7618 | 0.88119 | 91.9228 | 87.0258 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50.4735 | 126.9601
CID=1008751236 | 24 | 65 | 55.832 | 4 | 59 | 11.8 | 1.7302 | 146.5045 | 30.6472 | 285.881 | 438.355 | 415.8906 | 27565.3725 | 1.4515 | 0.03016 | 3.38 | 55.832 | 188.7121 | 24 | 65 | 4 | 59 | 645.7808 | 1889.8218 | 82.3713 | 2.9264 | 0.88918 | 72.1666 | 95.4002 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.832 | 126.9601
CID=-933766041 | 24 | 67.5 | 61.542 | 4 | 61.5 | 12.3 | 1.7302 | 146.5045 | 30.6472 | 289.9569 | 439.5127 | 415.8906 | 28560.0277 | 1.5173 | 0.033678 | 3.1048 | 61.542 | 191.0753 | 24 | 67.5 | 4 | 61.5 | 645.7808 | 2000.8736 | 85.5418 | 3.0984 | 0.89589 | 54.6982 | 104.3694 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.542 | 126.9602
CID=-1034522590 | 24 | 69.99 | 68.6833 | 4 | 63.99 | 12.798 | 1.7302 | 146.5045 | 30.6472 | 294.074 | 440.6434 | 415.8906 | 29079.7472 | 1.6229 | 0.038104 | 2.8783 | 68.6834 | 197.6932 | 24 | 69.99 | 4 | 63.99 | 645.7808 | 2116.3519 | 88.4796 | 3.2772 | 0.90226 | 62.5661 | 115.6574 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.6833 | 126.9601
CID=1674157789 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=87870872 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1828875051 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1728118502 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-12894774 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-113651323 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1699938240 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1008742139 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-933775138 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1034531687 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1674148692 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=87861775 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1828865954 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1728109405 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-12891575 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-113648124 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1699935041 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1008745338 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-933771939 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1034528488 | 27 | 42.5 | 16.346 | 4 | 36.5 | 7.3 | 1.7292 | 145.9744 | 33.5123 | 251.2145 | 426.563 | 417.481 | 19201.9902 | 1.0169 | 0.010412 | 10.3435 | 16.346 | 169.0759 | 27 | 42.5 | 4 | 36.5 | 705.9244 | 1086.4865 | 52.4207 | 1.5391 | 0.75165 | 47.9006 | 33.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.346 | 41.1277
CID=1674151891 | 27 | 45 | 16.5416 | 4 | 39 | 7.8 | 1.7292 | 145.9744 | 33.5123 | 254.9187 | 427.9352 | 417.481 | 19238.8163 | 0.86984 | 0.010713 | 8.5483 | 16.5416 | 141.4027 | 27 | 45 | 4 | 39 | 705.9244 | 1159.9242 | 56.132 | 1.6431 | 0.75306 | 38.0365 | 33.3739 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 16.5416 | 48.8753
CID=87864974 | 27 | 47.5 | 20.0626 | 4 | 41.5 | 8.3 | 1.7292 | 145.9744 | 33.5123 | 258.655 | 429.2823 | 417.481 | 20487.5582 | 0.94177 | 0.012161 | 7.4555 | 20.0626 | 149.5773 | 27 | 47.5 | 4 | 41.5 | 705.9244 | 1237.0237 | 59.4985 | 1.7523 | 0.77651 | 27.4859 | 39.255 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.0626 | 58.5775
CID=1828869153 | 27 | 50 | 23.8529 | 4 | 44 | 8.8 | 1.7292 | 145.9744 | 33.5123 | 262.425 | 430.6045 | 417.481 | 21235.6769 | 1.0135 | 0.013795 | 6.5883 | 23.8529 | 157.1514 | 27 | 50 | 4 | 44 | 705.9244 | 1317.9055 | 62.8074 | 1.8669 | 0.79809 | 51.3115 | 45.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 23.8529 | 69.1973
CID=1728112604 | 27 | 52.5 | 27.4146 | 4 | 46.5 | 9.3 | 1.7292 | 145.9744 | 33.5123 | 266.2308 | 431.902 | 417.481 | 22297.3712 | 1.0852 | 0.01544 | 5.9875 | 27.4146 | 164.1439 | 27 | 52.5 | 4 | 46.5 | 705.9244 | 1402.6932 | 65.7044 | 1.987 | 0.8154 | 44.6177 | 51.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 27.4146 | 80.6498
CID=1068842605 | 27 | 55 | 31.1505 | 4 | 49 | 9.8 | 1.7292 | 145.9744 | 33.5123 | 270.0745 | 433.1751 | 417.481 | 23218.814 | 1.1568 | 0.017248 | 5.4742 | 31.1505 | 170.5226 | 27 | 55 | 4 | 49 | 705.9244 | 1491.5141 | 68.5605 | 2.1129 | 0.83093 | 46.1921 | 56.9585 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 31.1505 | 89.9111
CID=-235119310 | 27 | 57.5 | 35.5589 | 4 | 51.5 | 10.3 | 1.7292 | 145.9744 | 33.5123 | 273.9586 | 434.4241 | 417.481 | 23956.3065 | 1.228 | 0.019423 | 4.9565 | 35.5589 | 176.2489 | 27 | 57.5 | 4 | 51.5 | 705.9244 | 1584.4992 | 71.7043 | 2.2446 | 0.84631 | 59.8676 | 63.8376 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.5589 | 102.1624
CID=-618200861 | 27 | 60 | 40.7067 | 4 | 54 | 10.8 | 1.7292 | 145.9744 | 33.5123 | 277.8855 | 435.6491 | 417.481 | 25018.8375 | 1.2988 | 0.022026 | 4.454 | 40.7067 | 181.3065 | 27 | 60 | 4 | 54 | 705.9244 | 1681.7842 | 75.1196 | 2.3824 | 0.86094 | 48.719 | 71.8372 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.7067 | 116.2504
CID=-1922162776 | 27 | 62.5 | 45.5787 | 4 | 56.5 | 11.3 | 1.7292 | 145.9744 | 33.5123 | 281.8586 | 436.8505 | 417.481 | 25526.2685 | 1.3695 | 0.024679 | 4.0751 | 45.5787 | 185.7384 | 27 | 62.5 | 4 | 56.5 | 705.9244 | 1783.5096 | 78.1938 | 2.5265 | 0.8721 | 65.5957 | 79.4055 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 45.5787 | 126.9601
CID=147962241 | 27 | 65 | 51.2946 | 4 | 59 | 11.8 | 1.7292 | 145.9744 | 33.5123 | 285.881 | 438.0286 | 417.481 | 26315.3351 | 1.4555 | 0.027864 | 3.7341 | 51.2946 | 191.5399 | 27 | 65 | 4 | 59 | 705.9244 | 1889.8218 | 81.2946 | 2.6771 | 0.88254 | 80.1564 | 88.3066 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 51.2946 | 126.9601
CID=-1155999674 | 27 | 67.5 | 56.4575 | 4 | 61.5 | 12.3 | 1.7292 | 145.9744 | 33.5123 | 289.9569 | 439.1838 | 417.481 | 27035.0003 | 1.5099 | 0.031023 | 3.4106 | 56.4575 | 192.5538 | 27 | 67.5 | 4 | 61.5 | 705.9244 | 2000.8736 | 84.5212 | 2.8344 | 0.89 | 83.6476 | 96.3804 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.4575 | 126.9602
CID=-1539081225 | 27 | 69.99 | 63.2881 | 4 | 63.99 | 12.798 | 1.7292 | 145.9744 | 33.5123 | 294.074 | 440.3118 | 417.481 | 27922.4208 | 1.6211 | 0.035161 | 3.1611 | 63.2881 | 200.0608 | 27 | 69.99 | 4 | 63.99 | 705.9244 | 2116.3519 | 87.4046 | 2.998 | 0.89763 | 66.6222 | 107.122 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.2881 | 126.9602
CID=1451924156 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1384363963 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1606641418 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1068845804 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-235116111 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-618197662 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1922159577 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=147965440 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1155996475 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1539078026 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1451927355 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1384360764 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1606644617 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1068844651 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-235117264 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-618198815 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1922160730 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=147964287 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1155997628 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1539079179 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1451926202 | 30 | 45 | 17.2285 | 4 | 39 | 7.8 | 1.7283 | 145.3777 | 36.5977 | 254.9187 | 427.6403 | 419.0371 | 19062.9139 | 1.1581 | 0.010836 | 11.0319 | 17.2285 | 190.0632 | 30 | 45 | 4 | 39 | 770.1963 | 1159.9242 | 54.3128 | 1.506 | 0.75791 | 52.6403 | 34.5368 | 0 | 0 | 0 | 0 | 0 | 0 | 10.164 | 17.2285 | 35.2368
CID=-1384361917 | 30 | 47.5 | 17.3626 | 4 | 41.5 | 8.3 | 1.7283 | 145.3777 | 36.5977 | 258.655 | 428.9849 | 419.0371 | 19005.8747 | 0.98372 | 0.011133 | 9.0868 | 17.3626 | 157.7713 | 30 | 47.5 | 4 | 41.5 | 770.1963 | 1237.0237 | 57.914 | 1.6061 | 0.75885 | 42.6255 | 34.763 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1524 | 17.3626 | 49.4867
CID=1606643464 | 30 | 50 | 20.758 | 4 | 44 | 8.8 | 1.7283 | 145.3777 | 36.5977 | 262.425 | 430.3047 | 419.0371 | 20000.9457 | 1.0249 | 0.012575 | 7.7327 | 20.758 | 160.5153 | 30 | 50 | 4 | 44 | 770.1963 | 1317.9055 | 61.5228 | 1.7111 | 0.78074 | 29.1111 | 40.3958 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 20.758 | 59.6018
CID=1068839402 | 30 | 52.5 | 24.5286 | 4 | 46.5 | 9.3 | 1.7283 | 145.3777 | 36.5977 | 266.2308 | 431.5997 | 419.0371 | 21028.1613 | 1.0807 | 0.014241 | 6.7327 | 24.5286 | 165.1446 | 30 | 52.5 | 4 | 46.5 | 770.1963 | 1402.6932 | 65.0019 | 1.8212 | 0.80158 | 23.1824 | 46.4923 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24.5286 | 70.4551
CID=-235122513 | 30 | 55 | 28.2091 | 4 | 49 | 9.8 | 1.7283 | 145.3777 | 36.5977 | 270.0745 | 432.8703 | 419.0371 | 21755.8811 | 1.1593 | 0.015973 | 6.1219 | 28.2091 | 172.6925 | 30 | 55 | 4 | 49 | 770.1963 | 1491.5141 | 67.8538 | 1.9365 | 0.81892 | 54.3168 | 52.3367 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 28.2091 | 82.2635
CID=-618204064 | 30 | 57.5 | 32.0207 | 4 | 51.5 | 10.3 | 1.7283 | 145.3777 | 36.5977 | 273.9586 | 434.1168 | 419.0371 | 22912.2198 | 1.2331 | 0.017858 | 5.5871 | 32.0207 | 178.9023 | 30 | 57.5 | 4 | 51.5 | 770.1963 | 1584.4992 | 70.7099 | 2.0573 | 0.8342 | 33.7811 | 58.3201 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 32.0207 | 95.0594
CID=-1922165979 | 30 | 60 | 36.1156 | 4 | 54 | 10.8 | 1.7283 | 145.3777 | 36.5977 | 277.8855 | 435.3393 | 419.0371 | 23431.0331 | 1.3022 | 0.019969 | 5.0896 | 36.1156 | 183.8132 | 30 | 60 | 4 | 54 | 770.1963 | 1681.7842 | 73.675 | 2.1836 | 0.84805 | 61.2611 | 64.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.1156 | 104.3567
CID=147959038 | 30 | 62.5 | 41.2449 | 4 | 56.5 | 11.3 | 1.7283 | 145.3777 | 36.5977 | 281.8586 | 436.5383 | 419.0371 | 24502.2416 | 1.3663 | 0.022633 | 4.5443 | 41.2449 | 187.4305 | 30 | 62.5 | 4 | 56.5 | 770.1963 | 1783.5096 | 77.1569 | 2.3157 | 0.86229 | 51.2498 | 72.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.2449 | 118.617
CID=-1156002877 | 30 | 65 | 47.3217 | 4 | 59 | 11.8 | 1.7283 | 145.3777 | 36.5977 | 285.881 | 437.7139 | 419.0371 | 25150.612 | 1.4905 | 0.025868 | 4.194 | 47.3217 | 198.4659 | 30 | 65 | 4 | 59 | 770.1963 | 1889.8218 | 80.0011 | 2.4537 | 0.87556 | 62.5091 | 82.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.3217 | 126.9601
CID=-1539084428 | 30 | 67.5 | 52.7777 | 4 | 61.5 | 12.3 | 1.7283 | 145.3777 | 36.5977 | 289.9569 | 438.8665 | 419.0371 | 25844.5967 | 1.5601 | 0.029051 | 3.8155 | 52.7777 | 201.3733 | 30 | 67.5 | 4 | 61.5 | 770.1963 | 2000.8736 | 83.2103 | 2.5979 | 0.88485 | 66.5089 | 90.6222 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 52.7777 | 126.9602
CID=1451920953 | 30 | 69.99 | 58.743 | 4 | 63.99 | 12.798 | 1.7283 | 145.3777 | 36.5977 | 294.074 | 439.9919 | 419.0371 | 26598.2368 | 1.6433 | 0.032684 | 3.4957 | 58.743 | 205.3486 | 30 | 69.99 | 4 | 63.99 | 770.1963 | 2116.3519 | 86.3017 | 2.7478 | 0.89281 | 91.8935 | 99.9666 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 58.743 | 126.9602
CID=-1384367166 | -18 | -5 | 6.2915 | 4 | -11 | 0 | 1.7524 | 147.8757 | 7.2169 | 185.3801 | 401.7246 | 391.078 | 20092.8994 | 0.31603 | 0.0061334 | 10.3324 | 6.2915 | 65.007 | -18 | -5 | 4 | -11 | 144.6004 | 243.3424 | 7.6743 | 1.6829 | 0.66059 | 110 | 14.4704 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5498 | 11.5167
CID=1606638215 | -18 | -2.5 | 7.8378 | 4 | -8.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 188.676 | 403.6805 | 391.078 | 21630.309 | 0.35483 | 0.0064849 | 9.1629 | 7.8378 | 71.8175 | -18 | -2.5 | 4 | -8.5 | 144.6004 | 267.1911 | 11.1354 | 1.8478 | 0.67728 | 110 | 17.5827 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.577 | 14.6204
CID=1068846705 | -18 | 0 | 9.637 | 4 | -6 | 0 | 1.7524 | 147.8757 | 7.2169 | 191.9873 | 405.6071 | 391.078 | 23112.0586 | 0.39665 | 0.0069823 | 8.1944 | 9.637 | 78.9696 | -18 | 0 | 4 | -6 | 144.6004 | 292.8032 | 14.5027 | 2.0249 | 0.69535 | 110 | 21.0569 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.7893 | 18.1802
CID=-235115210 | -18 | 2.5 | 11.2248 | 4 | -3.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 195.3144 | 407.5045 | 391.078 | 24306.693 | 0.42537 | 0.0074893 | 7.4186 | 11.2248 | 83.2723 | -18 | 2.5 | 4 | -3.5 | 144.6004 | 320.2635 | 17.575 | 2.2148 | 0.71017 | 110 | 24.0143 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8511 | 21.3458
CID=-618196761 | -18 | 5 | 13.6118 | 4 | -1 | 0 | 1.7524 | 147.8757 | 7.2169 | 198.6579 | 409.3731 | 391.078 | 25667.9479 | 0.4767 | 0.0082484 | 6.7387 | 13.6118 | 91.7265 | -18 | 5 | 4 | -1 | 144.6004 | 349.6586 | 20.8001 | 2.4181 | 0.73064 | 110 | 28.3053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5588 | 25.7708
CID=-1922158676 | -18 | 7.5 | 15.9837 | 4 | 1.5 | 0.3 | 1.7524 | 147.8757 | 7.2169 | 202.0183 | 411.2128 | 391.078 | 26878.878 | 0.51838 | 0.0090545 | 6.1316 | 15.9837 | 98.0053 | -18 | 7.5 | 4 | 1.5 | 144.6004 | 381.0767 | 24.0355 | 2.6354 | 0.749 | 110 | 32.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.097 | 30.644
CID=147966341 | -18 | 10 | 18.808 | 4 | 4 | 0.8 | 1.7524 | 147.8757 | 7.2169 | 205.396 | 413.024 | 391.078 | 28069.8605 | 0.56889 | 0.010036 | 5.6163 | 18.808 | 105.6323 | -18 | 10 | 4 | 4 | 144.6004 | 414.6075 | 27.211 | 2.8673 | 0.76856 | 110 | 37.1811 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0916 | 35.9571
CID=-1155995574 | -18 | 12.5 | 21.4318 | 4 | 6.5 | 1.3 | 1.7524 | 147.8757 | 7.2169 | 208.7918 | 414.8068 | 391.078 | 29071.1089 | 0.60825 | 0.011006 | 5.1735 | 21.4318 | 110.8764 | -18 | 12.5 | 4 | 6.5 | 144.6004 | 450.3422 | 30.268 | 3.1144 | 0.78472 | 110 | 41.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2624 | 39.94
CID=-1539077125 | -18 | 15 | 24.6415 | 4 | 9 | 1.8 | 1.7524 | 147.8757 | 7.2169 | 212.2062 | 416.5615 | 391.078 | 30095.8079 | 0.6569 | 0.0122 | 4.7684 | 24.6415 | 117.5009 | -18 | 15 | 4 | 9 | 144.6004 | 488.3739 | 33.4297 | 3.3774 | 0.80216 | 110 | 46.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.7059 | 45.4484
CID=1451928256 | -18 | 17.5 | 27.9202 | 4 | 11.5 | 2.3 | 1.7524 | 147.8757 | 7.2169 | 215.6398 | 418.2881 | 391.078 | 31047.2267 | 0.70114 | 0.013471 | 4.4056 | 27.9202 | 123.0061 | -18 | 17.5 | 4 | 11.5 | 144.6004 | 528.7968 | 36.5918 | 3.657 | 0.81765 | 110 | 51.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3419 | 50.6552
CID=-1384359863 | -18 | 20 | 30.4452 | 4 | 14 | 2.8 | 1.7524 | 147.8757 | 7.2169 | 219.0933 | 419.9871 | 391.078 | 31804.1072 | 0.71922 | 0.014555 | 4.0629 | 30.4452 | 123.6957 | -18 | 20 | 4 | 14 | 144.6004 | 571.7069 | 39.8772 | 3.9537 | 0.82818 | 110 | 55.8532 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3788 | 51.6444
CID=1606645518 | -18 | 22.5 | 32.8006 | 4 | 16.5 | 3.3 | 1.7524 | 147.8757 | 7.2169 | 222.5675 | 421.6585 | 391.078 | 32517.1899 | 0.73382 | 0.015632 | 3.77 | 32.8006 | 123.6571 | -18 | 22.5 | 4 | 16.5 | 144.6004 | 617.2019 | 43.013 | 4.2683 | 0.83703 | 108.9014 | 59.5385 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6859 | 26.5651 | 51.5068
CID=1068849904 | -18 | 25 | 36.1156 | 4 | 19 | 3.8 | 1.7524 | 147.8757 | 7.2169 | 226.0633 | 423.3026 | 391.078 | 33337.2865 | 0.76772 | 0.017081 | 3.5078 | 36.1156 | 126.6857 | -18 | 25 | 4 | 19 | 144.6004 | 665.3809 | 46.1549 | 4.6015 | 0.84805 | 109.5449 | 64.7038 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9592 | 30.9668 | 51.5623
CID=-235112011 | -18 | 27.5 | 39.6895 | 4 | 21.5 | 4.3 | 1.7524 | 147.8757 | 7.2169 | 229.5813 | 424.9196 | 391.078 | 34145.7624 | 0.80073 | 0.018687 | 3.2582 | 39.6895 | 129.3146 | -18 | 27.5 | 4 | 21.5 | 144.6004 | 716.3449 | 49.4497 | 4.954 | 0.8583 | 108.948 | 70.2575 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 35.6287 | 51.8719
CID=-618193562 | -18 | 30 | 43.6961 | 4 | 24 | 4.8 | 1.7524 | 147.8757 | 7.2169 | 233.1226 | 426.5097 | 391.078 | 34936.2772 | 0.83819 | 0.020523 | 3.0299 | 43.6961 | 132.3966 | -18 | 30 | 4 | 24 | 144.6004 | 770.1963 | 52.7742 | 5.3264 | 0.86806 | 108.5254 | 76.4799 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.9637 | 51.8934
CID=-1922155477 | -18 | 32.5 | 49.0721 | 4 | 26.5 | 5.3 | 1.7524 | 147.8757 | 7.2169 | 236.688 | 428.0733 | 391.078 | 35791.9466 | 0.90883 | 0.022945 | 2.8594 | 49.0721 | 140.3146 | -18 | 32.5 | 4 | 26.5 | 144.6004 | 827.0396 | 55.503 | 5.7195 | 0.87878 | 108.8329 | 84.8415 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.2998 | 51.389
CID=147969540 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1155992375 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1539073926 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1451931455 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1384356664 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1606648717 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1068848751 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-235113164 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-618194715 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1922156630 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=147968387 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1155993528 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1539075079 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1451930302 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1384357817 | -18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1606647564 | -15 | -5 | 0 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1068843502 | -15 | -2.5 | 6.6501 | 4 | -8.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 188.676 | 402.9994 | 392.9623 | 19751.2679 | 0.35298 | 0.0062231 | 10.8433 | 6.6501 | 72.1087 | -15 | -2.5 | 4 | -8.5 | 163.9401 | 267.1911 | 9.7672 | 1.6298 | 0.66456 | 109.3291 | 15.2037 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5365 | 4.9292 | 11.8126
CID=-235118413 | -15 | 0 | 8.1179 | 4 | -6 | 0 | 1.7499 | 148.1062 | 8.1279 | 191.9873 | 404.9188 | 392.9623 | 21158.7005 | 0.38671 | 0.0065866 | 9.5738 | 8.1179 | 77.719 | -15 | 0 | 4 | -6 | 163.9401 | 292.8032 | 13.0687 | 1.786 | 0.68018 | 109.7218 | 18.1331 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2782 | 5.7776 | 15.1388
CID=-618199964 | -15 | 2.5 | 9.9091 | 4 | -3.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 195.3144 | 406.8092 | 392.9623 | 22571.867 | 0.42807 | 0.0070973 | 8.5383 | 9.9091 | 84.607 | -15 | 2.5 | 4 | -3.5 | 163.9401 | 320.2635 | 16.3336 | 1.9535 | 0.69796 | 110 | 21.5704 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.9172 | 18.8847
CID=-1922161879 | -15 | 5 | 12.0105 | 4 | -1 | 0 | 1.7499 | 148.1062 | 8.1279 | 198.6579 | 408.6707 | 392.9623 | 23947.2188 | 0.47421 | 0.0077471 | 7.6717 | 12.0105 | 92.1416 | -15 | 5 | 4 | -1 | 163.9401 | 349.6586 | 19.5698 | 2.1328 | 0.71714 | 110 | 25.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3095 | 23.1137
CID=147963138 | -15 | 7.5 | 14.0189 | 4 | 1.5 | 0.3 | 1.7499 | 148.1062 | 8.1279 | 202.0183 | 410.5034 | 392.9623 | 25105.2076 | 0.51172 | 0.008423 | 6.9698 | 14.0189 | 97.709 | -15 | 7.5 | 4 | 1.5 | 163.9401 | 381.0767 | 22.5996 | 2.3245 | 0.73393 | 110 | 29.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.7669 | 26.7752
CID=-1155998777 | -15 | 10 | 16.8282 | 4 | 4 | 0.8 | 1.7499 | 148.1062 | 8.1279 | 205.396 | 412.3077 | 392.9623 | 26410.9034 | 0.5683 | 0.0093668 | 6.3342 | 16.8282 | 106.5934 | -15 | 10 | 4 | 4 | 163.9401 | 414.6075 | 25.8115 | 2.529 | 0.7551 | 110 | 33.8601 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7699 | 32.0031
CID=-1539080328 | -15 | 12.5 | 19.5875 | 4 | 6.5 | 1.3 | 1.7499 | 148.1062 | 8.1279 | 208.7918 | 414.0836 | 392.9623 | 27554.2189 | 0.6149 | 0.010348 | 5.7816 | 19.5875 | 113.2465 | -15 | 12.5 | 4 | 6.5 | 163.9401 | 450.3422 | 28.9787 | 2.747 | 0.77355 | 110 | 38.4721 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.601 | 37.5469
CID=1451925053 | -15 | 15 | 22.3799 | 4 | 9 | 1.8 | 1.7499 | 148.1062 | 8.1279 | 212.2062 | 415.8315 | 392.9623 | 28568.3575 | 0.65731 | 0.011386 | 5.3089 | 22.3799 | 118.8124 | -15 | 15 | 4 | 9 | 163.9401 | 488.3739 | 32.0624 | 2.979 | 0.79012 | 110 | 43.0349 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8508 | 41.9673
CID=-1384363066 | -15 | 17.5 | 25.7156 | 4 | 11.5 | 2.3 | 1.7499 | 148.1062 | 8.1279 | 215.6398 | 417.5513 | 392.9623 | 29575.5136 | 0.71046 | 0.012641 | 4.899 | 25.7156 | 125.9797 | -15 | 17.5 | 4 | 11.5 | 163.9401 | 528.7968 | 35.1084 | 3.2255 | 0.80748 | 110 | 48.3864 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.3412 | 47.8386
CID=1606642315 | -15 | 20 | 29.2755 | 4 | 14 | 2.8 | 1.7499 | 148.1062 | 8.1279 | 219.0933 | 419.2435 | 392.9623 | 30546.1298 | 0.76044 | 0.014024 | 4.5163 | 29.2755 | 132.2171 | -15 | 20 | 4 | 14 | 163.9401 | 571.7069 | 38.2781 | 3.4873 | 0.82345 | 110 | 54.0163 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.1691 | 53.5948
CID=1068834405 | -15 | 22.5 | 32.6556 | 4 | 16.5 | 3.3 | 1.7499 | 148.1062 | 8.1279 | 222.5675 | 420.9082 | 392.9623 | 31399.3341 | 0.80054 | 0.015412 | 4.1771 | 32.6556 | 136.4072 | -15 | 22.5 | 4 | 16.5 | 163.9401 | 617.2019 | 41.4094 | 3.7648 | 0.83651 | 110 | 59.3122 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0585 | 58.447
CID=-235127510 | -15 | 25 | 35.5809 | 4 | 19 | 3.8 | 1.7499 | 148.1062 | 8.1279 | 226.0633 | 422.5457 | 392.9623 | 32149.288 | 0.82473 | 0.01671 | 3.8685 | 35.5809 | 137.6459 | -15 | 25 | 4 | 19 | 163.9401 | 665.3809 | 44.5604 | 4.0587 | 0.84638 | 110 | 63.8718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8402 | 58.803
CID=-618209061 | -15 | 27.5 | 38.1599 | 4 | 21.5 | 4.3 | 1.7499 | 148.1062 | 8.1279 | 229.5813 | 424.156 | 392.9623 | 32823.679 | 0.84049 | 0.01795 | 3.5985 | 38.1599 | 137.3199 | -15 | 27.5 | 4 | 21.5 | 163.9401 | 716.3449 | 47.6096 | 4.3696 | 0.8541 | 109.7179 | 67.8816 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5769 | 31.3546 | 58.5759
CID=-1922170976 | -15 | 30 | 41.8013 | 4 | 24 | 4.8 | 1.7499 | 148.1062 | 8.1279 | 233.1226 | 425.7396 | 392.9623 | 33614.5479 | 0.87494 | 0.019619 | 3.3456 | 41.8013 | 139.8509 | -15 | 30 | 4 | 24 | 163.9401 | 770.1963 | 50.7838 | 4.698 | 0.86366 | 109.5656 | 73.5369 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.422 | 57.9392
CID=147954041 | -15 | 32.5 | 45.7204 | 4 | 26.5 | 5.3 | 1.7499 | 148.1062 | 8.1279 | 236.688 | 427.2966 | 392.9623 | 34380.2308 | 0.91039 | 0.021468 | 3.1118 | 45.7204 | 142.2709 | -15 | 32.5 | 4 | 26.5 | 163.9401 | 827.0396 | 54.0136 | 5.0448 | 0.87239 | 108.6109 | 79.6257 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 41.4958 | 58.3942
CID=-1156007874 | -15 | 35 | 50.764 | 4 | 29 | 5.8 | 1.7499 | 148.1062 | 8.1279 | 240.2788 | 428.8272 | 392.9623 | 35188.4321 | 0.96396 | 0.023822 | 2.8993 | 50.764 | 147.1804 | -15 | 35 | 4 | 29 | 163.9401 | 886.981 | 57.2505 | 5.4104 | 0.88168 | 108.5905 | 87.4789 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.0343 | 58.9531
CID=-1539089425 | -15 | 37.5 | 55.6823 | 4 | 31.5 | 6.3 | 1.7499 | 148.1062 | 8.1279 | 243.8959 | 430.3317 | 392.9623 | 35925.8576 | 1.0231 | 0.026248 | 2.7388 | 55.6823 | 152.5051 | -15 | 37.5 | 4 | 31.5 | 163.9401 | 950.1287 | 59.8932 | 5.7956 | 0.88898 | 108.7501 | 95.1658 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.3815 | 56.5848
CID=1451915956 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1384372163 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1606633218 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1068837604 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-235124311 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-618205862 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1922167777 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=147957240 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1156004675 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1539086226 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1451919155 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1384368964 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1606636417 | -15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-739677048 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-840433597 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1862070510 | -12 | 0 | 7.1901 | 4 | -6 | 0 | 1.7476 | 148.2918 | 9.1273 | 191.9873 | 404.2823 | 394.8346 | 19589.3634 | 0.40185 | 0.0063526 | 11.3369 | 7.1901 | 81.5136 | -12 | 0 | 4 | -6 | 185.2442 | 292.8032 | 12.0033 | 1.5806 | 0.67042 | 108.0403 | 16.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3196 | 5.4538 | 12.3991
CID=846609869 | -12 | 2.5 | 8.368 | 4 | -3.5 | 0 | 1.7476 | 148.2918 | 9.1273 | 195.3144 | 406.166 | 394.8346 | 20680.0028 | 0.41943 | 0.0066863 | 10.0005 | 8.368 | 83.6847 | -12 | 2.5 | 4 | -3.5 | 185.2442 | 320.2635 | 15.0312 | 1.7289 | 0.68275 | 109.982 | 18.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0449 | 5.9439 | 15.6403
CID=-1660557412 | -12 | 5 | 10.3835 | 4 | -1 | 0 | 1.7476 | 148.2918 | 9.1273 | 198.6579 | 408.021 | 394.8346 | 22134.5337 | 0.46795 | 0.0072651 | 8.8411 | 10.3835 | 91.8016 | -12 | 5 | 4 | -1 | 185.2442 | 349.6586 | 18.3846 | 1.8876 | 0.70244 | 110 | 22.4588 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3298 | 19.5445
CID=-1761313961 | -12 | 7.5 | 12.4179 | 4 | 1.5 | 0.3 | 1.7476 | 148.2918 | 9.1273 | 202.0183 | 409.8472 | 394.8346 | 23432.5067 | 0.51187 | 0.0079137 | 7.9479 | 12.4179 | 98.6966 | -12 | 7.5 | 4 | 1.5 | 185.2442 | 381.0767 | 21.4715 | 2.0572 | 0.72067 | 110 | 26.18 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5649 | 23.9769
CID=1512016422 | -12 | 10 | 14.4464 | 4 | 4 | 0.8 | 1.7476 | 148.2918 | 9.1273 | 205.396 | 411.6451 | 394.8346 | 24571.2154 | 0.54833 | 0.0086078 | 7.1904 | 14.4464 | 103.8757 | -12 | 10 | 4 | 4 | 185.2442 | 414.6075 | 24.5072 | 2.2382 | 0.73732 | 110 | 29.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.993 | 27.8065
CID=-74270495 | -12 | 12.5 | 17.4118 | 4 | 6.5 | 1.3 | 1.7476 | 148.2918 | 9.1273 | 208.7918 | 413.4146 | 394.8346 | 25868.6144 | 0.6113 | 0.0096117 | 6.5316 | 17.4118 | 113.7276 | -12 | 12.5 | 4 | 6.5 | 185.2442 | 450.3422 | 27.6475 | 2.4311 | 0.75919 | 110 | 34.8458 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1391 | 33.2299
CID=1102083680 | -12 | 15 | 20.2983 | 4 | 9 | 1.8 | 1.7476 | 148.2918 | 9.1273 | 212.2062 | 415.1561 | 394.8346 | 27010.7226 | 0.66171 | 0.010647 | 5.9536 | 20.2983 | 120.8477 | -12 | 15 | 4 | 9 | 185.2442 | 488.3739 | 30.7712 | 2.6364 | 0.77796 | 110 | 39.6423 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0304 | 39.1019
CID=1001327131 | -12 | 17.5 | 23.6861 | 4 | 11.5 | 2.3 | 1.7476 | 148.2918 | 9.1273 | 215.6398 | 416.8697 | 394.8346 | 28130.078 | 0.72141 | 0.011885 | 5.4578 | 23.6861 | 129.2729 | -12 | 17.5 | 4 | 11.5 | 185.2442 | 528.7968 | 33.8581 | 2.8546 | 0.79721 | 110 | 45.1413 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.4121 | 45.5079
CID=-739673849 | -12 | 20 | 26.8146 | 4 | 14 | 2.8 | 1.7476 | 148.2918 | 9.1273 | 219.0933 | 418.5557 | 394.8346 | 29076.6618 | 0.76786 | 0.0131 | 5.0325 | 26.8146 | 134.9448 | -12 | 20 | 4 | 14 | 185.2442 | 571.7069 | 36.8357 | 3.0862 | 0.81267 | 110 | 50.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.032 | 50.1624
CID=-840430398 | -12 | 22.5 | 30.5868 | 4 | 16.5 | 3.3 | 1.7476 | 148.2918 | 9.1273 | 222.5675 | 420.2141 | 394.8346 | 30035.7022 | 0.82494 | 0.014577 | 4.6461 | 30.5868 | 142.1101 | -12 | 22.5 | 4 | 16.5 | 185.2442 | 617.2019 | 39.8843 | 3.3318 | 0.82874 | 110 | 56.0752 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.8538 | 56.7855
CID=-1862067311 | -12 | 25 | 34.4434 | 4 | 19 | 3.8 | 1.7476 | 148.2918 | 9.1273 | 226.0633 | 421.8454 | 394.8346 | 30937.7994 | 0.87636 | 0.016149 | 4.2942 | 34.4434 | 147.905 | -12 | 25 | 4 | 19 | 185.2442 | 665.3809 | 42.9775 | 3.5919 | 0.84269 | 110 | 62.1006 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9272 | 62.9919
CID=846613068 | -12 | 27.5 | 37.883 | 4 | 21.5 | 4.3 | 1.7476 | 148.2918 | 9.1273 | 229.5813 | 423.4496 | 394.8346 | 31713.6291 | 0.90945 | 0.017653 | 3.9672 | 37.883 | 150.29 | -12 | 27.5 | 4 | 21.5 | 185.2442 | 716.3449 | 46.1565 | 3.867 | 0.85332 | 110 | 67.4513 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.6206 | 65.6702
CID=-1660554213 | -12 | 30 | 40.7165 | 4 | 24 | 4.8 | 1.7476 | 148.2918 | 9.1273 | 233.1226 | 425.027 | 394.8346 | 32390.6453 | 0.92763 | 0.019017 | 3.6842 | 40.7165 | 150.0085 | -12 | 30 | 4 | 24 | 185.2442 | 770.1963 | 49.2091 | 4.1577 | 0.86096 | 109.8789 | 71.8523 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2108 | 32.3085 | 65.9405
CID=-1761310762 | -12 | 32.5 | 43.9099 | 4 | 26.5 | 5.3 | 1.7476 | 148.2918 | 9.1273 | 236.688 | 426.5779 | 394.8346 | 33082.3349 | 0.95349 | 0.020574 | 3.4341 | 43.9099 | 150.7904 | -12 | 32.5 | 4 | 26.5 | 185.2442 | 827.0396 | 52.1966 | 4.4646 | 0.86854 | 109.6885 | 76.8119 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 36.6126 | 65.8016
CID=1512019621 | -12 | 35 | 48.2119 | 4 | 29 | 5.8 | 1.7476 | 148.2918 | 9.1273 | 240.2788 | 428.1024 | 394.8346 | 33866.1468 | 0.99566 | 0.022609 | 3.1918 | 48.2119 | 153.8849 | -12 | 35 | 4 | 29 | 185.2442 | 886.981 | 55.3851 | 4.7882 | 0.87723 | 109.2461 | 83.5019 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.4028 | 65.639
CID=-74267296 | -12 | 37.5 | 52.5181 | 4 | 31.5 | 6.3 | 1.7476 | 148.2918 | 9.1273 | 243.8959 | 429.6009 | 394.8346 | 34595.5067 | 1.0336 | 0.024748 | 2.9707 | 52.5181 | 156.0163 | -12 | 37.5 | 4 | 31.5 | 185.2442 | 950.1287 | 58.576 | 5.1291 | 0.88446 | 108.6331 | 90.2166 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 47.9875 | 66.1098
CID=1102086879 | -12 | 40 | 58.4262 | 4 | 34 | 6.8 | 1.7476 | 148.2918 | 9.1273 | 247.5407 | 431.0734 | 394.8346 | 35394.1603 | 1.1014 | 0.027608 | 2.7766 | 58.4262 | 162.2279 | -12 | 40 | 4 | 34 | 185.2442 | 1016.593 | 61.6573 | 5.4879 | 0.89243 | 108.6424 | 99.469 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.8685 | 66.0993
CID=1001330330 | -12 | 42.5 | 63.3441 | 4 | 36.5 | 7.3 | 1.7476 | 148.2918 | 9.1273 | 251.2145 | 432.5204 | 394.8346 | 36069.1876 | 1.1568 | 0.030234 | 2.6228 | 63.3441 | 166.1403 | -12 | 42.5 | 4 | 36.5 | 185.2442 | 1086.4865 | 64.2753 | 5.8652 | 0.89769 | 108.6189 | 107.2104 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1387 | 63.9602
CID=-739675002 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-840431551 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1862068464 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=846611915 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1660555366 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1761311915 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1512018468 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-74268449 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1102085726 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1001329177 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-739680251 | -12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-840436800 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1862073713 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=846606666 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1660560615 | -9 | 2.5 | 7.001 | 4 | -3.5 | 0 | 1.7455 | 148.4312 | 10.2212 | 195.3144 | 405.5712 | 396.6938 | 19526.3252 | 0.41725 | 0.0063672 | 12.0019 | 7.001 | 84.0249 | -9 | 2.5 | 4 | -3.5 | 208.6448 | 320.2635 | 13.7509 | 1.535 | 0.66838 | 87.8902 | 15.9143 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5.8776 | 10.3709
CID=-1761317164 | -9 | 5 | 8.4983 | 4 | -1 | 0 | 1.7455 | 148.4312 | 10.2212 | 198.6579 | 407.4201 | 396.6938 | 20139.9695 | 0.44895 | 0.0067641 | 10.4619 | 8.4983 | 88.9076 | -9 | 5 | 4 | -1 | 208.6448 | 349.6586 | 16.9693 | 1.6759 | 0.68407 | 110 | 18.8748 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9672 | 16.0914
CID=1512013219 | -9 | 7.5 | 10.563 | 4 | 1.5 | 0.3 | 1.7455 | 148.4312 | 10.2212 | 202.0183 | 409.2404 | 396.6938 | 21578.2692 | 0.50069 | 0.0073654 | 9.2277 | 10.563 | 97.472 | -9 | 7.5 | 4 | 1.5 | 208.6448 | 381.0767 | 20.2411 | 1.8264 | 0.70412 | 110 | 22.7929 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3549 | 20.1873
CID=-74273698 | -9 | 10 | 12.899 | 4 | 4 | 0.8 | 1.7455 | 148.4312 | 10.2212 | 205.396 | 411.0322 | 396.6938 | 22947.0676 | 0.55337 | 0.0081048 | 8.2068 | 12.899 | 105.8592 | -9 | 10 | 4 | 4 | 208.6448 | 414.6075 | 23.492 | 1.9871 | 0.72475 | 110 | 27.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9222 | 24.8293
CID=1102080477 | -9 | 12.5 | 15.2405 | 4 | 6.5 | 1.3 | 1.7455 | 148.4312 | 10.2212 | 208.7918 | 412.7959 | 396.6938 | 24162.9151 | 0.60134 | 0.0089006 | 7.4139 | 15.2405 | 112.9921 | -9 | 12.5 | 4 | 6.5 | 208.6448 | 450.3422 | 26.5048 | 2.1584 | 0.74345 | 110 | 31.1461 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.5321 | 29.3656
CID=1001323928 | -9 | 15 | 17.8364 | 4 | 9 | 1.8 | 1.7455 | 148.4312 | 10.2212 | 212.2062 | 414.5315 | 396.6938 | 25298.1534 | 0.65215 | 0.0098165 | 6.7454 | 17.8364 | 120.3144 | -9 | 15 | 4 | 9 | 208.6448 | 488.3739 | 29.4706 | 2.3407 | 0.7621 | 110 | 35.5592 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3102 | 34.4149
CID=-739672948 | -9 | 17.5 | 21.2466 | 4 | 11.5 | 2.3 | 1.7455 | 148.4312 | 10.2212 | 215.6398 | 416.2392 | 396.6938 | 26535.3497 | 0.71939 | 0.011025 | 6.1303 | 21.2466 | 130.2476 | -9 | 17.5 | 4 | 11.5 | 208.6448 | 528.7968 | 32.622 | 2.5344 | 0.78363 | 110 | 41.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7558 | 40.7191
CID=-840429497 | -9 | 20 | 24.5863 | 4 | 14 | 2.8 | 1.7455 | 148.4312 | 10.2212 | 219.0933 | 417.9194 | 396.6938 | 27622.2158 | 0.77618 | 0.012271 | 5.6068 | 24.5863 | 137.8503 | -9 | 20 | 4 | 14 | 208.6448 | 571.7069 | 35.6878 | 2.7401 | 0.80188 | 110 | 46.5846 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9978 | 47.3518
CID=-1862066410 | -9 | 22.5 | 27.9222 | 4 | 16.5 | 3.3 | 1.7455 | 148.4312 | 10.2212 | 222.5675 | 419.5721 | 396.6938 | 28581.4823 | 0.82689 | 0.013573 | 5.1566 | 27.9222 | 143.9831 | -9 | 22.5 | 4 | 16.5 | 208.6448 | 617.2019 | 38.6835 | 2.9581 | 0.81766 | 110 | 51.8838 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.6774 | 52.6566
CID=846613969 | -9 | 25 | 31.7645 | 4 | 19 | 3.8 | 1.7455 | 148.4312 | 10.2212 | 226.0633 | 421.1976 | 396.6938 | 29517.5729 | 0.88731 | 0.0151 | 4.7664 | 31.7645 | 151.4022 | -9 | 25 | 4 | 19 | 208.6448 | 665.3809 | 41.6269 | 3.1891 | 0.83325 | 110 | 57.9194 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5308 | 59.4656
CID=-1660553312 | -9 | 27.5 | 35.9234 | 4 | 21.5 | 4.3 | 1.7455 | 148.4312 | 10.2212 | 229.5813 | 422.7961 | 396.6938 | 30432.2369 | 0.94623 | 0.016803 | 4.4018 | 35.9234 | 158.1273 | -9 | 27.5 | 4 | 21.5 | 208.6448 | 716.3449 | 44.6852 | 3.4333 | 0.84745 | 110 | 64.4047 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.7566 | 66.4236
CID=-1761309861 | -9 | 30 | 40.2152 | 4 | 24 | 4.8 | 1.7455 | 148.4312 | 10.2212 | 233.1226 | 424.3678 | 396.6938 | 31283.2108 | 1.0031 | 0.01863 | 4.08 | 40.2152 | 164.0793 | -9 | 30 | 4 | 24 | 208.6448 | 770.1963 | 47.6976 | 3.6914 | 0.85968 | 110 | 71.0739 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1758 | 73.3333
CID=1512020522 | -9 | 32.5 | 43.4972 | 4 | 26.5 | 5.3 | 1.7455 | 148.4312 | 10.2212 | 236.688 | 425.913 | 396.6938 | 31971.5302 | 1.026 | 0.020191 | 3.7742 | 43.4972 | 164.167 | -9 | 32.5 | 4 | 26.5 | 208.6448 | 827.0396 | 50.8342 | 3.9639 | 0.86762 | 110 | 76.1708 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.425 | 73.7137
CID=-74266395 | -9 | 35 | 46.4276 | 4 | 29 | 5.8 | 1.7455 | 148.4312 | 10.2212 | 240.2788 | 427.4319 | 396.6938 | 32606.863 | 1.0418 | 0.021702 | 3.5099 | 46.4276 | 162.954 | -9 | 35 | 4 | 29 | 208.6448 | 886.981 | 53.8427 | 4.2512 | 0.87382 | 109.0068 | 80.7254 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1147 | 37.4523 | 73.3536
CID=1102087780 | -9 | 37.5 | 50.5323 | 4 | 31.5 | 6.3 | 1.7455 | 148.4312 | 10.2212 | 243.8959 | 428.9247 | 396.6938 | 33333.4771 | 1.0825 | 0.023719 | 3.2733 | 50.5323 | 165.409 | -9 | 37.5 | 4 | 31.5 | 208.6448 | 950.1287 | 56.8243 | 4.5538 | 0.88129 | 109.3515 | 87.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 42.9142 | 73.3866
CID=1001331231 | -9 | 40 | 55.2702 | 4 | 34 | 6.8 | 1.7455 | 148.4312 | 10.2212 | 247.5407 | 430.3916 | 396.6938 | 34084.082 | 1.1281 | 0.026078 | 3.0442 | 55.2702 | 168.2545 | -9 | 40 | 4 | 34 | 208.6448 | 1016.593 | 59.9807 | 4.8724 | 0.88843 | 109.1431 | 94.5204 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.0108 | 74.0486
CID=-739669749 | -9 | 42.5 | 59.9742 | 4 | 36.5 | 7.3 | 1.7455 | 148.4312 | 10.2212 | 251.2145 | 431.833 | 396.6938 | 34779.1093 | 1.1684 | 0.028549 | 2.8341 | 59.9742 | 169.9749 | -9 | 42.5 | 4 | 36.5 | 208.6448 | 1086.4865 | 63.1442 | 5.2074 | 0.89421 | 108.6152 | 101.9018 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.1264 | 74.5178
CID=-840426298 | -9 | 45 | 66.9935 | 4 | 39 | 7.8 | 1.7455 | 148.4312 | 10.2212 | 254.9187 | 433.2489 | 396.6938 | 35552.8119 | 1.0155 | 0.031284 | 2.2149 | 65.0043 | 143.9788 | -9 | 45 | 4 | 39 | 208.6448 | 1159.9242 | 74.7802 | 5.5593 | 0.89922 | 98.353 | 109.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.4822 | 74.5276
CID=-1862063211 | -9 | 47.5 | 71.5236 | 4 | 41.5 | 8.3 | 1.7455 | 148.4312 | 10.2212 | 258.655 | 434.6398 | 396.6938 | 36119.6991 | 1.3082 | 0.034478 | 2.5514 | 70.7774 | 180.5813 | -9 | 47.5 | 4 | 41.5 | 208.6448 | 1237.0237 | 67.9309 | 5.9289 | 0.90379 | 109.5196 | 118.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.7723 | 70.7774
CID=846617168 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1660550113 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1761306662 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1512023721 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-74263196 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1102090979 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1001334430 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-739670902 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-840427451 | -9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1862064364 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=846616015 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1660551266 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1761307815 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1512022568 | -6 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-74264349 | -6 | 7.5 | 8.9548 | 4 | 1.5 | 0.3 | 1.7436 | 148.523 | 11.416 | 202.0183 | 408.6791 | 398.5385 | 19801.1672 | 0.49666 | 0.0069168 | 10.8996 | 8.9548 | 97.6037 | -6 | 7.5 | 4 | 1.5 | 234.2779 | 381.0767 | 19.1051 | 1.6266 | 0.68866 | 108.7941 | 19.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9997 | 6.453 | 16.4601
CID=1102089826 | -6 | 10 | 10.9567 | 4 | 4 | 0.8 | 1.7436 | 148.523 | 11.416 | 205.396 | 410.4654 | 398.5385 | 21142.0766 | 0.54291 | 0.0075228 | 9.5703 | 10.9567 | 104.8586 | -6 | 10 | 4 | 4 | 234.2779 | 414.6075 | 22.3029 | 1.7697 | 0.70774 | 109.9392 | 23.5213 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0608 | 7.6696 | 20.8178
CID=1001333277 | -6 | 12.5 | 13.3301 | 4 | 6.5 | 1.3 | 1.7436 | 148.523 | 11.416 | 208.7918 | 412.2236 | 398.5385 | 22479.9413 | 0.59964 | 0.0082878 | 8.5356 | 13.3301 | 113.7805 | -6 | 12.5 | 4 | 6.5 | 234.2779 | 450.3422 | 25.384 | 1.9223 | 0.72833 | 110 | 27.8072 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2176 | 25.6674
CID=-739676151 | -6 | 15 | 15.8192 | 4 | 9 | 1.8 | 1.7436 | 148.523 | 11.416 | 212.2062 | 413.9537 | 398.5385 | 23690.5383 | 0.64938 | 0.0091401 | 7.649 | 15.8192 | 121.0012 | -6 | 15 | 4 | 9 | 234.2779 | 488.3739 | 28.4902 | 2.0846 | 0.74779 | 110 | 32.1411 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7286 | 31.091
CID=-840432700 | -6 | 17.5 | 18.5218 | 4 | 11.5 | 2.3 | 1.7436 | 148.523 | 11.416 | 215.6398 | 415.6561 | 398.5385 | 24821.0517 | 0.70272 | 0.010104 | 6.9392 | 18.5218 | 128.5264 | -6 | 17.5 | 4 | 11.5 | 234.2779 | 528.7968 | 31.4515 | 2.2571 | 0.76668 | 110 | 36.7048 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.814 | 35.6449
CID=-1862069613 | -6 | 20 | 21.9132 | 4 | 14 | 2.8 | 1.7436 | 148.523 | 11.416 | 219.0933 | 417.3308 | 398.5385 | 26003.5015 | 0.77066 | 0.011327 | 6.3109 | 21.9132 | 138.2911 | -6 | 20 | 4 | 14 | 234.2779 | 571.7069 | 34.4979 | 2.4403 | 0.78749 | 110 | 42.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1569 | 42.1821
CID=846610766 | -6 | 22.5 | 25.4334 | 4 | 16.5 | 3.3 | 1.7436 | 148.523 | 11.416 | 222.5675 | 418.9782 | 398.5385 | 27095.0726 | 0.83286 | 0.012649 | 5.7625 | 25.4334 | 146.5598 | -6 | 22.5 | 4 | 16.5 | 234.2779 | 617.2019 | 37.5406 | 2.6345 | 0.8061 | 110 | 47.9369 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.5255 | 49.1571
CID=-1660556515 | -6 | 25 | 29.4527 | 4 | 19 | 3.8 | 1.7436 | 148.523 | 11.416 | 226.0633 | 420.5983 | 398.5385 | 28150.9026 | 0.90304 | 0.014195 | 5.2882 | 29.4527 | 155.7524 | -6 | 25 | 4 | 19 | 234.2779 | 665.3809 | 40.5565 | 2.8401 | 0.82418 | 110 | 54.2949 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3432 | 56.7809
CID=-1761313064 | -6 | 27.5 | 33.0158 | 4 | 21.5 | 4.3 | 1.7436 | 148.523 | 11.416 | 229.5813 | 422.1916 | 398.5385 | 29027.8384 | 0.95383 | 0.015661 | 4.8812 | 33.0158 | 161.1573 | -6 | 27.5 | 4 | 21.5 | 234.2779 | 716.3449 | 43.469 | 3.0577 | 0.83779 | 110 | 59.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3062 | 62.1448
CID=1512017319 | -6 | 30 | 37.347 | 4 | 24 | 4.8 | 1.7436 | 148.523 | 11.416 | 233.1226 | 423.758 | 398.5385 | 29923.7972 | 1.0189 | 0.017455 | 4.5129 | 37.347 | 168.5422 | -6 | 30 | 4 | 24 | 234.2779 | 770.1963 | 46.4307 | 3.2875 | 0.85176 | 110 | 66.6183 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4924 | 69.9107
CID=-74269598 | -6 | 32.5 | 42.0085 | 4 | 26.5 | 5.3 | 1.7436 | 148.523 | 11.416 | 236.688 | 425.298 | 398.5385 | 30804.4709 | 1.0825 | 0.019447 | 4.1707 | 42.0085 | 175.2026 | -6 | 32.5 | 4 | 26.5 | 234.2779 | 827.0396 | 49.4874 | 3.5302 | 0.86415 | 110 | 73.8586 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2611 | 77.2504
CID=1102084577 | -6 | 35 | 46.3235 | 4 | 29 | 5.8 | 1.7436 | 148.523 | 11.416 | 240.2788 | 426.8116 | 398.5385 | 31565.8743 | 1.1309 | 0.021412 | 3.8636 | 46.3235 | 178.9757 | -6 | 35 | 4 | 29 | 234.2779 | 886.981 | 52.5296 | 3.786 | 0.87361 | 110 | 80.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.2819 | 82.4485
CID=1001328028 | -6 | 37.5 | 50.0707 | 4 | 31.5 | 6.3 | 1.7436 | 148.523 | 11.416 | 243.8959 | 428.2991 | 398.5385 | 32244.6231 | 1.1621 | 0.023269 | 3.5891 | 50.0707 | 179.7089 | -6 | 37.5 | 4 | 31.5 | 234.2779 | 950.1287 | 55.5323 | 4.0556 | 0.88052 | 110 | 86.3978 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.1102 | 82.9524
CID=-739685248 | -6 | 40 | 53.2564 | 4 | 34 | 6.8 | 1.7436 | 148.523 | 11.416 | 247.5407 | 429.7609 | 398.5385 | 32845.747 | 1.1795 | 0.025012 | 3.3442 | 53.2564 | 178.0982 | -6 | 40 | 4 | 34 | 234.2779 | 1016.593 | 58.4756 | 4.3393 | 0.88557 | 109.5564 | 91.3702 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2045 | 43.5036 | 82.5148
CID=-840441797 | -6 | 42.5 | 57.7468 | 4 | 36.5 | 7.3 | 1.7436 | 148.523 | 11.416 | 251.2145 | 431.197 | 398.5385 | 33549.923 | 1.2213 | 0.027344 | 3.1158 | 57.7469 | 179.9282 | -6 | 42.5 | 4 | 36.5 | 234.2779 | 1086.4865 | 61.4916 | 4.6376 | 0.89162 | 109.6141 | 98.4025 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 49.8837 | 81.3364
CID=-1862078710 | -6 | 45 | 62.8366 | 4 | 39 | 7.8 | 1.7436 | 148.523 | 11.416 | 254.9187 | 432.6077 | 398.5385 | 34260.2255 | 1.2692 | 0.030036 | 2.9008 | 62.8366 | 182.2766 | -6 | 45 | 4 | 39 | 234.2779 | 1159.9242 | 64.5919 | 4.9511 | 0.8972 | 109.0422 | 106.4097 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 56.269 | 82.5395
CID=846601669 | -6 | 47.5 | 68.1326 | 4 | 41.5 | 8.3 | 1.7436 | 148.523 | 11.416 | 258.655 | 433.9933 | 398.5385 | 34934.2965 | 1.3158 | 0.032962 | 2.7015 | 68.1326 | 184.0572 | -6 | 47.5 | 4 | 41.5 | 234.2779 | 1237.0237 | 67.7236 | 5.2802 | 0.90184 | 108.5356 | 114.784 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1967 | 82.9402
CID=-1660565612 | -6 | 50 | 75.8977 | 4 | 44 | 8.8 | 1.7436 | 148.523 | 11.416 | 262.425 | 435.3541 | 398.5385 | 35722.2242 | 1.1082 | 0.036298 | 2.0381 | 74.0091 | 150.8396 | -6 | 50 | 4 | 44 | 234.2779 | 1317.9055 | 81.0313 | 5.6254 | 0.90589 | 95.8314 | 124.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.7545 | 82.3271
CID=-1761322161 | -6 | 52.5 | 81.0335 | 4 | 46.5 | 9.3 | 1.7436 | 148.523 | 11.416 | 266.2308 | 436.6902 | 398.5385 | 36189.9086 | 1.461 | 0.039595 | 2.437 | 79.3179 | 193.2958 | -6 | 52.5 | 4 | 46.5 | 234.2779 | 1402.6932 | 72.3832 | 5.9873 | 0.90877 | 109.5619 | 132.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 81.6054 | 79.3179
CID=1512008222 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-74278695 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1102075480 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1001318931 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-739682049 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-840438598 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1862075511 | -6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=846604868 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1660562413 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1761318962 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1512011421 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-74275496 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1102078679 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1001322130 | -3 | 10 | 9.6872 | 4 | 4 | 0.8 | 1.7418 | 148.5658 | 12.7186 | 205.396 | 409.9411 | 400.3675 | 19636.5194 | 0.56138 | 0.0071418 | 11.2987 | 9.6872 | 109.4529 | -3 | 10 | 4 | 4 | 262.283 | 414.6075 | 21.3893 | 1.5808 | 0.69583 | 108.7559 | 21.152 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4727 | 7.2395 | 17.0303
CID=342052131 | -3 | 12.5 | 11.2108 | 4 | 6.5 | 1.3 | 1.7418 | 148.5658 | 12.7186 | 208.7918 | 411.6941 | 400.3675 | 20658.2542 | 0.58322 | 0.0076494 | 9.9664 | 11.2108 | 111.7304 | -3 | 12.5 | 4 | 6.5 | 262.283 | 450.3422 | 24.2977 | 1.717 | 0.71005 | 109.7983 | 23.9885 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5043 | 7.8059 | 21.4254
CID=-961909784 | -3 | 15 | 13.7975 | 4 | 9 | 1.8 | 1.7418 | 148.5658 | 12.7186 | 212.2062 | 413.4192 | 400.3675 | 22004.5754 | 0.64493 | 0.0084863 | 8.7951 | 13.7975 | 121.3506 | -3 | 15 | 4 | 9 | 262.283 | 488.3739 | 27.5034 | 1.862 | 0.73215 | 110 | 28.6324 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5793 | 26.4523
CID=-780341331 | -3 | 17.5 | 16.5621 | 4 | 11.5 | 2.3 | 1.7418 | 148.5658 | 12.7186 | 215.6398 | 415.1165 | 400.3675 | 23265.0676 | 0.70643 | 0.0094337 | 7.8793 | 16.5621 | 130.4977 | -3 | 17.5 | 4 | 11.5 | 262.283 | 528.7968 | 30.5527 | 2.0161 | 0.7532 | 110 | 33.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.3834 | 32.0983
CID=-2084303246 | -3 | 20 | 19.0553 | 4 | 14 | 2.8 | 1.7418 | 148.5658 | 12.7186 | 219.0933 | 416.7863 | 400.3675 | 24315.4249 | 0.75072 | 0.010354 | 7.1416 | 19.0553 | 136.0859 | -3 | 20 | 4 | 14 | 262.283 | 571.7069 | 33.4416 | 2.1797 | 0.77016 | 110 | 37.5916 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.1276 | 36.8384
CID=-578828233 | -3 | 22.5 | 22.4036 | 4 | 16.5 | 3.3 | 1.7418 | 148.5658 | 12.7186 | 222.5675 | 418.4287 | 400.3675 | 25442.2888 | 0.81955 | 0.011583 | 6.5041 | 22.4036 | 145.716 | -3 | 22.5 | 4 | 16.5 | 262.283 | 617.2019 | 36.3754 | 2.3532 | 0.79025 | 110 | 43.0732 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3536 | 43.5534
CID=-1882790148 | -3 | 25 | 26.4845 | 4 | 19 | 3.8 | 1.7418 | 148.5658 | 12.7186 | 226.0633 | 420.0439 | 400.3675 | 26614.7984 | 0.89918 | 0.013103 | 5.9178 | 26.4845 | 156.7307 | -3 | 25 | 4 | 19 | 262.283 | 665.3809 | 39.4613 | 2.5369 | 0.81113 | 110 | 49.6083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2962 | 51.0495
CID=-1701221695 | -3 | 27.5 | 30.4608 | 4 | 21.5 | 4.3 | 1.7418 | 148.5658 | 12.7186 | 229.5813 | 421.6322 | 400.3675 | 27647.1901 | 0.96726 | 0.014662 | 5.4232 | 30.4608 | 165.1955 | -3 | 27.5 | 4 | 21.5 | 262.283 | 716.3449 | 42.4456 | 2.7312 | 0.82824 | 110 | 55.8777 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.9887 | 58.877
CID=1289783686 | -3 | 30 | 34.4086 | 4 | 24 | 4.8 | 1.7418 | 148.5658 | 12.7186 | 233.1226 | 423.1938 | 400.3675 | 28556.0331 | 1.028 | 0.016285 | 4.9966 | 34.4086 | 171.9266 | -3 | 30 | 4 | 24 | 262.283 | 770.1963 | 45.3646 | 2.9365 | 0.84257 | 110 | 62.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0589 | 65.4577
CID=-2111154437 | -3 | 32.5 | 38.7345 | 4 | 26.5 | 5.3 | 1.7418 | 148.5658 | 12.7186 | 236.688 | 424.7289 | 400.3675 | 29422.3737 | 1.0946 | 0.018113 | 4.6255 | 38.7345 | 179.1677 | -3 | 32.5 | 4 | 26.5 | 262.283 | 827.0396 | 48.228 | 3.1532 | 0.85571 | 110 | 68.7742 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.3282 | 72.9534
CID=879850944 | -3 | 35 | 43.7455 | 4 | 29 | 5.8 | 1.7418 | 148.5658 | 12.7186 | 240.2788 | 426.2376 | 400.3675 | 30308.4625 | 1.1684 | 0.020267 | 4.2758 | 43.7455 | 187.0475 | -3 | 35 | 4 | 29 | 262.283 | 886.981 | 51.2202 | 3.3818 | 0.86817 | 110 | 76.5566 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.2318 | 81.2868
CID=342055330 | -3 | 37.5 | 48.8797 | 4 | 31.5 | 6.3 | 1.7418 | 148.5658 | 12.7186 | 243.8959 | 427.7203 | 400.3675 | 31137.5105 | 1.2389 | 0.022571 | 3.9658 | 48.8797 | 193.8456 | -3 | 37.5 | 4 | 31.5 | 262.283 | 950.1287 | 54.1731 | 3.6225 | 0.87844 | 110 | 84.5418 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.4207 | 89.2568
CID=-961906585 | -3 | 40 | 52.9179 | 4 | 34 | 6.8 | 1.7418 | 148.5658 | 12.7186 | 247.5407 | 429.1772 | 400.3675 | 31805.6118 | 1.2702 | 0.024589 | 3.6684 | 52.9179 | 194.1224 | -3 | 40 | 4 | 34 | 262.283 | 1016.593 | 57.2675 | 3.8759 | 0.88507 | 110 | 90.8412 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.004 | 91.6597
CID=-780338132 | -3 | 42.5 | 56.6089 | 4 | 36.5 | 7.3 | 1.7418 | 148.5658 | 12.7186 | 251.2145 | 430.6085 | 400.3675 | 32428.699 | 1.2952 | 0.026581 | 3.4125 | 56.6089 | 193.1797 | -3 | 42.5 | 4 | 36.5 | 262.283 | 1086.4865 | 60.2235 | 4.1424 | 0.89019 | 109.9074 | 96.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9257 | 44.8066 | 92.0158
CID=-2084300047 | -3 | 45 | 60.48 | 4 | 39 | 7.8 | 1.7418 | 148.5658 | 12.7186 | 254.9187 | 432.0144 | 400.3675 | 33040.3197 | 1.3238 | 0.02875 | 3.1837 | 60.48 | 192.5519 | -3 | 45 | 4 | 39 | 262.283 | 1159.9242 | 63.1271 | 4.4224 | 0.89476 | 109.7526 | 102.6973 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8832 | 50.0122 | 91.8833
CID=-578825034 | -3 | 47.5 | 65.7238 | 4 | 41.5 | 8.3 | 1.7418 | 148.5658 | 12.7186 | 258.655 | 433.3951 | 400.3675 | 33743.1311 | 1.3745 | 0.031583 | 2.9637 | 65.7238 | 194.7847 | -3 | 47.5 | 4 | 41.5 | 262.283 | 1237.0237 | 66.1723 | 4.7164 | 0.89986 | 109.5581 | 110.9697 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 57.2677 | 91.0918
CID=-1882786949 | -3 | 50 | 71.2323 | 4 | 44 | 8.8 | 1.7418 | 148.5658 | 12.7186 | 262.425 | 434.7511 | 400.3675 | 34417.8064 | 1.4257 | 0.034687 | 2.7609 | 71.2323 | 196.6671 | -3 | 50 | 4 | 44 | 262.283 | 1317.9055 | 69.2295 | 5.0247 | 0.90411 | 108.6866 | 119.7053 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.1843 | 92.3763
CID=-1701218496 | -3 | 52.5 | 77.3151 | 4 | 46.5 | 9.3 | 1.7418 | 148.5658 | 12.7186 | 266.2308 | 436.0824 | 400.3675 | 35081.7838 | 1.4823 | 0.038216 | 2.5716 | 77.3151 | 198.8266 | -3 | 52.5 | 4 | 46.5 | 262.283 | 1402.6932 | 72.3289 | 5.348 | 0.90776 | 108.5539 | 129.4038 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72.1709 | 92.7477
CID=1289786885 | -3 | 55 | 85.8503 | 4 | 49 | 9.8 | 1.7418 | 148.5658 | 12.7186 | 270.0745 | 437.3893 | 400.3675 | 35839.1471 | 1.2333 | 0.042163 | 1.9162 | 83.8581 | 160.6883 | -3 | 55 | 4 | 49 | 262.283 | 1491.5141 | 86.0361 | 5.6867 | 0.91076 | 95.4659 | 139.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.791 | 92.0281
CID=-2111151238 | -3 | 57.5 | 91.2842 | 4 | 51.5 | 10.3 | 1.7418 | 148.5658 | 12.7186 | 273.9586 | 438.6721 | 400.3675 | 36239.4688 | 1.6267 | 0.045541 | 2.3224 | 88.544 | 205.6311 | -3 | 57.5 | 4 | 51.5 | 262.283 | 1584.4992 | 76.8958 | 6.0412 | 0.91245 | 109.5992 | 147.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.1977 | 88.544
CID=879854143 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=342054177 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-961907738 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-780339285 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2084301200 | -3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-578826187 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1882788102 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1701219649 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1289785732 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2111152391 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=879852990 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=342048928 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-961912987 | 0 | 12.5 | 9.6212 | 4 | 6.5 | 1.3 | 1.7401 | 148.5582 | 14.1363 | 208.7918 | 411.2041 | 402.1796 | 19543.1395 | 0.59135 | 0.0071845 | 11.8862 | 9.6212 | 114.3593 | 0 | 12.5 | 4 | 6.5 | 292.8032 | 450.3422 | 23.3083 | 1.538 | 0.69519 | 92.7288 | 21.027 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7.6527 | 15.5267
CID=-780344534 | 0 | 15 | 11.3774 | 4 | 9 | 1.8 | 1.7401 | 148.5582 | 14.1363 | 212.2062 | 412.9246 | 402.1796 | 20147.0181 | 0.62187 | 0.0077573 | 10.3835 | 11.3774 | 118.1379 | 0 | 15 | 4 | 9 | 292.8032 | 488.3739 | 26.3111 | 1.6679 | 0.71155 | 109.9611 | 24.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0627 | 7.8476 | 21.9668
CID=-2084306449 | 0 | 17.5 | 14.0277 | 4 | 11.5 | 2.3 | 1.7401 | 148.5582 | 14.1363 | 215.6398 | 414.6172 | 402.1796 | 21488.9026 | 0.68912 | 0.0086243 | 9.1639 | 14.0277 | 128.5489 | 0 | 17.5 | 4 | 11.5 | 292.8032 | 528.7968 | 29.415 | 1.806 | 0.734 | 110 | 29.0367 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6303 | 27.2198
CID=-578831436 | 0 | 20 | 16.9039 | 4 | 14 | 2.8 | 1.7401 | 148.5582 | 14.1363 | 219.0933 | 416.2824 | 402.1796 | 22736.0864 | 0.75199 | 0.0096181 | 8.1448 | 16.9039 | 137.6791 | 0 | 20 | 4 | 14 | 292.8032 | 571.7069 | 32.5375 | 1.9525 | 0.75564 | 110 | 33.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4976 | 33.1226
CID=-1882793351 | 0 | 22.5 | 20.1945 | 4 | 16.5 | 3.3 | 1.7401 | 148.5582 | 14.1363 | 222.5675 | 417.9202 | 402.1796 | 23960.4451 | 0.82479 | 0.010794 | 7.3358 | 20.1945 | 148.1431 | 0 | 22.5 | 4 | 16.5 | 292.8032 | 617.2019 | 35.5413 | 2.1079 | 0.77732 | 110 | 39.4718 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.7099 | 39.6483
CID=-1701224898 | 0 | 25 | 23.284 | 4 | 19 | 3.8 | 1.7401 | 148.5582 | 14.1363 | 226.0633 | 419.5308 | 402.1796 | 24988.9076 | 0.88273 | 0.011967 | 6.6768 | 23.284 | 155.4629 | 0 | 25 | 4 | 19 | 292.8032 | 665.3809 | 38.4058 | 2.2725 | 0.79507 | 110 | 44.4945 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0491 | 44.9885
CID=1289780483 | 0 | 27.5 | 27.2299 | 4 | 21.5 | 4.3 | 1.7401 | 148.5582 | 14.1363 | 229.5813 | 421.1145 | 402.1796 | 26091.7016 | 0.95969 | 0.013471 | 6.0831 | 27.2299 | 165.6411 | 0 | 27.5 | 4 | 21.5 | 292.8032 | 716.3449 | 41.3814 | 2.4465 | 0.81457 | 110 | 50.7895 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.7183 | 52.7648
CID=-2111157640 | 0 | 30 | 31.4571 | 4 | 24 | 4.8 | 1.7401 | 148.5582 | 14.1363 | 233.1226 | 422.6716 | 402.1796 | 27134.3921 | 1.0353 | 0.01514 | 5.5638 | 31.457 | 175.0194 | 0 | 30 | 4 | 24 | 292.8032 | 770.1963 | 44.3609 | 2.6304 | 0.83209 | 110 | 57.4384 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.6284 | 60.943
CID=879847741 | 0 | 32.5 | 36.1632 | 4 | 26.5 | 5.3 | 1.7401 | 148.5582 | 14.1363 | 236.688 | 424.2021 | 402.1796 | 28131.0228 | 1.1169 | 0.017048 | 5.1112 | 36.1632 | 184.839 | 0 | 32.5 | 4 | 26.5 | 292.8032 | 827.0396 | 47.3219 | 2.8246 | 0.8482 | 110 | 64.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9262 | 69.8742
CID=342056231 | 0 | 35 | 40.1614 | 4 | 29 | 5.8 | 1.7401 | 148.5582 | 14.1363 | 240.2788 | 425.7063 | 402.1796 | 28944.3571 | 1.1715 | 0.018804 | 4.7225 | 40.1614 | 189.6608 | 0 | 35 | 4 | 29 | 292.8032 | 886.981 | 50.1842 | 3.0293 | 0.85954 | 110 | 70.9904 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2143 | 76.0029
CID=-961905684 | 0 | 37.5 | 45.2821 | 4 | 31.5 | 6.3 | 1.7401 | 148.5582 | 14.1363 | 243.8959 | 427.1845 | 402.1796 | 29802.1961 | 1.2509 | 0.021041 | 4.3724 | 45.2821 | 197.9933 | 0 | 37.5 | 4 | 31.5 | 292.8032 | 950.1287 | 53.0755 | 3.2449 | 0.87149 | 110 | 78.9444 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0433 | 84.9985
CID=-780337231 | 0 | 40 | 50.8001 | 4 | 34 | 6.8 | 1.7401 | 148.5582 | 14.1363 | 247.5407 | 428.6369 | 402.1796 | 30648.0917 | 1.3283 | 0.023534 | 4.0435 | 50.8001 | 205.4122 | 0 | 40 | 4 | 34 | 292.8032 | 1016.593 | 56.0751 | 3.4719 | 0.88173 | 110 | 87.5352 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5584 | 93.5253
CID=-2084299146 | 0 | 42.5 | 55.9478 | 4 | 36.5 | 7.3 | 1.7401 | 148.5582 | 14.1363 | 251.2145 | 430.0637 | 402.1796 | 31385.5502 | 1.3926 | 0.026016 | 3.7576 | 55.9479 | 210.2319 | 0 | 42.5 | 4 | 36.5 | 292.8032 | 1086.4865 | 58.9741 | 3.7106 | 0.88933 | 110 | 95.5817 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6283 | 101.9065
CID=-578824133 | 0 | 45 | 60.0493 | 4 | 39 | 7.8 | 1.7401 | 148.5582 | 14.1363 | 254.9187 | 431.4651 | 402.1796 | 32007.1649 | 1.4207 | 0.028232 | 3.4839 | 60.0493 | 209.2065 | 0 | 45 | 4 | 39 | 292.8032 | 1159.9242 | 61.996 | 3.9614 | 0.89429 | 110 | 102.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.0942 | 101.9148
CID=-1882786048 | 0 | 47.5 | 63.5993 | 4 | 41.5 | 8.3 | 1.7401 | 148.5582 | 14.1363 | 258.655 | 432.8414 | 402.1796 | 32576.338 | 1.4372 | 0.030354 | 3.2433 | 63.5993 | 206.2745 | 0 | 47.5 | 4 | 41.5 | 292.8032 | 1237.0237 | 64.9248 | 4.2248 | 0.89793 | 109.2317 | 107.6131 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4308 | 51.0502 | 101.2467
CID=-1701217595 | 0 | 50 | 68.6525 | 4 | 44 | 8.8 | 1.7401 | 148.5582 | 14.1363 | 262.425 | 434.1928 | 402.1796 | 33225.1904 | 1.4874 | 0.033201 | 3.0278 | 68.6525 | 207.8688 | 0 | 50 | 4 | 44 | 292.8032 | 1317.9055 | 67.8092 | 4.501 | 0.90224 | 109.5375 | 115.6084 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3598 | 57.491 | 102.1367
CID=1289787786 | 0 | 52.5 | 74.3877 | 4 | 46.5 | 9.3 | 1.7401 | 148.5582 | 14.1363 | 266.2308 | 435.5196 | 402.1796 | 33902.8814 | 1.5411 | 0.036498 | 2.8165 | 74.3877 | 209.5158 | 0 | 52.5 | 4 | 46.5 | 292.8032 | 1402.6932 | 70.8656 | 4.7906 | 0.90612 | 109.2962 | 124.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65.2952 | 101.6651
CID=-2111150337 | 0 | 55 | 80.0931 | 4 | 49 | 9.8 | 1.7401 | 148.5582 | 14.1363 | 270.0745 | 436.822 | 402.1796 | 34534.296 | 1.5903 | 0.039985 | 2.623 | 80.0931 | 210.0873 | 0 | 55 | 4 | 49 | 292.8032 | 1491.5141 | 73.908 | 5.0939 | 0.90914 | 108.6285 | 133.8504 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72.7779 | 102.0387
CID=879855044 | 0 | 57.5 | 87.1933 | 4 | 51.5 | 10.3 | 1.7401 | 148.5582 | 14.1363 | 273.9586 | 438.1003 | 402.1796 | 35196.0612 | 1.6618 | 0.044306 | 2.4437 | 87.1933 | 213.0766 | 0 | 57.5 | 4 | 51.5 | 292.8032 | 1584.4992 | 76.9668 | 5.4115 | 0.912 | 108.5559 | 145.2596 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82.0777 | 102.54
CID=342059430 | 0 | 60 | 95.8531 | 4 | 54 | 10.8 | 1.7401 | 148.5582 | 14.1363 | 277.8855 | 439.3549 | 402.1796 | 35914.8119 | 1.3827 | 0.048861 | 1.8249 | 94.1757 | 171.8647 | 0 | 60 | 4 | 54 | 292.8032 | 1681.7842 | 90.2399 | 5.7437 | 0.91407 | 95.3496 | 156.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.1756 | 100.8854
CID=-961902485 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-780334032 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2084295947 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-578820934 | 0 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1882782849 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1701214396 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1289790985 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2111147138 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=879858243 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=342058277 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-961903638 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-780335185 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2084297100 | 3 | 15 | 9.1102 | 4 | 9 | 1.8 | 1.7385 | 148.4988 | 15.6766 | 212.2062 | 412.4664 | 403.9734 | 19534.8417 | 0.59697 | 0.0071242 | 12.566 | 9.1102 | 114.4784 | 3 | 15 | 4 | 9 | 325.9849 | 488.3739 | 25.1347 | 1.4981 | 0.6902 | 72.5696 | 20.0543 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.4251 | 11.1654
CID=-578822087 | 3 | 17.5 | 12.0707 | 4 | 11.5 | 2.3 | 1.7385 | 148.4988 | 15.6766 | 215.6398 | 414.1547 | 403.9734 | 19863.3913 | 0.68883 | 0.0080088 | 10.7474 | 12.0707 | 129.7291 | 3 | 17.5 | 4 | 11.5 | 325.9849 | 528.7968 | 28.5322 | 1.6222 | 0.71767 | 109.7411 | 25.5543 | 0 | 0 | 0 | 0 | 0 | 0 | 5.222 | 8.626 | 22.4048
CID=-1882784002 | 3 | 20 | 14.5449 | 4 | 14 | 2.8 | 1.7385 | 148.4988 | 15.6766 | 219.0933 | 415.8156 | 403.9734 | 21076.1863 | 0.74334 | 0.008848 | 9.4486 | 14.5449 | 137.4288 | 3 | 20 | 4 | 14 | 325.9849 | 571.7069 | 31.5823 | 1.7538 | 0.73809 | 110 | 29.9404 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0707 | 27.9674
CID=-1701215549 | 3 | 22.5 | 17.6134 | 4 | 16.5 | 3.3 | 1.7385 | 148.4988 | 15.6766 | 222.5675 | 417.4491 | 403.9734 | 22332.3072 | 0.81608 | 0.0099171 | 8.4051 | 17.6134 | 148.0422 | 3 | 22.5 | 4 | 16.5 | 325.9849 | 617.2019 | 34.616 | 1.8933 | 0.76058 | 110 | 35.1849 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1238 | 34.0823
CID=1289789832 | 3 | 25 | 20.7823 | 4 | 19 | 3.8 | 1.7385 | 148.4988 | 15.6766 | 226.0633 | 419.0555 | 403.9734 | 23477.6744 | 0.88286 | 0.011077 | 7.5579 | 20.7823 | 157.0702 | 3 | 25 | 4 | 19 | 325.9849 | 665.3809 | 37.5685 | 2.0411 | 0.78088 | 110 | 40.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0916 | 40.8543
CID=-2111148291 | 3 | 27.5 | 23.7402 | 4 | 21.5 | 4.3 | 1.7385 | 148.4988 | 15.6766 | 229.5813 | 420.635 | 403.9734 | 24460.4142 | 0.93377 | 0.012229 | 6.8594 | 23.7402 | 162.8427 | 3 | 27.5 | 4 | 21.5 | 325.9849 | 716.3449 | 40.4289 | 2.1975 | 0.7975 | 110 | 45.2283 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.1927 | 46.3828
CID=879857090 | 3 | 30 | 27.9548 | 4 | 24 | 4.8 | 1.7385 | 148.4988 | 15.6766 | 233.1226 | 422.1878 | 403.9734 | 25568.7843 | 1.0229 | 0.013844 | 6.2514 | 27.9548 | 174.7562 | 3 | 30 | 4 | 24 | 325.9849 | 770.1963 | 43.3443 | 2.3627 | 0.8178 | 110 | 51.9352 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.1571 | 54.3477
CID=342053028 | 3 | 32.5 | 32.6055 | 4 | 26.5 | 5.3 | 1.7385 | 148.4988 | 15.6766 | 236.688 | 423.7141 | 403.9734 | 26650.569 | 1.1111 | 0.015681 | 5.7006 | 32.6055 | 185.8719 | 3 | 32.5 | 4 | 26.5 | 325.9849 | 827.0396 | 46.349 | 2.537 | 0.83633 | 110 | 59.2339 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.4325 | 63.1245
CID=-961908887 | 3 | 35 | 37.2743 | 4 | 29 | 5.8 | 1.7385 | 148.4988 | 15.6766 | 240.2788 | 425.2142 | 403.9734 | 27630.9356 | 1.1917 | 0.017613 | 5.2334 | 37.2743 | 195.0707 | 3 | 35 | 4 | 29 | 325.9849 | 886.981 | 49.2709 | 2.7209 | 0.85155 | 110 | 66.5054 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6165 | 72.2476
CID=-780340434 | 3 | 37.5 | 41.8983 | 4 | 31.5 | 6.3 | 1.7385 | 148.4988 | 15.6766 | 243.8959 | 426.6882 | 403.9734 | 28493.3611 | 1.264 | 0.019624 | 4.8291 | 41.8983 | 202.3324 | 3 | 37.5 | 4 | 31.5 | 325.9849 | 950.1287 | 52.1317 | 2.9146 | 0.86389 | 110 | 73.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.0856 | 80.3364
CID=-2084302349 | 3 | 40 | 46.8183 | 4 | 34 | 6.8 | 1.7385 | 148.4988 | 15.6766 | 247.5407 | 428.1364 | 403.9734 | 29308.1857 | 1.339 | 0.021839 | 4.474 | 46.8183 | 209.4655 | 3 | 40 | 4 | 34 | 325.9849 | 1016.593 | 54.9521 | 3.1185 | 0.87459 | 110 | 81.3331 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.953 | 88.4142
CID=-578827336 | 3 | 42.5 | 52.7997 | 4 | 36.5 | 7.3 | 1.7385 | 148.4988 | 15.6766 | 251.2145 | 429.559 | 403.9734 | 30165.3189 | 1.4309 | 0.024556 | 4.1398 | 52.7997 | 218.5809 | 3 | 42.5 | 4 | 36.5 | 325.9849 | 1086.4865 | 57.8859 | 3.3329 | 0.88489 | 110 | 90.6565 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.6354 | 98.2926
CID=-1882789251 | 3 | 45 | 58.2841 | 4 | 39 | 7.8 | 1.7385 | 148.4988 | 15.6766 | 254.9187 | 430.9562 | 403.9734 | 30920.7681 | 1.4992 | 0.027228 | 3.8341 | 58.2842 | 223.4678 | 3 | 45 | 4 | 39 | 325.9849 | 1159.9242 | 60.8466 | 3.5582 | 0.89226 | 110 | 99.246 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9298 | 107.3472
CID=-1701220798 | 3 | 47.5 | 63.5782 | 4 | 41.5 | 8.3 | 1.7385 | 148.4988 | 15.6766 | 258.655 | 432.3283 | 403.9734 | 31602.6678 | 1.5549 | 0.029971 | 3.5539 | 63.5782 | 225.9536 | 3 | 47.5 | 4 | 41.5 | 325.9849 | 1237.0237 | 63.8369 | 3.7947 | 0.89791 | 110 | 107.5798 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.1667 | 112.8128
CID=1289784583 | 3 | 50 | 68.2334 | 4 | 44 | 8.8 | 1.7385 | 148.4988 | 15.6766 | 262.425 | 433.6755 | 403.9734 | 32216.1148 | 1.5933 | 0.032614 | 3.3052 | 68.2334 | 225.5239 | 3 | 50 | 4 | 44 | 325.9849 | 1317.9055 | 66.7629 | 4.0428 | 0.90192 | 110 | 114.9438 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1496 | 113.4849
CID=-2111153540 | 3 | 52.5 | 71.9453 | 4 | 46.5 | 9.3 | 1.7385 | 148.4988 | 15.6766 | 266.2308 | 434.9982 | 403.9734 | 32746.1857 | 1.609 | 0.035028 | 3.0806 | 71.9453 | 221.6321 | 3 | 52.5 | 4 | 46.5 | 325.9849 | 1402.6932 | 69.6481 | 4.3029 | 0.90459 | 109.2084 | 120.8393 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5914 | 58.3888 | 112.6148
CID=879851841 | 3 | 55 | 77.4961 | 4 | 49 | 9.8 | 1.7385 | 148.4988 | 15.6766 | 270.0745 | 436.2964 | 403.9734 | 33382.9087 | 1.6629 | 0.03836 | 2.8732 | 77.4961 | 222.6617 | 3 | 55 | 4 | 49 | 325.9849 | 1491.5141 | 72.555 | 4.5754 | 0.90786 | 109.4017 | 129.6933 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 65.8924 | 112.3073
CID=342043931 | 3 | 57.5 | 83.7568 | 4 | 51.5 | 10.3 | 1.7385 | 148.4988 | 15.6766 | 273.9586 | 437.5705 | 403.9734 | 34033.1816 | 1.7217 | 0.04221 | 2.6726 | 83.7568 | 223.8497 | 3 | 57.5 | 4 | 51.5 | 325.9849 | 1584.4992 | 75.589 | 4.8607 | 0.91072 | 109.1029 | 139.7298 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.9935 | 113.0467
CID=-961917984 | 3 | 60 | 89.8879 | 4 | 54 | 10.8 | 1.7385 | 148.4988 | 15.6766 | 277.8855 | 438.8208 | 403.9734 | 34635.9373 | 1.7733 | 0.046256 | 2.4874 | 89.8879 | 223.5881 | 3 | 60 | 4 | 54 | 325.9849 | 1681.7842 | 78.6222 | 5.1591 | 0.91287 | 108.6305 | 149.605 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82.0539 | 113.39
CID=-780349531 | 3 | 62.5 | 98.0676 | 4 | 56.5 | 11.3 | 1.7385 | 148.4988 | 15.6766 | 281.8586 | 440.0476 | 403.9734 | 35293.2983 | 1.8609 | 0.051523 | 2.3172 | 98.0675 | 227.2466 | 3 | 62.5 | 4 | 56.5 | 325.9849 | 1783.5096 | 81.6402 | 5.4711 | 0.91499 | 108.5947 | 162.8419 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.802 | 113.8644
CID=-2084311446 | 3 | 65 | 106.7869 | 4 | 59 | 11.8 | 1.7385 | 148.4988 | 15.6766 | 285.881 | 441.2512 | 403.9734 | 35929.5571 | 1.9734 | 0.057427 | 2.1823 | 106.7869 | 233.0453 | 3 | 65 | 4 | 59 | 325.9849 | 1889.8218 | 84.2314 | 5.7973 | 0.91655 | 108.8241 | 177.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 105.0584 | 111.9723
CID=-578836433 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1882798348 | 3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1701229895 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1289775486 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2111162637 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=879842744 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=342047130 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-961914785 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-780346332 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2084308247 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-578833234 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1882795149 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1701226696 | 6 | 20 | 12.8709 | 4 | 14 | 2.8 | 1.7371 | 148.3861 | 17.3476 | 219.0933 | 415.3827 | 405.7474 | 19627.9235 | 0.76532 | 0.0082987 | 11.0986 | 12.8709 | 142.8492 | 6 | 20 | 4 | 14 | 361.9781 | 571.7069 | 30.8075 | 1.5794 | 0.72451 | 109.5115 | 26.991 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5782 | 9.5417 | 22.8585
CID=1289778685 | 6 | 22.5 | 14.7918 | 4 | 16.5 | 3.3 | 1.7371 | 148.3861 | 17.3476 | 222.5675 | 417.0123 | 405.7474 | 20592.2992 | 0.79241 | 0.0090009 | 9.8131 | 14.7918 | 145.1538 | 6 | 22.5 | 4 | 16.5 | 361.9781 | 617.2019 | 33.6273 | 1.7051 | 0.74001 | 109.716 | 30.3695 | 0 | 0 | 0 | 0 | 0 | 0 | 5.71 | 10.1644 | 28.6739
CID=-2111159438 | 6 | 25 | 18.0116 | 4 | 19 | 3.8 | 1.7371 | 148.3861 | 17.3476 | 226.0633 | 418.6147 | 405.7474 | 21836.3543 | 0.86895 | 0.010131 | 8.6687 | 18.0116 | 156.1366 | 6 | 25 | 4 | 19 | 361.9781 | 665.3809 | 36.7126 | 1.8382 | 0.76328 | 110 | 35.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3537 | 34.9853
CID=879845943 | 6 | 27.5 | 21.5606 | 4 | 21.5 | 4.3 | 1.7371 | 148.3861 | 17.3476 | 229.5813 | 420.1903 | 405.7474 | 23036.3291 | 0.94902 | 0.011428 | 7.7542 | 21.5606 | 167.1844 | 6 | 27.5 | 4 | 21.5 | 361.9781 | 716.3449 | 39.719 | 1.979 | 0.78546 | 110 | 41.7052 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.739 | 42.0253
CID=1796924734 | 6 | 30 | 25.1123 | 4 | 24 | 4.8 | 1.7371 | 148.3861 | 17.3476 | 233.1226 | 421.7392 | 405.7474 | 24113.0261 | 1.0227 | 0.012792 | 7.0301 | 25.1123 | 176.5423 | 6 | 30 | 4 | 24 | 361.9781 | 770.1963 | 42.5682 | 2.1277 | 0.80452 | 110 | 47.4249 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.1012 | 49.1455
CID=1696168185 | 6 | 32.5 | 28.7987 | 4 | 26.5 | 5.3 | 1.7371 | 148.3861 | 17.3476 | 236.688 | 423.2616 | 405.7474 | 25089.4408 | 1.0923 | 0.014267 | 6.4122 | 28.7987 | 184.6642 | 6 | 32.5 | 4 | 26.5 | 361.9781 | 827.0396 | 45.3895 | 2.2848 | 0.82145 | 110 | 53.2659 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7427 | 55.9665
CID=109881268 | 6 | 35 | 33.5182 | 4 | 29 | 5.8 | 1.7371 | 148.3861 | 17.3476 | 240.2788 | 424.7577 | 405.7474 | 26148.0919 | 1.185 | 0.01616 | 5.8499 | 33.5182 | 196.0797 | 6 | 35 | 4 | 29 | 361.9781 | 886.981 | 48.3257 | 2.4504 | 0.83955 | 110 | 60.6585 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.991 | 65.1
CID=-1476405649 | 6 | 37.5 | 38.4327 | 4 | 31.5 | 6.3 | 1.7371 | 148.3861 | 17.3476 | 243.8959 | 426.2278 | 405.7474 | 27130.7877 | 1.2727 | 0.018213 | 5.3595 | 38.4327 | 205.9814 | 6 | 37.5 | 4 | 31.5 | 361.9781 | 950.1287 | 51.2504 | 2.6248 | 0.85487 | 110 | 68.3055 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.3835 | 74.5803
CID=-1577162198 | 6 | 40 | 43.8827 | 4 | 34 | 6.8 | 1.7371 | 148.3861 | 17.3476 | 247.5407 | 427.6721 | 405.7474 | 28072.5457 | 1.3669 | 0.020557 | 4.9279 | 43.8827 | 216.2473 | 6 | 40 | 4 | 34 | 361.9781 | 1016.593 | 54.1724 | 2.8084 | 0.86848 | 110 | 76.7696 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2032 | 84.9212
CID=-1677918747 | 6 | 42.5 | 48.301 | 4 | 36.5 | 7.3 | 1.7371 | 148.3861 | 17.3476 | 251.2145 | 429.0909 | 405.7474 | 28824.3568 | 1.4246 | 0.022645 | 4.5579 | 48.301 | 220.1534 | 6 | 42.5 | 4 | 36.5 | 361.9781 | 1086.4865 | 56.9908 | 3.0015 | 0.87739 | 110 | 83.6406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7881 | 91.8398
CID=1030761632 | 6 | 45 | 54.408 | 4 | 39 | 7.8 | 1.7371 | 148.3861 | 17.3476 | 254.9187 | 430.4842 | 405.7474 | 29658.8007 | 1.5232 | 0.025468 | 4.2226 | 54.408 | 229.7427 | 6 | 45 | 4 | 39 | 361.9781 | 1159.9242 | 59.8467 | 3.2044 | 0.88723 | 110 | 93.171 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.4962 | 102.1436
CID=-555525285 | 6 | 47.5 | 60.4183 | 4 | 41.5 | 8.3 | 1.7371 | 148.3861 | 17.3476 | 258.655 | 431.8524 | 405.7474 | 30434.1931 | 1.6069 | 0.028405 | 3.912 | 60.4183 | 236.3572 | 6 | 47.5 | 4 | 41.5 | 361.9781 | 1237.0237 | 62.7566 | 3.4174 | 0.8947 | 110 | 102.6003 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.1636 | 112.1825
CID=-44835994 | 6 | 50 | 66.7816 | 4 | 44 | 8.8 | 1.7371 | 148.3861 | 17.3476 | 262.425 | 433.1958 | 405.7474 | 31176.8955 | 1.6937 | 0.031642 | 3.6349 | 66.7816 | 242.7447 | 6 | 50 | 4 | 44 | 361.9781 | 1317.9055 | 65.6316 | 3.6408 | 0.90075 | 110 | 112.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3056 | 122.2097
CID=-145592543 | 6 | 52.5 | 71.6884 | 4 | 46.5 | 9.3 | 1.7371 | 148.3861 | 17.3476 | 266.2308 | 434.5145 | 405.7474 | 31777.3117 | 1.7297 | 0.034479 | 3.3662 | 71.6884 | 241.3156 | 6 | 52.5 | 4 | 46.5 | 361.9781 | 1402.6932 | 68.6488 | 3.8751 | 0.90441 | 110 | 120.4306 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.1646 | 124.2598
CID=1796927933 | 6 | 55 | 76.3943 | 4 | 49 | 9.8 | 1.7371 | 148.3861 | 17.3476 | 270.0745 | 435.8088 | 405.7474 | 32352.8587 | 1.7638 | 0.037403 | 3.1324 | 76.3943 | 239.2944 | 6 | 55 | 4 | 49 | 361.9781 | 1491.5141 | 71.5523 | 4.1205 | 0.90727 | 109.9534 | 127.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4657 | 60.3101 | 124.6468
CID=1696171384 | 6 | 57.5 | 81.0133 | 4 | 51.5 | 10.3 | 1.7371 | 148.3861 | 17.3476 | 273.9586 | 437.0791 | 405.7474 | 32894.3427 | 1.7956 | 0.040473 | 2.9211 | 81.0133 | 236.6443 | 6 | 57.5 | 4 | 51.5 | 361.9781 | 1584.4992 | 74.4148 | 4.3773 | 0.90956 | 109.7217 | 135.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6487 | 66.4309 | 124.7604
CID=109884467 | 6 | 60 | 87.2959 | 4 | 54 | 10.8 | 1.7371 | 148.3861 | 17.3476 | 277.8855 | 438.3255 | 405.7474 | 33524.2679 | 1.8572 | 0.044475 | 2.7203 | 87.2959 | 237.4681 | 6 | 60 | 4 | 54 | 361.9781 | 1681.7842 | 77.357 | 4.6461 | 0.91203 | 109.6482 | 145.4249 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9737 | 75.0155 | 124.137
CID=-1476402450 | 6 | 62.5 | 93.85 | 4 | 56.5 | 11.3 | 1.7371 | 148.3861 | 17.3476 | 281.8586 | 439.5483 | 405.7474 | 34136.0237 | 1.9167 | 0.048873 | 2.5302 | 93.85 | 237.4579 | 6 | 62.5 | 4 | 56.5 | 361.9781 | 1783.5096 | 80.3601 | 4.9271 | 0.91399 | 109.1811 | 156.0085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.3904 | 125.2286
CID=-1577158999 | 6 | 65 | 100.4041 | 4 | 59 | 11.8 | 1.7371 | 148.3861 | 17.3476 | 285.881 | 440.748 | 405.7474 | 34711.1489 | 1.9704 | 0.053585 | 2.3523 | 100.4041 | 236.1806 | 6 | 65 | 4 | 59 | 361.9781 | 1889.8218 | 83.3892 | 5.2208 | 0.91547 | 108.6371 | 166.6345 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.0266 | 125.5368
CID=-1677915548 | 6 | 67.5 | 109.4321 | 4 | 61.5 | 12.3 | 1.7371 | 148.3861 | 17.3476 | 289.9569 | 441.9247 | 405.7474 | 35350.9145 | 2.0708 | 0.059852 | 2.1911 | 109.4321 | 239.7744 | 6 | 67.5 | 4 | 61.5 | 361.9781 | 2000.8736 | 86.3562 | 5.5276 | 0.91692 | 108.6055 | 181.3287 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 104.302 | 124.8224
CID=1030764831 | 6 | 69.99 | 118.4354 | 4 | 63.99 | 12.798 | 1.7371 | 148.3861 | 17.3476 | 294.074 | 443.0743 | 405.7474 | 35978.5349 | 1.7308 | 0.065687 | 1.6571 | 116.6407 | 193.2819 | 6 | 69.99 | 4 | 63.99 | 361.9781 | 2116.3519 | 98.2332 | 5.8466 | 0.91774 | 95.3496 | 193.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 116.6406 | 123.8195
CID=-555522086 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-44832795 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-145589344 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1796926780 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1696170231 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=109883314 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1476403603 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1577160152 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1677916701 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1030763678 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-555523239 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-44833948 | 9 | 22.5 | 13.0583 | 4 | 16.5 | 3.3 | 1.7357 | 148.2186 | 19.1581 | 222.5675 | 416.6065 | 407.5003 | 19498.5826 | 0.81759 | 0.0084279 | 11.5787 | 13.0583 | 151.199 | 9 | 22.5 | 4 | 16.5 | 400.9358 | 617.2019 | 32.8908 | 1.5394 | 0.72608 | 97.9377 | 27.3249 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9.8546 | 22.6697
CID=-145590497 | 9 | 25 | 14.9901 | 4 | 19 | 3.8 | 1.7357 | 148.2186 | 19.1581 | 226.0633 | 418.2053 | 407.5003 | 20102.7621 | 0.8418 | 0.0091449 | 10.189 | 14.9901 | 152.7345 | 9 | 25 | 4 | 19 | 400.9358 | 665.3809 | 35.7091 | 1.6596 | 0.74154 | 109.9336 | 30.7133 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1089 | 10.2198 | 29.301
CID=1796921531 | 9 | 27.5 | 18.3208 | 4 | 21.5 | 4.3 | 1.7357 | 148.2186 | 19.1581 | 229.5813 | 419.7772 | 407.5003 | 21359.1273 | 0.92789 | 0.010326 | 9.0111 | 18.3208 | 165.09 | 9 | 27.5 | 4 | 21.5 | 400.9358 | 716.3449 | 38.6966 | 1.7867 | 0.76535 | 110 | 36.3696 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4687 | 35.877
CID=1696164982 | 9 | 30 | 21.9976 | 4 | 24 | 4.8 | 1.7357 | 148.2186 | 19.1581 | 233.1226 | 421.3224 | 407.5003 | 22550.0888 | 1.0115 | 0.011682 | 8.018 | 21.9976 | 176.3761 | 9 | 30 | 4 | 24 | 400.9358 | 770.1963 | 41.7277 | 1.921 | 0.78797 | 110 | 42.4153 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.9305 | 43.1989
CID=109878065 | 9 | 32.5 | 25.7496 | 4 | 26.5 | 5.3 | 1.7357 | 148.2186 | 19.1581 | 236.688 | 422.8412 | 407.5003 | 23632.1885 | 1.0887 | 0.013134 | 7.222 | 25.7496 | 185.9641 | 9 | 32.5 | 4 | 26.5 | 400.9358 | 827.0396 | 44.6546 | 2.0628 | 0.80764 | 110 | 48.4406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2579 | 51.2247
CID=-1476408852 | 9 | 35 | 29.4338 | 4 | 29 | 5.8 | 1.7357 | 148.2186 | 19.1581 | 240.2788 | 424.3337 | 407.5003 | 24588.7722 | 1.1569 | 0.014634 | 6.5725 | 29.4338 | 193.455 | 9 | 35 | 4 | 29 | 400.9358 | 886.981 | 47.4744 | 2.2123 | 0.8241 | 110 | 54.2653 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0505 | 57.5838
CID=-1577165401 | 9 | 37.5 | 34.4894 | 4 | 31.5 | 6.3 | 1.7357 | 148.2186 | 19.1581 | 243.8959 | 425.8002 | 407.5003 | 25653.5119 | 1.2641 | 0.016675 | 5.9962 | 34.4894 | 206.8051 | 9 | 37.5 | 4 | 31.5 | 400.9358 | 950.1287 | 50.3656 | 2.3698 | 0.84284 | 110 | 62.1724 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6818 | 66.9124
CID=-1677921950 | 9 | 40 | 39.6659 | 4 | 34 | 6.8 | 1.7357 | 148.2186 | 19.1581 | 247.5407 | 427.2409 | 407.5003 | 26643.6446 | 1.3588 | 0.018859 | 5.4797 | 39.6659 | 217.3578 | 9 | 40 | 4 | 34 | 400.9358 | 1016.593 | 53.3052 | 2.5356 | 0.85824 | 110 | 70.2208 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2008 | 77.061
CID=1030758429 | 9 | 42.5 | 45.0848 | 4 | 36.5 | 7.3 | 1.7357 | 148.2186 | 19.1581 | 251.2145 | 428.656 | 407.5003 | 27574.8751 | 1.4533 | 0.021239 | 5.0377 | 45.0848 | 227.1252 | 9 | 42.5 | 4 | 36.5 | 400.9358 | 1086.4865 | 56.1829 | 2.7099 | 0.87107 | 110 | 78.6377 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9216 | 87.5743
CID=-555528488 | 9 | 45 | 50.4426 | 4 | 39 | 7.8 | 1.7357 | 148.2186 | 19.1581 | 254.9187 | 430.0457 | 407.5003 | 28393.6706 | 1.5386 | 0.02372 | 4.6541 | 50.4426 | 234.7652 | 9 | 45 | 4 | 39 | 400.9358 | 1159.9242 | 59.0033 | 2.893 | 0.88114 | 110 | 86.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.7915 | 97.396
CID=-44839197 | 9 | 47.5 | 56.099 | 4 | 41.5 | 8.3 | 1.7357 | 148.2186 | 19.1581 | 258.655 | 431.4103 | 407.5003 | 29172.4564 | 1.6246 | 0.026444 | 4.3105 | 56.099 | 241.8167 | 9 | 47.5 | 4 | 41.5 | 400.9358 | 1237.0237 | 61.8199 | 3.0853 | 0.88953 | 110 | 95.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.4856 | 105.939
CID=-145595746 | 9 | 50 | 62.5309 | 4 | 44 | 8.8 | 1.7357 | 148.2186 | 19.1581 | 262.425 | 432.7501 | 407.5003 | 29950.8828 | 1.7202 | 0.029616 | 3.9909 | 62.5309 | 249.5536 | 9 | 50 | 4 | 44 | 400.9358 | 1317.9055 | 64.709 | 3.2871 | 0.89689 | 110 | 105.9278 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3087 | 117.1977
CID=1796928834 | 9 | 52.5 | 68.9765 | 4 | 46.5 | 9.3 | 1.7357 | 148.2186 | 19.1581 | 266.2308 | 434.0651 | 407.5003 | 30687.3689 | 1.8041 | 0.032974 | 3.6949 | 68.9765 | 254.8593 | 9 | 52.5 | 4 | 46.5 | 400.9358 | 1402.6932 | 67.6508 | 3.4985 | 0.90249 | 110 | 116.1224 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.6486 | 126.9601
CID=1696172285 | 9 | 55 | 72.9421 | 4 | 49 | 9.8 | 1.7357 | 148.2186 | 19.1581 | 270.0745 | 435.3559 | 407.5003 | 31202.8881 | 1.8233 | 0.035515 | 3.4352 | 72.9421 | 250.5707 | 9 | 55 | 4 | 49 | 400.9358 | 1491.5141 | 70.4967 | 3.7201 | 0.90523 | 110 | 122.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.9361 | 126.9601
CID=109885368 | 9 | 57.5 | 77.9115 | 4 | 51.5 | 10.3 | 1.7357 | 148.2186 | 19.1581 | 273.9586 | 436.6225 | 407.5003 | 31785.0896 | 1.8583 | 0.038637 | 3.1851 | 77.9115 | 248.1582 | 9 | 57.5 | 4 | 51.5 | 400.9358 | 1584.4992 | 73.4731 | 3.952 | 0.90807 | 109.9739 | 130.3575 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6527 | 61.5619 | 126.9602
CID=-1476401549 | 9 | 60 | 82.3759 | 4 | 54 | 10.8 | 1.7357 | 148.2186 | 19.1581 | 277.8855 | 437.8652 | 407.5003 | 32333.9581 | 1.8826 | 0.041742 | 2.9623 | 82.3759 | 244.0189 | 9 | 60 | 4 | 54 | 400.9358 | 1681.7842 | 76.3838 | 4.1946 | 0.91016 | 108.8814 | 137.5117 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.5145 | 126.9601
CID=-1577158098 | 9 | 62.5 | 87.903 | 4 | 56.5 | 11.3 | 1.7357 | 148.2186 | 19.1581 | 281.8586 | 439.0844 | 407.5003 | 32898.375 | 1.9306 | 0.045532 | 2.7594 | 87.903 | 242.5635 | 9 | 62.5 | 4 | 56.5 | 400.9358 | 1783.5096 | 79.2699 | 4.4484 | 0.91224 | 109.2068 | 146.4033 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 74.8839 | 126.9602
CID=-1677914647 | 9 | 65 | 95.1488 | 4 | 59 | 11.8 | 1.7357 | 148.2186 | 19.1581 | 285.881 | 440.2804 | 407.5003 | 33523.875 | 2.0089 | 0.050385 | 2.5678 | 95.1488 | 244.325 | 9 | 65 | 4 | 59 | 400.9358 | 1889.8218 | 82.2121 | 4.7135 | 0.91432 | 109.3484 | 158.1111 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84.545 | 126.9602
CID=1030765732 | 9 | 67.5 | 101.8465 | 4 | 61.5 | 12.3 | 1.7357 | 148.2186 | 19.1581 | 289.9569 | 441.4534 | 407.5003 | 34100.5666 | 2.067 | 0.055333 | 2.3856 | 101.8465 | 242.9603 | 9 | 67.5 | 4 | 61.5 | 400.9358 | 2000.8736 | 85.2137 | 4.9905 | 0.91574 | 108.7071 | 168.9781 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 93.4753 | 126.9601
CID=-555521185 | 9 | 69.99 | 108.7322 | 4 | 63.99 | 12.798 | 1.7357 | 148.2186 | 19.1581 | 294.074 | 442.5993 | 407.5003 | 34652.6503 | 2.1231 | 0.060753 | 2.2148 | 108.7323 | 240.8203 | 9 | 69.99 | 4 | 63.99 | 400.9358 | 2116.3519 | 88.2335 | 5.2785 | 0.91683 | 108.3018 | 180.1876 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 102.6563 | 126.9602
CID=-44831894 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-145588443 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1796932033 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1696175484 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=109888567 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1476398350 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1577154899 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1677911448 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1030768931 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-555517986 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-44828695 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-145585244 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1796930880 | 12 | 25 | 12.2733 | 4 | 19 | 3.8 | 1.7345 | 147.9949 | 21.1172 | 226.0633 | 417.8241 | 409.2305 | 19468.6544 | 0.81968 | 0.0082905 | 12.233 | 12.2733 | 150.1393 | 12 | 25 | 4 | 19 | 443.0145 | 665.3809 | 34.7607 | 1.5019 | 0.71942 | 77.0505 | 25.9199 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.795 | 16.7083
CID=1696174331 | 12 | 27.5 | 15.7854 | 4 | 21.5 | 4.3 | 1.7345 | 147.9949 | 21.1172 | 229.5813 | 419.3925 | 409.2305 | 19805.6846 | 0.92361 | 0.0094701 | 10.5114 | 15.7853 | 165.9259 | 12 | 27.5 | 4 | 21.5 | 443.0145 | 716.3449 | 37.9589 | 1.617 | 0.74754 | 109.4634 | 32.0831 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4789 | 11.1128 | 29.8031
CID=109887414 | 12 | 30 | 18.9561 | 4 | 24 | 4.8 | 1.7345 | 147.9949 | 21.1172 | 233.1226 | 420.9344 | 409.2305 | 20960.0908 | 0.99591 | 0.010627 | 9.2523 | 18.9561 | 175.387 | 12 | 30 | 4 | 24 | 443.0145 | 770.1963 | 40.9398 | 1.7385 | 0.76952 | 110 | 37.427 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0293 | 36.7366
CID=-1476399503 | 12 | 32.5 | 22.8261 | 4 | 26.5 | 5.3 | 1.7345 | 147.9949 | 21.1172 | 236.688 | 422.4497 | 409.2305 | 22141.1595 | 1.0879 | 0.01207 | 8.2237 | 22.8261 | 187.7146 | 12 | 32.5 | 4 | 26.5 | 443.0145 | 827.0396 | 43.9337 | 1.8668 | 0.79259 | 110 | 43.7563 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.6766 | 44.2749
CID=-1577156052 | 12 | 35 | 26.7706 | 4 | 29 | 5.8 | 1.7345 | 147.9949 | 21.1172 | 240.2788 | 423.9389 | 409.2305 | 23220.8512 | 1.1735 | 0.013612 | 7.4062 | 26.7706 | 198.2687 | 12 | 35 | 4 | 29 | 443.0145 | 886.981 | 46.8136 | 2.0021 | 0.81247 | 110 | 50.062 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.1723 | 52.5653
CID=-1677912601 | 12 | 37.5 | 30.4431 | 4 | 31.5 | 6.3 | 1.7345 | 147.9949 | 21.1172 | 243.8959 | 425.402 | 409.2305 | 24153.6606 | 1.2397 | 0.01514 | 6.7328 | 30.4431 | 204.9671 | 12 | 37.5 | 4 | 31.5 | 443.0145 | 950.1287 | 49.6083 | 2.1447 | 0.82817 | 110 | 55.85 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8063 | 59.3536
CID=1030767778 | 12 | 40 | 35.191 | 4 | 34 | 6.8 | 1.7345 | 147.9949 | 21.1172 | 247.5407 | 426.8393 | 409.2305 | 25141.9355 | 1.338 | 0.017114 | 6.1478 | 35.191 | 216.3469 | 12 | 40 | 4 | 34 | 443.0145 | 1016.593 | 52.4258 | 2.2947 | 0.84513 | 110 | 63.265 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0173 | 68.7122
CID=-555519139 | 12 | 42.5 | 40.8318 | 4 | 36.5 | 7.3 | 1.7345 | 147.9949 | 21.1172 | 251.2145 | 428.251 | 409.2305 | 26166.2026 | 1.4504 | 0.019503 | 5.6129 | 40.8318 | 229.1856 | 12 | 42.5 | 4 | 36.5 | 443.0145 | 1086.4865 | 55.3449 | 2.4525 | 0.86126 | 110 | 72.0313 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0083 | 79.3022
CID=-44829848 | 12 | 45 | 46.4186 | 4 | 39 | 7.8 | 1.7345 | 147.9949 | 21.1172 | 254.9187 | 429.6374 | 409.2305 | 27085.91 | 1.5492 | 0.021994 | 5.1499 | 46.4186 | 239.0522 | 12 | 45 | 4 | 39 | 443.0145 | 1159.9242 | 58.2283 | 2.6183 | 0.8738 | 110 | 80.7114 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.8335 | 90.1739
CID=-145586397 | 12 | 47.5 | 52.6594 | 4 | 41.5 | 8.3 | 1.7345 | 147.9949 | 21.1172 | 258.655 | 430.9986 | 409.2305 | 27975.6964 | 1.6569 | 0.02486 | 4.7378 | 52.6594 | 249.4893 | 12 | 47.5 | 4 | 41.5 | 443.0145 | 1237.0237 | 61.1256 | 2.7923 | 0.88467 | 110 | 90.4374 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2059 | 102.0198
CID=1796925631 | 12 | 50 | 57.69 | 4 | 44 | 8.8 | 1.7345 | 147.9949 | 21.1172 | 262.425 | 432.335 | 409.2305 | 28687.2705 | 1.723 | 0.027419 | 4.3845 | 57.69 | 252.9404 | 12 | 50 | 4 | 44 | 443.0145 | 1317.9055 | 63.9234 | 2.9749 | 0.89155 | 110 | 98.3133 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.3372 | 109.7483
CID=1696169082 | 12 | 52.5 | 64.4953 | 4 | 46.5 | 9.3 | 1.7345 | 147.9949 | 21.1172 | 266.2308 | 433.6467 | 409.2305 | 29466.7873 | 1.8335 | 0.030817 | 4.0652 | 64.4953 | 262.1865 | 12 | 52.5 | 4 | 46.5 | 443.0145 | 1402.6932 | 66.7386 | 3.1662 | 0.89877 | 110 | 109.0279 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5194 | 121.423
CID=109882165 | 12 | 55 | 69.8509 | 4 | 49 | 9.8 | 1.7345 | 147.9949 | 21.1172 | 270.0745 | 434.934 | 409.2305 | 30100.2514 | 1.8927 | 0.033827 | 3.7706 | 69.8509 | 263.3778 | 12 | 55 | 4 | 49 | 443.0145 | 1491.5141 | 69.5806 | 3.3667 | 0.90313 | 110 | 117.5103 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8145 | 126.9602
CID=-1476404752 | 12 | 57.5 | 74.1751 | 4 | 51.5 | 10.3 | 1.7345 | 147.9949 | 21.1172 | 273.9586 | 436.1972 | 409.2305 | 30650.781 | 1.9154 | 0.036593 | 3.4931 | 74.1752 | 259.1014 | 12 | 57.5 | 4 | 51.5 | 443.0145 | 1584.4992 | 72.4959 | 3.5766 | 0.906 | 110 | 124.3909 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5802 | 126.9601
CID=-1577161301 | 12 | 60 | 78.9042 | 4 | 54 | 10.8 | 1.7345 | 147.9949 | 21.1172 | 277.8855 | 437.4365 | 409.2305 | 31206.345 | 1.9456 | 0.039708 | 3.2387 | 78.9042 | 255.5498 | 12 | 60 | 4 | 54 | 443.0145 | 1681.7842 | 75.4298 | 3.7962 | 0.90857 | 109.8734 | 131.9462 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2656 | 62.8856 | 126.9602
CID=-1677917850 | 12 | 62.5 | 84.3301 | 4 | 56.5 | 11.3 | 1.7345 | 147.9949 | 21.1172 | 281.8586 | 438.6523 | 409.2305 | 31791.7239 | 1.99 | 0.043338 | 3.0057 | 84.3301 | 253.4713 | 12 | 62.5 | 4 | 56.5 | 443.0145 | 1783.5096 | 78.3712 | 4.0258 | 0.91095 | 109.5236 | 140.6513 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70.1201 | 126.9601
CID=1030762529 | 12 | 65 | 88.8722 | 4 | 59 | 11.8 | 1.7345 | 147.9949 | 21.1172 | 285.881 | 439.8448 | 409.2305 | 32324.7648 | 2.0101 | 0.04682 | 2.79 | 88.8722 | 247.9494 | 12 | 65 | 4 | 59 | 443.0145 | 1889.8218 | 81.326 | 4.2658 | 0.91256 | 106.103 | 147.9661 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 76.1762 | 126.9602
CID=-555524388 | 12 | 67.5 | 95.2124 | 4 | 61.5 | 12.3 | 1.7345 | 147.9949 | 21.1172 | 289.9569 | 441.0144 | 409.2305 | 32889.9558 | 2.0737 | 0.051406 | 2.5978 | 95.2124 | 247.342 | 12 | 67.5 | 4 | 61.5 | 443.0145 | 2000.8736 | 84.2022 | 4.5165 | 0.91433 | 108.555 | 158.2141 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 84.6298 | 126.9602
CID=-44835097 | 12 | 69.99 | 102.7731 | 4 | 63.99 | 12.798 | 1.7345 | 147.9949 | 21.1172 | 294.074 | 442.1569 | 409.2305 | 33486.1752 | 2.1537 | 0.056932 | 2.4132 | 102.7731 | 248.0168 | 12 | 69.99 | 4 | 63.99 | 443.0145 | 2116.3519 | 87.1577 | 4.7772 | 0.91591 | 108.8735 | 170.4844 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.7107 | 126.9601
CID=-145591646 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1796916534 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1696159985 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=109873068 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1476413849 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1577170398 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1677926947 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1030753432 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-555533485 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-44844194 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-145600743 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1796919733 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1696163184 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=109876267 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1476410650 | 15 | 30 | 16.7698 | 4 | 24 | 4.8 | 1.7333 | 147.7132 | 23.2347 | 233.1226 | 420.5719 | 410.9364 | 19559.3007 | 1.0199 | 0.0098629 | 10.8146 | 16.7698 | 181.3589 | 15 | 30 | 4 | 24 | 488.3739 | 770.1963 | 40.2693 | 1.5771 | 0.75469 | 110 | 33.7611 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3198 | 30.1197
CID=-1577167199 | 15 | 32.5 | 19.1886 | 4 | 26.5 | 5.3 | 1.7333 | 147.7132 | 23.2347 | 236.688 | 422.0841 | 410.9364 | 20480.4794 | 1.0556 | 0.010813 | 9.5854 | 19.1886 | 183.9314 | 15 | 32.5 | 4 | 26.5 | 488.3739 | 827.0396 | 43.0416 | 1.6935 | 0.77102 | 109.6881 | 37.8125 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7798 | 13.0742 | 37.5319
CID=-1677923748 | 15 | 35 | 23.1047 | 4 | 29 | 5.8 | 1.7333 | 147.7132 | 23.2347 | 240.2788 | 423.5701 | 410.9364 | 21630.6513 | 1.149 | 0.012293 | 8.4867 | 23.1047 | 196.0824 | 15 | 35 | 4 | 29 | 488.3739 | 886.981 | 46.0343 | 1.8162 | 0.79411 | 110 | 44.2057 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.7101 | 45.2884
CID=1030756631 | 15 | 37.5 | 27.3222 | 4 | 31.5 | 6.3 | 1.7333 | 147.7132 | 23.2347 | 243.8959 | 425.03 | 410.9364 | 22734.7223 | 1.2441 | 0.01395 | 7.6059 | 27.3222 | 207.8099 | 15 | 37.5 | 4 | 31.5 | 488.3739 | 950.1287 | 48.956 | 1.9455 | 0.81499 | 110 | 50.9356 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.4587 | 53.9129
CID=-555530286 | 15 | 40 | 31.9319 | 4 | 34 | 6.8 | 1.7333 | 147.7132 | 23.2347 | 247.5407 | 426.4641 | 410.9364 | 23793.2957 | 1.3456 | 0.015826 | 6.8852 | 31.9319 | 219.8576 | 15 | 40 | 4 | 34 | 488.3739 | 1016.593 | 51.8091 | 2.0816 | 0.83387 | 110 | 58.1812 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4735 | 63.3068
CID=-44840995 | 15 | 42.5 | 36.2154 | 4 | 36.5 | 7.3 | 1.7333 | 147.7132 | 23.2347 | 251.2145 | 427.8727 | 410.9364 | 24687.8299 | 1.4252 | 0.017682 | 6.2856 | 36.2154 | 227.6368 | 15 | 42.5 | 4 | 36.5 | 488.3739 | 1086.4865 | 54.5809 | 2.2247 | 0.84836 | 110 | 64.8589 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7682 | 70.5569
CID=-145597544 | 15 | 45 | 42.0359 | 4 | 39 | 7.8 | 1.7333 | 147.7132 | 23.2347 | 254.9187 | 429.2559 | 410.9364 | 25690.5768 | 1.5463 | 0.020184 | 5.739 | 42.0359 | 241.2444 | 15 | 45 | 4 | 39 | 488.3739 | 1159.9242 | 57.4573 | 2.3751 | 0.86422 | 110 | 73.9011 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.93 | 81.3534
CID=-1416313383 | 15 | 47.5 | 47.7133 | 4 | 41.5 | 8.3 | 1.7333 | 147.7132 | 23.2347 | 258.655 | 430.614 | 410.9364 | 26595.2359 | 1.6464 | 0.022763 | 5.2547 | 47.7133 | 250.7169 | 15 | 47.5 | 4 | 41.5 | 488.3739 | 1237.0237 | 60.3487 | 2.5329 | 0.8763 | 110 | 82.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.6346 | 92.9494
CID=1574691998 | 15 | 50 | 53.9451 | 4 | 44 | 8.8 | 1.7333 | 147.7132 | 23.2347 | 262.425 | 431.9472 | 410.9364 | 27480.0961 | 1.7563 | 0.025691 | 4.8352 | 53.9451 | 260.8341 | 15 | 50 | 4 | 44 | 488.3739 | 1317.9055 | 63.2014 | 2.6986 | 0.88657 | 110 | 92.4469 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.943 | 104.9514
CID=1191610447 | 15 | 52.5 | 60.0817 | 4 | 46.5 | 9.3 | 1.7333 | 147.7132 | 23.2347 | 266.2308 | 433.2557 | 410.9364 | 28256.9517 | 1.856 | 0.028743 | 4.4702 | 60.0817 | 268.5777 | 15 | 52.5 | 4 | 46.5 | 488.3739 | 1402.6932 | 65.9989 | 2.8722 | 0.89433 | 110 | 102.0708 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2093 | 116.6989
CID=-112351468 | 15 | 55 | 66.5209 | 4 | 49 | 9.8 | 1.7333 | 147.7132 | 23.2347 | 270.0745 | 434.5399 | 410.9364 | 29000.6636 | 1.954 | 0.032091 | 4.1377 | 66.5209 | 275.2418 | 15 | 55 | 4 | 49 | 488.3739 | 1491.5141 | 68.8211 | 3.054 | 0.90054 | 110 | 112.231 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8297 | 125.5944
CID=-495433019 | 15 | 57.5 | 70.518 | 4 | 51.5 | 10.3 | 1.7333 | 147.7132 | 23.2347 | 273.9586 | 435.7999 | 410.9364 | 29516.1221 | 1.9776 | 0.034638 | 3.8413 | 70.518 | 270.8833 | 15 | 57.5 | 4 | 51.5 | 488.3739 | 1584.4992 | 71.597 | 3.2444 | 0.90361 | 110 | 118.57 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.704 | 126.9601
CID=-1799394934 | 15 | 60 | 75.3822 | 4 | 54 | 10.8 | 1.7333 | 147.7132 | 23.2347 | 277.8855 | 437.0361 | 410.9364 | 30108.2213 | 2.0116 | 0.037713 | 3.5505 | 75.3822 | 267.6449 | 15 | 60 | 4 | 54 | 488.3739 | 1681.7842 | 74.5411 | 3.4436 | 0.9067 | 110 | 126.3163 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.1896 | 126.9601
CID=2112490811 | 15 | 62.5 | 79.7119 | 4 | 56.5 | 11.3 | 1.7333 | 147.7132 | 23.2347 | 281.8586 | 438.2486 | 410.9364 | 30636.8151 | 2.0289 | 0.040757 | 3.2855 | 79.7118 | 261.8916 | 15 | 62.5 | 4 | 56.5 | 488.3739 | 1783.5096 | 77.491 | 3.6519 | 0.90896 | 109.3078 | 133.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 9.581 | 63.9624 | 126.9602
CID=808528896 | 15 | 65 | 85.1909 | 4 | 59 | 11.8 | 1.7333 | 147.7132 | 23.2347 | 285.881 | 439.4379 | 410.9364 | 31208.1259 | 2.0755 | 0.044528 | 3.0467 | 85.1909 | 259.5469 | 15 | 65 | 4 | 59 | 488.3739 | 1889.8218 | 80.4171 | 3.8696 | 0.91128 | 108.605 | 142.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.2677 | 126.9602
CID=1036893185 | 15 | 67.5 | 90.9672 | 4 | 61.5 | 12.3 | 1.7333 | 147.7132 | 23.2347 | 289.9569 | 440.6043 | 410.9364 | 31789.0651 | 2.1236 | 0.04871 | 2.8242 | 90.9672 | 256.9086 | 15 | 67.5 | 4 | 61.5 | 488.3739 | 2000.8736 | 83.3758 | 4.097 | 0.9132 | 108.605 | 151.3478 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 78.9695 | 126.9602
CID=-267068730 | 15 | 69.99 | 95.9846 | 4 | 63.99 | 12.798 | 1.7333 | 147.7132 | 23.2347 | 294.074 | 441.7436 | 410.9364 | 32317.7342 | 2.1467 | 0.052838 | 2.6137 | 95.9846 | 250.874 | 15 | 69.99 | 4 | 63.99 | 488.3739 | 2116.3519 | 86.3916 | 4.3335 | 0.91452 | 106.7651 | 159.4651 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 85.6595 | 126.9602
CID=-1416310184 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1574695197 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1191613646 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-112348269 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-495429820 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1799391735 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2112494010 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=808532095 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1036896384 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-267065531 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1416311337 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1574694044 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1191612493 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-112349422 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-495430973 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1799392888 | 18 | 32.5 | 17.7124 | 4 | 26.5 | 5.3 | 1.7322 | 147.3721 | 25.5211 | 236.688 | 421.7412 | 412.6163 | 19402.818 | 1.1218 | 0.010256 | 11.142 | 17.7124 | 197.352 | 18 | 32.5 | 4 | 26.5 | 537.1767 | 827.0396 | 42.565 | 1.5396 | 0.76125 | 106.0811 | 35.3512 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6387 | 12.839 | 32.3325
CID=2112492857 | 18 | 35 | 19.3923 | 4 | 29 | 5.8 | 1.7322 | 147.3721 | 25.5211 | 240.2788 | 423.2242 | 412.6163 | 20003.2582 | 1.1169 | 0.010997 | 9.9261 | 19.3923 | 192.4894 | 18 | 35 | 4 | 29 | 537.1767 | 886.981 | 45.1815 | 1.6512 | 0.77232 | 109.9794 | 38.1496 | 0 | 0 | 0 | 0 | 0 | 0 | 5.0355 | 13.112 | 38.233
CID=808530942 | 18 | 37.5 | 23.5425 | 4 | 31.5 | 6.3 | 1.7322 | 147.3721 | 25.5211 | 243.8959 | 424.6812 | 412.6163 | 21186.6751 | 1.2253 | 0.012576 | 8.7812 | 23.5425 | 206.7311 | 18 | 37.5 | 4 | 31.5 | 537.1767 | 950.1287 | 48.1285 | 1.7687 | 0.79645 | 109.7733 | 44.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2267 | 15.9579 | 46.2963
CID=1036895231 | 18 | 40 | 28.0789 | 4 | 34 | 6.8 | 1.7322 | 147.3721 | 25.5211 | 247.5407 | 426.1123 | 412.6163 | 22314.5408 | 1.3338 | 0.01437 | 7.8412 | 28.0789 | 220.1731 | 18 | 40 | 4 | 34 | 537.1767 | 1016.593 | 51.0608 | 1.8925 | 0.81835 | 110 | 52.1312 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0416 | 55.1907
CID=-267066684 | 18 | 42.5 | 32.6804 | 4 | 36.5 | 7.3 | 1.7322 | 147.3721 | 25.5211 | 251.2145 | 427.5179 | 412.6163 | 23328.6045 | 1.4299 | 0.016279 | 7.0621 | 32.6804 | 230.7938 | 18 | 42.5 | 4 | 36.5 | 537.1767 | 1086.4865 | 53.9583 | 2.0226 | 0.8366 | 110 | 59.3509 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9546 | 64.858
CID=-1416316586 | 18 | 45 | 36.8595 | 4 | 39 | 7.8 | 1.7322 | 147.3721 | 25.5211 | 254.9187 | 428.8982 | 412.6163 | 24195.6302 | 1.503 | 0.018137 | 6.4305 | 36.8595 | 237.0255 | 18 | 45 | 4 | 39 | 537.1767 | 1159.9242 | 56.7417 | 2.1593 | 0.85031 | 110 | 65.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0409 | 72.3151
CID=1574688795 | 18 | 47.5 | 42.5117 | 4 | 41.5 | 8.3 | 1.7322 | 147.3721 | 25.5211 | 258.655 | 430.2533 | 412.6163 | 25149.3434 | 1.6235 | 0.020626 | 5.8798 | 42.5117 | 249.9624 | 18 | 47.5 | 4 | 41.5 | 537.1767 | 1237.0237 | 59.5458 | 2.3028 | 0.86535 | 110 | 74.6401 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.9027 | 83.3388
CID=1191607244 | 18 | 50 | 49.1812 | 4 | 44 | 8.8 | 1.7322 | 147.3721 | 25.5211 | 262.425 | 431.5835 | 412.6163 | 26139.6218 | 1.759 | 0.023627 | 5.3717 | 49.1812 | 264.1851 | 18 | 50 | 4 | 44 | 537.1767 | 1317.9055 | 62.455 | 2.4534 | 0.87898 | 110 | 85.0116 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7506 | 95.4733
CID=-112354671 | 18 | 52.5 | 55.4678 | 4 | 46.5 | 9.3 | 1.7322 | 147.3721 | 25.5211 | 266.2308 | 432.8891 | 412.6163 | 27001.0668 | 1.8694 | 0.026647 | 4.9335 | 55.4678 | 273.6511 | 18 | 52.5 | 4 | 46.5 | 537.1767 | 1402.6932 | 65.3144 | 2.6112 | 0.88869 | 110 | 94.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.0197 | 107.8119
CID=-495436222 | 18 | 55 | 62.5311 | 4 | 49 | 9.8 | 1.7322 | 147.3721 | 25.5211 | 270.0745 | 434.1702 | 412.6163 | 27840.5175 | 1.9913 | 0.030143 | 4.5393 | 62.5311 | 283.8484 | 18 | 55 | 4 | 49 | 537.1767 | 1491.5141 | 68.2009 | 2.7766 | 0.89689 | 110 | 105.928 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9579 | 121.2507
CID=-1799398137 | 18 | 57.5 | 67.5028 | 4 | 51.5 | 10.3 | 1.7322 | 147.3721 | 25.5211 | 273.9586 | 435.4273 | 412.6163 | 28463.941 | 2.046 | 0.032999 | 4.2027 | 67.5028 | 283.6966 | 18 | 57.5 | 4 | 51.5 | 537.1767 | 1584.4992 | 70.9785 | 2.9497 | 0.90134 | 110 | 113.7859 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.6837 | 126.9601
CID=2112487608 | 18 | 60 | 71.5994 | 4 | 54 | 10.8 | 1.7322 | 147.3721 | 25.5211 | 277.8855 | 436.6604 | 412.6163 | 28981.5366 | 2.0738 | 0.035667 | 3.9023 | 71.5994 | 279.4051 | 18 | 60 | 4 | 54 | 537.1767 | 1681.7842 | 73.7245 | 3.1308 | 0.90435 | 110 | 120.2892 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1459 | 126.9601
CID=808525693 | 18 | 62.5 | 76.434 | 4 | 56.5 | 11.3 | 1.7322 | 147.3721 | 25.5211 | 281.8586 | 437.87 | 412.6163 | 29562.8128 | 2.1073 | 0.038826 | 3.6051 | 76.434 | 275.5491 | 18 | 62.5 | 4 | 56.5 | 537.1767 | 1783.5096 | 76.6459 | 3.3202 | 0.90729 | 109.9336 | 127.9958 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6638 | 59.592 | 126.9601
CID=1036889982 | 18 | 65 | 80.8331 | 4 | 59 | 11.8 | 1.7322 | 147.3721 | 25.5211 | 285.881 | 439.0563 | 412.6163 | 30096.6896 | 2.1257 | 0.042007 | 3.3328 | 80.8331 | 269.4025 | 18 | 65 | 4 | 59 | 537.1767 | 1889.8218 | 79.5844 | 3.5181 | 0.90948 | 108.5916 | 135.0364 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7237 | 65.4574 | 126.9601
CID=-267071933 | 18 | 67.5 | 85.8533 | 4 | 61.5 | 12.3 | 1.7322 | 147.3721 | 25.5211 | 289.9569 | 440.2196 | 412.6163 | 30643.4642 | 2.1567 | 0.045701 | 3.0813 | 85.8533 | 264.5383 | 18 | 67.5 | 4 | 61.5 | 537.1767 | 2000.8736 | 82.5546 | 3.7248 | 0.91152 | 107.4904 | 143.1016 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72.1509 | 126.9602
CID=-1416309283 | 18 | 69.99 | 91.6827 | 4 | 63.99 | 12.798 | 1.7322 | 147.3721 | 25.5211 | 294.074 | 441.3558 | 412.6163 | 31200.4095 | 2.2092 | 0.05005 | 2.8565 | 91.6828 | 261.8881 | 18 | 69.99 | 4 | 63.99 | 537.1767 | 2116.3519 | 85.469 | 3.9398 | 0.9134 | 106.2101 | 152.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 79.9236 | 126.9602
CID=1574696098 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1191614547 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-112347368 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-495428919 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1799390834 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2112494911 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=808532996 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1036897285 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-267064630 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1416306084 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1574699297 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1191617746 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-112344169 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-495425720 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1799387635 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2112498110 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=808536195 | 21 | 35 | 16.3013 | 4 | 29 | 5.8 | 1.7312 | 146.9698 | 27.9878 | 240.2788 | 422.8982 | 414.2684 | 19333.929 | 1.1078 | 0.0099359 | 11.8237 | 16.3013 | 192.7419 | 21 | 35 | 4 | 29 | 589.5892 | 886.981 | 44.4012 | 1.5044 | 0.75132 | 82.4711 | 32.9649 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.5732 | 24.4855
CID=1036900484 | 21 | 37.5 | 20.2315 | 4 | 31.5 | 6.3 | 1.7312 | 146.9698 | 27.9878 | 243.8959 | 424.3523 | 414.2684 | 19683.0409 | 1.2132 | 0.011391 | 10.2162 | 20.2315 | 206.6889 | 21 | 37.5 | 4 | 31.5 | 589.5892 | 950.1287 | 47.4583 | 1.6115 | 0.77755 | 109.185 | 39.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7666 | 14.0444 | 38.7928
CID=-267061431 | 21 | 40 | 24.2504 | 4 | 34 | 6.8 | 1.7312 | 146.9698 | 27.9878 | 247.5407 | 425.7807 | 414.2684 | 20791.8496 | 1.3096 | 0.01296 | 9.0039 | 24.2504 | 218.3466 | 21 | 40 | 4 | 34 | 589.5892 | 1016.593 | 50.401 | 1.7242 | 0.80016 | 110 | 46.0467 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5838 | 47.2501
CID=-1416307237 | 21 | 42.5 | 28.9571 | 4 | 36.5 | 7.3 | 1.7312 | 146.9698 | 27.9878 | 251.2145 | 427.1835 | 414.2684 | 21893.2767 | 1.4225 | 0.014846 | 8.0101 | 28.9571 | 231.9493 | 21 | 42.5 | 4 | 36.5 | 589.5892 | 1086.4865 | 53.3504 | 1.8428 | 0.82212 | 110 | 53.5153 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8198 | 56.3689
CID=1574698144 | 21 | 45 | 33.8321 | 4 | 39 | 7.8 | 1.7312 | 146.9698 | 27.9878 | 254.9187 | 428.5609 | 414.2684 | 22918.1586 | 1.531 | 0.01689 | 7.2108 | 33.8321 | 243.9583 | 21 | 45 | 4 | 39 | 589.5892 | 1159.9242 | 56.2203 | 1.9673 | 0.84063 | 110 | 61.148 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9995 | 66.3301
CID=1191616593 | 21 | 47.5 | 38.8055 | 4 | 41.5 | 8.3 | 1.7312 | 146.9698 | 27.9878 | 258.655 | 429.9132 | 414.2684 | 23864.9027 | 1.6358 | 0.019077 | 6.5596 | 38.8055 | 254.5497 | 21 | 47.5 | 4 | 41.5 | 589.5892 | 1237.0237 | 58.9992 | 2.0981 | 0.85591 | 110 | 68.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2319 | 76.5263
CID=-112345322 | 21 | 50 | 43.7944 | 4 | 44 | 8.8 | 1.7312 | 146.9698 | 27.9878 | 262.425 | 431.2407 | 414.2684 | 24714.1475 | 1.7299 | 0.021386 | 5.9977 | 43.7944 | 262.6664 | 21 | 50 | 4 | 44 | 589.5892 | 1317.9055 | 61.7626 | 2.2353 | 0.86828 | 110 | 76.6325 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9299 | 85.388
CID=-495426873 | 21 | 52.5 | 50.3217 | 4 | 46.5 | 9.3 | 1.7312 | 146.9698 | 27.9878 | 266.2308 | 432.5434 | 414.2684 | 25650.8547 | 1.8633 | 0.024402 | 5.4815 | 50.3217 | 275.8404 | 21 | 52.5 | 4 | 46.5 | 589.5892 | 1402.6932 | 64.625 | 2.3791 | 0.88094 | 110 | 86.7891 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.5049 | 97.772
CID=-1799388788 | 21 | 55 | 56.7853 | 4 | 49 | 9.8 | 1.7312 | 146.9698 | 27.9878 | 270.0745 | 433.8218 | 414.2684 | 26505.6385 | 1.9781 | 0.027564 | 5.0231 | 56.7853 | 285.2358 | 21 | 55 | 4 | 49 | 589.5892 | 1491.5141 | 67.5016 | 2.5298 | 0.89042 | 110 | 96.8942 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.7568 | 110.8709
CID=2112496957 | 21 | 57.5 | 63.9044 | 4 | 51.5 | 10.3 | 1.7312 | 146.9698 | 27.9878 | 273.9586 | 435.076 | 414.2684 | 27347.4955 | 2.1057 | 0.031171 | 4.6233 | 63.9044 | 295.4492 | 21 | 57.5 | 4 | 51.5 | 589.5892 | 1584.4992 | 70.3475 | 2.6875 | 0.89822 | 110 | 108.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.7196 | 124.4588
CID=808535042 | 21 | 60 | 68.0198 | 4 | 54 | 10.8 | 1.7312 | 146.9698 | 27.9878 | 277.8855 | 436.3063 | 414.2684 | 27893.63 | 2.133 | 0.033762 | 4.2768 | 68.0198 | 290.9083 | 21 | 60 | 4 | 54 | 589.5892 | 1681.7842 | 73.1137 | 2.8525 | 0.90175 | 110 | 114.6052 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.373 | 126.9601
CID=1036899331 | 21 | 62.5 | 72.788 | 4 | 56.5 | 11.3 | 1.7312 | 146.9698 | 27.9878 | 281.8586 | 437.513 | 414.2684 | 28478.415 | 2.1707 | 0.036796 | 3.9487 | 72.788 | 287.4167 | 21 | 62.5 | 4 | 56.5 | 589.5892 | 1783.5096 | 75.9761 | 3.025 | 0.90513 | 110 | 122.1807 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7306 | 126.9601
CID=-267062584 | 21 | 65 | 77.099 | 4 | 59 | 11.8 | 1.7312 | 146.9698 | 27.9878 | 285.881 | 438.6964 | 414.2684 | 29011.9347 | 2.1973 | 0.039833 | 3.6591 | 77.099 | 282.1099 | 21 | 65 | 4 | 59 | 589.5892 | 1889.8218 | 78.7875 | 3.2053 | 0.90765 | 109.5951 | 129.0585 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0247 | 60.4786 | 126.9602
CID=-1416312486 | 21 | 67.5 | 82.0149 | 4 | 61.5 | 12.3 | 1.7312 | 146.9698 | 27.9878 | 289.9569 | 439.8569 | 414.2684 | 29571.5146 | 2.226 | 0.04336 | 3.3739 | 82.0149 | 276.7126 | 21 | 67.5 | 4 | 61.5 | 589.5892 | 2000.8736 | 81.7598 | 3.3937 | 0.91 | 108.7796 | 136.9323 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 67.0331 | 126.9602
CID=1574692895 | 21 | 69.99 | 87.356 | 4 | 63.99 | 12.798 | 1.7312 | 146.9698 | 27.9878 | 294.074 | 440.9902 | 414.2684 | 30129.1371 | 2.2652 | 0.04734 | 3.1167 | 87.356 | 272.259 | 21 | 69.99 | 4 | 63.99 | 589.5892 | 2116.3519 | 84.7121 | 3.5895 | 0.91205 | 108.3352 | 145.5217 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 74.1546 | 126.9602
CID=1191611344 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-112350571 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-495432122 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1799394037 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2112491708 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=808529793 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1036894082 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-267067833 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1416321583 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1574683798 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1191602247 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-112359668 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-495441219 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1799403134 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=2112482611 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=808520696 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1036884985 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-267076930 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1416318384 | 24 | 40 | 21.373 | 4 | 34 | 6.8 | 1.7302 | 146.5045 | 30.6472 | 247.5407 | 425.4661 | 415.8906 | 19435.9061 | 1.331 | 0.011898 | 10.4843 | 21.373 | 224.0819 | 24 | 40 | 4 | 34 | 645.7808 | 1016.593 | 49.7958 | 1.5742 | 0.78437 | 109.5537 | 41.3999 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2997 | 15.4516 | 39.1373
CID=1574686997 | 24 | 42.5 | 24.4806 | 4 | 36.5 | 7.3 | 1.7302 | 146.5045 | 30.6472 | 251.2145 | 426.8662 | 415.8906 | 20322.2136 | 1.3831 | 0.013198 | 9.3035 | 24.4806 | 227.7557 | 24 | 42.5 | 4 | 36.5 | 645.7808 | 1086.4865 | 52.5657 | 1.6824 | 0.80134 | 109.695 | 46.4154 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7625 | 16.6006 | 48.1204
CID=1191605446 | 24 | 45 | 29.1717 | 4 | 39 | 7.8 | 1.7302 | 146.5045 | 30.6472 | 254.9187 | 428.241 | 415.8906 | 21390.4311 | 1.4969 | 0.015112 | 8.2598 | 29.1717 | 240.9532 | 24 | 45 | 4 | 39 | 645.7808 | 1159.9242 | 55.4926 | 1.7962 | 0.82301 | 110 | 53.853 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7334 | 57.4863
CID=-112356469 | 24 | 47.5 | 34.1284 | 4 | 41.5 | 8.3 | 1.7302 | 146.5045 | 30.6472 | 258.655 | 429.5907 | 415.8906 | 22409.3541 | 1.6095 | 0.017222 | 7.4151 | 34.1284 | 253.066 | 24 | 47.5 | 4 | 41.5 | 645.7808 | 1237.0237 | 58.3649 | 1.9155 | 0.84163 | 110 | 61.6098 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.8929 | 67.8348
CID=-495438020 | 24 | 50 | 39.4309 | 4 | 44 | 8.8 | 1.7302 | 146.5045 | 30.6472 | 262.425 | 430.9154 | 415.8906 | 23381.3443 | 1.7246 | 0.019571 | 6.7121 | 39.4309 | 264.6639 | 24 | 50 | 4 | 44 | 645.7808 | 1317.9055 | 61.2004 | 2.0408 | 0.85761 | 110 | 69.8558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2397 | 79.0043
CID=-1799399935 | 24 | 52.5 | 44.2332 | 4 | 46.5 | 9.3 | 1.7302 | 146.5045 | 30.6472 | 266.2308 | 432.2155 | 415.8906 | 24199.8026 | 1.8106 | 0.021862 | 6.1259 | 44.2332 | 270.9669 | 24 | 52.5 | 4 | 46.5 | 645.7808 | 1402.6932 | 63.9668 | 2.1721 | 0.86925 | 110 | 77.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.8629 | 87.3441
CID=2112485810 | 24 | 55 | 50.7987 | 4 | 49 | 9.8 | 1.7302 | 146.5045 | 30.6472 | 270.0745 | 433.4912 | 415.8906 | 25111.9353 | 1.9526 | 0.024957 | 5.6049 | 50.7987 | 284.724 | 24 | 55 | 4 | 49 | 645.7808 | 1491.5141 | 66.7749 | 2.3096 | 0.88173 | 110 | 87.533 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4237 | 99.9239
CID=808523895 | 24 | 57.5 | 58.6202 | 4 | 51.5 | 10.3 | 1.7302 | 146.5045 | 30.6472 | 273.9586 | 434.7427 | 415.8906 | 26069.707 | 2.1161 | 0.028727 | 5.1235 | 58.6202 | 300.3387 | 24 | 57.5 | 4 | 51.5 | 645.7808 | 1584.4992 | 69.6775 | 2.4536 | 0.89266 | 110 | 99.7738 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.2609 | 113.6981
CID=1036888184 | 24 | 60 | 65.4787 | 4 | 54 | 10.8 | 1.7302 | 146.5045 | 30.6472 | 277.8855 | 435.9703 | 415.8906 | 26866.6301 | 2.2339 | 0.032332 | 4.7082 | 65.4787 | 308.2846 | 24 | 60 | 4 | 54 | 645.7808 | 1681.7842 | 72.5255 | 2.6043 | 0.89964 | 110 | 110.5822 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.9849 | 126.9601
CID=-267073731 | 24 | 62.5 | 69.5951 | 4 | 56.5 | 11.3 | 1.7302 | 146.5045 | 30.6472 | 281.8586 | 437.1743 | 415.8906 | 27420.0301 | 2.2508 | 0.035013 | 4.3349 | 69.5951 | 301.6847 | 24 | 62.5 | 4 | 56.5 | 645.7808 | 1783.5096 | 75.3724 | 2.7618 | 0.90295 | 110 | 117.1042 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4735 | 126.9601
CID=1194059221 | 24 | 65 | 73.614 | 4 | 59 | 11.8 | 1.7302 | 146.5045 | 30.6472 | 285.881 | 438.355 | 415.8906 | 27950.7861 | 2.2666 | 0.037831 | 4.0031 | 73.614 | 294.6855 | 24 | 65 | 4 | 59 | 645.7808 | 1889.8218 | 78.1994 | 2.9264 | 0.90565 | 110 | 123.4964 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.832 | 126.9601
CID=1194059318 | 24 | 67.5 | 77.8965 | 4 | 61.5 | 12.3 | 1.7302 | 146.5045 | 30.6472 | 289.9569 | 439.5127 | 415.8906 | 28474.7815 | 2.2869 | 0.040965 | 3.6972 | 77.8966 | 287.9968 | 24 | 67.5 | 4 | 61.5 | 645.7808 | 2000.8736 | 81.0641 | 3.0984 | 0.90807 | 109.282 | 130.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 61.542 | 126.9602
CID=1194059283 | 24 | 69.99 | 83.2525 | 4 | 63.99 | 12.798 | 1.7302 | 146.5045 | 30.6472 | 294.074 | 440.6434 | 415.8906 | 29056.9802 | 2.3349 | 0.044818 | 3.4164 | 83.2525 | 284.4267 | 24 | 69.99 | 4 | 63.99 | 645.7808 | 2116.3519 | 83.9479 | 3.2772 | 0.91052 | 108.5543 | 138.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68.6833 | 126.9601
CID=1194059124 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194059345 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194059442 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194059407 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194059248 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194058973 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194059070 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178896 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178799 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178834 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178993 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178772 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178675 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178710 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019178869 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179144 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179047 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356199691 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356199788 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356199753 | 27 | 42.5 | 22.5415 | 4 | 36.5 | 7.3 | 1.7292 | 145.9744 | 33.5123 | 251.2145 | 426.563 | 417.481 | 19249.1155 | 1.4587 | 0.012431 | 10.7597 | 22.5415 | 242.5384 | 27 | 42.5 | 4 | 36.5 | 705.9244 | 1086.4865 | 52.1403 | 1.5391 | 0.79102 | 107.2306 | 43.2963 | 0 | 0 | 0 | 0 | 0 | 0 | 8.278 | 16.346 | 41.1277
CID=1356199594 | 27 | 45 | 24.625 | 4 | 39 | 7.8 | 1.7292 | 145.9744 | 33.5123 | 254.9187 | 427.9352 | 417.481 | 19845.1898 | 1.4563 | 0.013419 | 9.6138 | 24.625 | 236.7401 | 27 | 45 | 4 | 39 | 705.9244 | 1159.9242 | 54.7561 | 1.6431 | 0.80207 | 110 | 46.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5416 | 48.8753
CID=1356199815 | 27 | 47.5 | 29.6913 | 4 | 41.5 | 8.3 | 1.7292 | 145.9744 | 33.5123 | 258.655 | 429.2823 | 417.481 | 20960.382 | 1.5913 | 0.015498 | 8.5123 | 29.6913 | 252.7421 | 27 | 47.5 | 4 | 41.5 | 705.9244 | 1237.0237 | 57.6787 | 1.7523 | 0.82516 | 109.6453 | 54.6699 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3547 | 20.0626 | 58.5775
CID=1356199912 | 27 | 50 | 35.189 | 4 | 44 | 8.8 | 1.7292 | 145.9744 | 33.5123 | 262.425 | 430.6045 | 417.481 | 22021.584 | 1.726 | 0.017845 | 7.6053 | 35.189 | 267.6224 | 27 | 50 | 4 | 44 | 705.9244 | 1317.9055 | 60.5904 | 1.8669 | 0.84513 | 110 | 63.2619 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.8529 | 69.1973
CID=1356199877 | 27 | 52.5 | 40.7234 | 4 | 46.5 | 9.3 | 1.7292 | 145.9744 | 33.5123 | 266.2308 | 431.902 | 417.481 | 22977.0054 | 1.8466 | 0.020335 | 6.8585 | 40.7234 | 279.3031 | 27 | 52.5 | 4 | 46.5 | 705.9244 | 1402.6932 | 63.4554 | 1.987 | 0.86098 | 110 | 71.863 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.4146 | 80.6498
CID=1356199718 | 27 | 55 | 45.8406 | 4 | 49 | 9.8 | 1.7292 | 145.9744 | 33.5123 | 270.0745 | 433.1751 | 417.481 | 23807.7664 | 1.9417 | 0.022805 | 6.2439 | 45.8406 | 286.2227 | 27 | 55 | 4 | 49 | 705.9244 | 1491.5141 | 66.2417 | 2.1129 | 0.87264 | 110 | 79.8126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.1505 | 89.9111
CID=1356199443 | 27 | 57.5 | 52.2098 | 4 | 51.5 | 10.3 | 1.7292 | 145.9744 | 33.5123 | 273.9586 | 434.4241 | 417.481 | 24676.8549 | 2.0761 | 0.025906 | 5.7071 | 52.2098 | 297.9657 | 27 | 57.5 | 4 | 51.5 | 705.9244 | 1584.4992 | 69.0397 | 2.2446 | 0.88399 | 110 | 89.7351 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.5589 | 102.1624
CID=1356199540 | 27 | 60 | 59.5926 | 4 | 54 | 10.8 | 1.7292 | 145.9744 | 33.5123 | 277.8855 | 435.6491 | 417.481 | 25565.2903 | 2.2272 | 0.029599 | 5.2171 | 59.5926 | 310.9029 | 27 | 60 | 4 | 54 | 705.9244 | 1681.7842 | 71.9075 | 2.3824 | 0.89378 | 110 | 101.3018 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7067 | 116.2504
CID=-1857038426 | 27 | 62.5 | 65.9241 | 4 | 56.5 | 11.3 | 1.7292 | 145.9744 | 33.5123 | 281.8586 | 436.8505 | 417.481 | 26307.4382 | 2.3263 | 0.033084 | 4.7858 | 65.9241 | 315.4984 | 27 | 62.5 | 4 | 56.5 | 705.9244 | 1783.5096 | 74.7616 | 2.5265 | 0.90003 | 110 | 111.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5787 | 126.9601
CID=-1857038329 | 27 | 65 | 70.211 | 4 | 59 | 11.8 | 1.7292 | 145.9744 | 33.5123 | 285.881 | 438.0286 | 417.481 | 26888.3481 | 2.3489 | 0.035923 | 4.4027 | 70.211 | 309.1191 | 27 | 65 | 4 | 59 | 705.9244 | 1889.8218 | 77.6009 | 2.6771 | 0.90339 | 110 | 118.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.2946 | 126.9601
CID=-1857038364 | 27 | 67.5 | 74.0832 | 4 | 61.5 | 12.3 | 1.7292 | 145.9744 | 33.5123 | 289.9569 | 439.1838 | 417.481 | 27401.9112 | 2.3526 | 0.038775 | 4.0497 | 74.0832 | 300.0137 | 27 | 67.5 | 4 | 61.5 | 705.9244 | 2000.8736 | 80.4889 | 2.8344 | 0.90594 | 109.7947 | 124.2442 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0531 | 56.4575 | 126.9602
CID=-1857038523 | 27 | 69.99 | 79.2061 | 4 | 63.99 | 12.798 | 1.7292 | 145.9744 | 33.5123 | 294.074 | 440.3118 | 417.481 | 27982.9587 | 2.3973 | 0.042399 | 3.7351 | 79.2061 | 295.8408 | 27 | 69.99 | 4 | 63.99 | 705.9244 | 2116.3519 | 83.3573 | 2.998 | 0.90872 | 108.6757 | 132.4294 | 0 | 0 | 0 | 0 | 0 | 0 | 9.47 | 63.2881 | 126.9602
CID=-1857038302 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857038205 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857038240 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857038399 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857038674 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857038577 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109801 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109898 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109863 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109704 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109925 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110022 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109987 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109828 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109553 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162109650 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051128316 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051128219 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051128254 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051128413 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051128192 | 30 | 45 | 21.7305 | 4 | 39 | 7.8 | 1.7283 | 145.3777 | 36.5977 | 254.9187 | 427.6403 | 419.0371 | 19124.6991 | 1.4924 | 0.012324 | 11.2714 | 21.7305 | 244.9337 | 30 | 45 | 4 | 39 | 770.1963 | 1159.9242 | 54.2058 | 1.506 | 0.78644 | 90.9645 | 41.9816 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17.2285 | 35.2368
CID=-2051128095 | 30 | 47.5 | 25.3936 | 4 | 41.5 | 8.3 | 1.7283 | 145.3777 | 36.5977 | 258.655 | 428.9849 | 419.0371 | 19490.1921 | 1.5642 | 0.013865 | 9.8794 | 25.3936 | 250.8729 | 30 | 47.5 | 4 | 41.5 | 770.1963 | 1237.0237 | 57.0566 | 1.6061 | 0.80591 | 108.8838 | 47.8736 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1317 | 17.3626 | 49.4867
CID=-2051128130 | 30 | 50 | 30.469 | 4 | 44 | 8.8 | 1.7283 | 145.3777 | 36.5977 | 262.425 | 430.3047 | 419.0371 | 20568.4922 | 1.6948 | 0.015992 | 8.7114 | 30.469 | 265.4263 | 30 | 50 | 4 | 44 | 770.1963 | 1317.9055 | 59.9927 | 1.7111 | 0.82828 | 110 | 55.8906 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.758 | 59.6018
CID=-2051128289 | 30 | 52.5 | 36.0102 | 4 | 46.5 | 9.3 | 1.7283 | 145.3777 | 36.5977 | 266.2308 | 431.5997 | 419.0371 | 21587.4984 | 1.8295 | 0.018407 | 7.7635 | 36.0102 | 279.5654 | 30 | 52.5 | 4 | 46.5 | 770.1963 | 1402.6932 | 62.9059 | 1.8212 | 0.84772 | 110 | 64.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.5286 | 70.4551
CID=-2051128564 | 30 | 55 | 41.7227 | 4 | 49 | 9.8 | 1.7283 | 145.3777 | 36.5977 | 270.0745 | 432.8703 | 419.0371 | 22540.5752 | 1.9586 | 0.021022 | 6.9929 | 41.7227 | 291.7611 | 30 | 55 | 4 | 49 | 770.1963 | 1491.5141 | 65.7612 | 1.9365 | 0.86346 | 110 | 73.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2091 | 82.2635
CID=-2051128467 | 30 | 57.5 | 47.7804 | 4 | 51.5 | 10.3 | 1.7283 | 145.3777 | 36.5977 | 273.9586 | 434.1168 | 419.0371 | 23450.6605 | 2.0933 | 0.023919 | 6.356 | 47.7804 | 303.6907 | 30 | 57.5 | 4 | 51.5 | 770.1963 | 1584.4992 | 68.5574 | 2.0573 | 0.87643 | 110 | 82.8302 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0207 | 95.0594
CID=1324250271 | 30 | 60 | 53.1759 | 4 | 54 | 10.8 | 1.7283 | 145.3777 | 36.5977 | 277.8855 | 435.3393 | 419.0371 | 24209.4451 | 2.1894 | 0.026725 | 5.8116 | 53.1759 | 309.0376 | 30 | 60 | 4 | 54 | 770.1963 | 1681.7842 | 71.3183 | 2.1836 | 0.88545 | 110 | 91.2443 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.1156 | 104.3567
CID=1324250368 | 30 | 62.5 | 60.5879 | 4 | 56.5 | 11.3 | 1.7283 | 145.3777 | 36.5977 | 281.8586 | 436.5383 | 419.0371 | 25069.7134 | 2.3475 | 0.030527 | 5.3151 | 60.5879 | 322.0313 | 30 | 62.5 | 4 | 56.5 | 770.1963 | 1783.5096 | 74.1508 | 2.3157 | 0.89488 | 110 | 102.8672 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2449 | 118.617
CID=1324250333 | 30 | 65 | 67.2313 | 4 | 59 | 11.8 | 1.7283 | 145.3777 | 36.5977 | 285.881 | 437.7139 | 419.0371 | 25825.9211 | 2.4597 | 0.034248 | 4.8716 | 67.2313 | 327.5272 | 30 | 65 | 4 | 59 | 770.1963 | 1889.8218 | 76.9958 | 2.4537 | 0.90112 | 110 | 113.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.3217 | 126.9601
CID=1324250174 | 30 | 67.5 | 71.3233 | 4 | 61.5 | 12.3 | 1.7283 | 145.3777 | 36.5977 | 289.9569 | 438.8665 | 419.0371 | 26381.0162 | 2.4698 | 0.037108 | 4.4698 | 71.3233 | 318.8004 | 30 | 67.5 | 4 | 61.5 | 770.1963 | 2000.8736 | 79.8623 | 2.5979 | 0.90417 | 110 | 119.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.7777 | 126.9602
CID=1324250395 | 30 | 69.99 | 75.7973 | 4 | 63.99 | 12.798 | 1.7283 | 145.3777 | 36.5977 | 294.074 | 439.9919 | 419.0371 | 26937.8082 | 2.4878 | 0.04034 | 4.1015 | 75.7973 | 310.8845 | 30 | 69.99 | 4 | 63.99 | 770.1963 | 2116.3519 | 82.7706 | 2.7478 | 0.90694 | 109.593 | 126.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 8.557 | 58.743 | 126.9602
CID=1324250492 | -18 | -5 | 8.0333 | 4 | -11 | 0 | 1.7524 | 147.8757 | 7.2169 | 185.3801 | 401.7246 | 391.078 | 21488.9311 | 0.38999 | 0.0064187 | 9.9859 | 8.0333 | 80.2194 | -18 | -5 | 4 | -11 | 144.6004 | 243.3424 | 9.1949 | 1.6829 | 0.67931 | 110 | 17.9672 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5498 | 11.5167
CID=1324250457 | -18 | -2.5 | 10.0987 | 4 | -8.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 188.676 | 403.6805 | 391.078 | 23068.3605 | 0.44203 | 0.0069747 | 8.8594 | 10.0987 | 89.4685 | -18 | -2.5 | 4 | -8.5 | 144.6004 | 267.1911 | 12.6008 | 1.8478 | 0.69976 | 110 | 21.9265 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.577 | 14.6204
CID=1324250298 | -18 | 0 | 12.4847 | 4 | -6 | 0 | 1.7524 | 147.8757 | 7.2169 | 191.9873 | 405.6071 | 391.078 | 24581.1481 | 0.4967 | 0.0076813 | 7.9207 | 12.4847 | 98.8883 | -18 | 0 | 4 | -6 | 144.6004 | 292.8032 | 15.9551 | 2.0249 | 0.72124 | 110 | 26.3 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.7893 | 18.1802
CID=1324250023 | -18 | 2.5 | 14.5985 | 4 | -3.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 195.3144 | 407.5045 | 391.078 | 25746.0218 | 0.53672 | 0.0083705 | 7.1974 | 14.5985 | 105.0705 | -18 | 2.5 | 4 | -3.5 | 144.6004 | 320.2635 | 18.9479 | 2.2148 | 0.73851 | 110 | 30.0336 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8511 | 21.3458
CID=1324250120 | -18 | 5 | 17.6648 | 4 | -1 | 0 | 1.7524 | 147.8757 | 7.2169 | 198.6579 | 409.3731 | 391.078 | 27111.1048 | 0.59558 | 0.0093638 | 6.4876 | 17.6648 | 114.6025 | -18 | 5 | 4 | -1 | 144.6004 | 349.6586 | 22.3745 | 2.4181 | 0.76093 | 110 | 35.2713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5588 | 25.7708
CID=-1888987846 | -18 | 7.5 | 20.8705 | 4 | 1.5 | 0.3 | 1.7524 | 147.8757 | 7.2169 | 202.0183 | 411.2128 | 391.078 | 28379.8452 | 0.6503 | 0.010449 | 5.8908 | 20.8705 | 122.9448 | -18 | 7.5 | 4 | 1.5 | 144.6004 | 381.0767 | 25.7152 | 2.6354 | 0.78141 | 110 | 40.5797 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.097 | 30.644
CID=-1888987749 | -18 | 10 | 24.5244 | 4 | 4 | 0.8 | 1.7524 | 147.8757 | 7.2169 | 205.396 | 413.024 | 391.078 | 29609.7829 | 0.70744 | 0.011718 | 5.3563 | 24.5244 | 131.3593 | -18 | 10 | 4 | 4 | 144.6004 | 414.6075 | 29.1647 | 2.8673 | 0.80156 | 110 | 46.4855 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0916 | 35.9571
CID=-1888987784 | -18 | 12.5 | 27.6012 | 4 | 6.5 | 1.3 | 1.7524 | 147.8757 | 7.2169 | 208.7918 | 414.8068 | 391.078 | 30507.824 | 0.74858 | 0.012868 | 4.9438 | 27.6012 | 136.4551 | -18 | 12.5 | 4 | 6.5 | 144.6004 | 450.3422 | 32.193 | 3.1144 | 0.81624 | 110 | 51.3767 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2624 | 39.94
CID=-1888987943 | -18 | 15 | 31.5771 | 4 | 9 | 1.8 | 1.7524 | 147.8757 | 7.2169 | 212.2062 | 416.5615 | 391.078 | 31527.2875 | 0.80051 | 0.014346 | 4.5346 | 31.5771 | 143.189 | -18 | 15 | 4 | 9 | 144.6004 | 488.3739 | 35.5865 | 3.3774 | 0.83254 | 110 | 57.6263 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.7059 | 45.4484
CID=-1888987722 | -18 | 17.5 | 35.4985 | 4 | 11.5 | 2.3 | 1.7524 | 147.8757 | 7.2169 | 215.6398 | 418.2881 | 391.078 | 32427.6481 | 0.84861 | 0.01587 | 4.194 | 35.4985 | 148.8791 | -18 | 17.5 | 4 | 11.5 | 144.6004 | 528.7968 | 38.771 | 3.657 | 0.84612 | 110 | 63.7436 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3419 | 50.6552
CID=-1888987625 | -18 | 20 | 37.5116 | 4 | 14 | 2.8 | 1.7524 | 147.8757 | 7.2169 | 219.0933 | 419.9871 | 391.078 | 32941.5644 | 0.8633 | 0.016841 | 3.9581 | 37.5116 | 148.4736 | -18 | 20 | 4 | 14 | 144.6004 | 571.7069 | 41.1736 | 3.9537 | 0.85224 | 110 | 66.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3788 | 51.6444
CID=-1888987660 | -18 | 22.5 | 39.036 | 4 | 16.5 | 3.3 | 1.7524 | 147.8757 | 7.2169 | 222.5675 | 421.6585 | 391.078 | 33412.1575 | 0.86227 | 0.017693 | 3.7223 | 39.036 | 145.3023 | -18 | 22.5 | 4 | 16.5 | 144.6004 | 617.2019 | 43.7534 | 4.2683 | 0.85654 | 110 | 69.2425 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.5651 | 51.5068
CID=-1888987819 | -18 | 25 | 41.2645 | 4 | 19 | 3.8 | 1.7524 | 147.8757 | 7.2169 | 226.0633 | 423.3026 | 391.078 | 34006.6564 | 0.87179 | 0.018822 | 3.4863 | 41.2645 | 143.8586 | -18 | 25 | 4 | 19 | 144.6004 | 665.3809 | 46.5795 | 4.6015 | 0.86234 | 110 | 72.7033 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9668 | 51.5623
CID=-1888988094 | -18 | 27.5 | 43.7503 | 4 | 21.5 | 4.3 | 1.7524 | 147.8757 | 7.2169 | 229.5813 | 424.9196 | 391.078 | 34620.2704 | 0.88251 | 0.020092 | 3.2576 | 43.7503 | 142.5222 | -18 | 27.5 | 4 | 21.5 | 144.6004 | 716.3449 | 49.5734 | 4.954 | 0.86818 | 110 | 76.564 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.6287 | 51.8719
CID=-1888987997 | -18 | 30 | 46.4285 | 4 | 24 | 4.8 | 1.7524 | 147.8757 | 7.2169 | 233.1226 | 426.5097 | 391.078 | 35219.8497 | 0.89337 | 0.021491 | 3.0393 | 46.4286 | 141.1124 | -18 | 30 | 4 | 24 | 144.6004 | 770.1963 | 52.7031 | 5.3264 | 0.87382 | 109.2269 | 80.7269 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 40.9637 | 51.8934
CID=1130160381 | -18 | 32.5 | 49.8444 | 4 | 26.5 | 5.3 | 1.7524 | 147.8757 | 7.2169 | 236.688 | 428.0733 | 391.078 | 35863.7853 | 0.92477 | 0.023225 | 2.8644 | 49.8444 | 142.7755 | -18 | 32.5 | 4 | 26.5 | 144.6004 | 827.0396 | 55.4371 | 5.7195 | 0.88013 | 108.9941 | 86.045 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.2998 | 51.389
CID=1130160478 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160443 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160284 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160505 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160602 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160567 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160408 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160133 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130160230 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077736 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077639 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077674 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077833 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077612 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077515 | -18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077550 | -15 | -5 | 0 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083077709 | -15 | -2.5 | 8.3709 | 4 | -8.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 188.676 | 402.9994 | 392.9623 | 21055.9073 | 0.42746 | 0.0065309 | 10.4318 | 8.3709 | 87.3235 | -15 | -2.5 | 4 | -8.5 | 163.9401 | 267.1911 | 11.1793 | 1.6298 | 0.68278 | 110 | 18.6273 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.9292 | 11.8126
CID=-2083077984 | -15 | 0 | 10.4582 | 4 | -6 | 0 | 1.7499 | 148.1062 | 8.1279 | 191.9873 | 404.9188 | 392.9623 | 22578.0897 | 0.4786 | 0.0071094 | 9.1972 | 10.4582 | 96.1862 | -15 | 0 | 4 | -6 | 163.9401 | 292.8032 | 14.551 | 1.786 | 0.70314 | 110 | 22.598 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7776 | 15.1388
CID=-2083077887 | -15 | 2.5 | 12.901 | 4 | -3.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 195.3144 | 406.8092 | 392.9623 | 24042.4362 | 0.53542 | 0.0078449 | 8.2028 | 12.901 | 105.8245 | -15 | 2.5 | 4 | -3.5 | 163.9401 | 320.2635 | 17.8347 | 1.9535 | 0.72476 | 110 | 27.0446 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.9172 | 18.8847
CID=1194056022 | -15 | 5 | 15.7116 | 4 | -1 | 0 | 1.7499 | 148.1062 | 8.1279 | 198.6579 | 408.6707 | 392.9623 | 25448.8949 | 0.59653 | 0.0087357 | 7.3772 | 15.7116 | 115.9079 | -15 | 5 | 4 | -1 | 163.9401 | 349.6586 | 21.0677 | 2.1328 | 0.74699 | 110 | 31.9566 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3095 | 23.1137
CID=1194056053 | -15 | 7.5 | 18.271 | 4 | 1.5 | 0.3 | 1.7499 | 148.1062 | 8.1279 | 202.0183 | 410.5034 | 392.9623 | 26564.6021 | 0.64176 | 0.0096073 | 6.7068 | 18.271 | 122.5406 | -15 | 7.5 | 4 | 1.5 | 163.9401 | 381.0767 | 24.1002 | 2.3245 | 0.76502 | 110 | 36.2865 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.7669 | 26.7752
CID=1194056084 | -15 | 10 | 21.8865 | 4 | 4 | 0.8 | 1.7499 | 148.1062 | 8.1279 | 205.396 | 412.3077 | 392.9623 | 27876.5785 | 0.70752 | 0.010828 | 6.0634 | 21.8865 | 132.7061 | -15 | 10 | 4 | 4 | 163.9401 | 414.6075 | 27.4877 | 2.529 | 0.78734 | 110 | 42.235 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7699 | 32.0031
CID=1194056115 | -15 | 12.5 | 25.574 | 4 | 6.5 | 1.3 | 1.7499 | 148.1062 | 8.1279 | 208.7918 | 414.0836 | 392.9623 | 29066.7298 | 0.76748 | 0.012128 | 5.527 | 25.574 | 141.3472 | -15 | 12.5 | 4 | 6.5 | 163.9401 | 450.3422 | 30.7535 | 2.747 | 0.80679 | 110 | 48.1609 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.601 | 37.5469
CID=1194056146 | -15 | 15 | 28.909 | 4 | 9 | 1.8 | 1.7499 | 148.1062 | 8.1279 | 212.2062 | 415.8315 | 392.9623 | 30003.0012 | 0.81398 | 0.013378 | 5.0895 | 28.909 | 147.1317 | -15 | 15 | 4 | 9 | 163.9401 | 488.3739 | 33.7865 | 2.979 | 0.82191 | 110 | 53.4397 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8508 | 41.9673
CID=1194056177 | -15 | 17.5 | 33.0899 | 4 | 11.5 | 2.3 | 1.7499 | 148.1062 | 8.1279 | 215.6398 | 417.5513 | 392.9623 | 31010.0017 | 0.87226 | 0.014946 | 4.6743 | 33.0899 | 154.6707 | -15 | 17.5 | 4 | 11.5 | 163.9401 | 528.7968 | 37.043 | 3.2255 | 0.83805 | 110 | 59.9902 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.3412 | 47.8386
CID=1194056208 | -15 | 20 | 37.3819 | 4 | 14 | 2.8 | 1.7499 | 148.1062 | 8.1279 | 219.0933 | 419.2435 | 392.9623 | 31952.5053 | 0.92442 | 0.016617 | 4.2996 | 37.3819 | 160.7274 | -15 | 20 | 4 | 14 | 163.9401 | 571.7069 | 40.3532 | 3.4873 | 0.85186 | 110 | 66.6727 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.1691 | 53.5948
CID=1194056239 | -15 | 22.5 | 41.2528 | 4 | 16.5 | 3.3 | 1.7499 | 148.1062 | 8.1279 | 222.5675 | 420.9082 | 392.9623 | 32726.9481 | 0.96867 | 0.018224 | 4.0011 | 41.2528 | 165.0567 | -15 | 22.5 | 4 | 16.5 | 163.9401 | 617.2019 | 43.3078 | 3.7648 | 0.86231 | 110 | 72.6851 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0585 | 58.447
CID=1194055774 | -15 | 25 | 43.3216 | 4 | 19 | 3.8 | 1.7499 | 148.1062 | 8.1279 | 226.0633 | 422.5457 | 392.9623 | 33204.781 | 0.98232 | 0.019298 | 3.7844 | 43.3216 | 163.9484 | -15 | 25 | 4 | 19 | 163.9401 | 665.3809 | 45.6404 | 4.0587 | 0.86722 | 110 | 75.8981 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8402 | 58.803
CID=1194055805 | -15 | 27.5 | 44.9652 | 4 | 21.5 | 4.3 | 1.7499 | 148.1062 | 8.1279 | 229.5813 | 424.156 | 392.9623 | 33665.1499 | 0.97842 | 0.020276 | 3.5551 | 44.9652 | 159.8557 | -15 | 27.5 | 4 | 21.5 | 163.9401 | 716.3449 | 48.2824 | 4.3696 | 0.87082 | 110 | 78.4518 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.3546 | 58.5759
CID=-2019182095 | -15 | 30 | 47.1806 | 4 | 24 | 4.8 | 1.7499 | 148.1062 | 8.1279 | 233.1226 | 425.7396 | 392.9623 | 34213.5134 | 0.98407 | 0.0215 | 3.3338 | 47.1806 | 157.293 | -15 | 30 | 4 | 24 | 163.9401 | 770.1963 | 51.0609 | 4.698 | 0.87529 | 110 | 81.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.422 | 57.9392
CID=-2019182064 | -15 | 32.5 | 49.945 | 4 | 26.5 | 5.3 | 1.7499 | 148.1062 | 8.1279 | 236.688 | 427.2966 | 392.9623 | 34799.3692 | 0.99621 | 0.022981 | 3.1171 | 49.945 | 155.6821 | -15 | 32.5 | 4 | 26.5 | 163.9401 | 827.0396 | 54.0308 | 5.0448 | 0.8803 | 109.9124 | 86.2018 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7297 | 41.4958 | 58.3942
CID=-2019182033 | -15 | 35 | 53.4937 | 4 | 29 | 5.8 | 1.7499 | 148.1062 | 8.1279 | 240.2788 | 428.8272 | 392.9623 | 35431.8743 | 1.0205 | 0.024823 | 2.9127 | 53.4937 | 155.8113 | -15 | 35 | 4 | 29 | 163.9401 | 886.981 | 57.0945 | 5.4104 | 0.88592 | 109.2277 | 91.7412 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.0343 | 58.9531
CID=-2019182002 | -15 | 37.5 | 55.9832 | 4 | 31.5 | 6.3 | 1.7499 | 148.1062 | 8.1279 | 243.8959 | 430.3317 | 392.9623 | 35950.5963 | 1.0293 | 0.026361 | 2.7407 | 55.9832 | 153.4335 | -15 | 37.5 | 4 | 31.5 | 163.9401 | 950.1287 | 59.8669 | 5.7956 | 0.88938 | 108.8204 | 95.637 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.3815 | 56.5848
CID=-2019181971 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019181940 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019181909 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019181878 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019182343 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019182312 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196492 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196523 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196554 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196585 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196616 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196647 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196678 | -15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196709 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196244 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356196275 | -12 | 0 | 8.9264 | 4 | -6 | 0 | 1.7476 | 148.2918 | 9.1273 | 191.9873 | 404.2823 | 394.8346 | 20766.3989 | 0.47388 | 0.0066949 | 10.7687 | 8.9264 | 96.1258 | -12 | 0 | 4 | -6 | 185.2442 | 292.8032 | 13.4586 | 1.5806 | 0.68838 | 110 | 19.7018 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4538 | 12.3991
CID=-1857041625 | -12 | 2.5 | 10.7921 | 4 | -3.5 | 0 | 1.7476 | 148.2918 | 9.1273 | 195.3144 | 406.166 | 394.8346 | 22080.1312 | 0.5173 | 0.0072421 | 9.5636 | 10.7921 | 103.2111 | -12 | 2.5 | 4 | -3.5 | 185.2442 | 320.2635 | 16.4952 | 1.7289 | 0.70623 | 110 | 23.2174 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9439 | 15.6403
CID=-1857041594 | -12 | 5 | 13.4372 | 4 | -1 | 0 | 1.7476 | 148.2918 | 9.1273 | 198.6579 | 408.021 | 394.8346 | 23561.5758 | 0.58169 | 0.0080444 | 8.4925 | 13.4372 | 114.1148 | -12 | 5 | 4 | -1 | 185.2442 | 349.6586 | 19.7733 | 1.8876 | 0.72921 | 110 | 27.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3298 | 19.5445
CID=-1857041563 | -12 | 7.5 | 16.2709 | 4 | 1.5 | 0.3 | 1.7476 | 148.2918 | 9.1273 | 202.0183 | 409.8472 | 394.8346 | 24922.0308 | 0.64307 | 0.0089574 | 7.6206 | 16.2709 | 123.9936 | -12 | 7.5 | 4 | 1.5 | 185.2442 | 381.0767 | 22.9467 | 2.0572 | 0.7511 | 110 | 32.9131 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5649 | 23.9769
CID=-1857041532 | -12 | 10 | 18.8998 | 4 | 4 | 0.8 | 1.7476 | 148.2918 | 9.1273 | 205.396 | 411.6451 | 394.8346 | 26023.1301 | 0.69183 | 0.009863 | 6.9345 | 18.8998 | 131.06 | -12 | 10 | 4 | 4 | 185.2442 | 414.6075 | 25.8697 | 2.2382 | 0.76915 | 110 | 37.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.993 | 27.8065
CID=-1857041501 | -12 | 12.5 | 22.6845 | 4 | 6.5 | 1.3 | 1.7476 | 148.2918 | 9.1273 | 208.7918 | 413.4146 | 394.8346 | 27313.9567 | 0.7637 | 0.011152 | 6.2634 | 22.6845 | 142.081 | -12 | 12.5 | 4 | 6.5 | 185.2442 | 450.3422 | 29.183 | 2.4311 | 0.79181 | 110 | 43.5275 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1391 | 33.2299
CID=-1857041470 | -12 | 15 | 26.5662 | 4 | 9 | 1.8 | 1.7476 | 148.2918 | 9.1273 | 212.2062 | 415.1561 | 394.8346 | 28512.6976 | 0.82865 | 0.012531 | 5.6965 | 26.5662 | 151.3351 | -12 | 15 | 4 | 9 | 185.2442 | 488.3739 | 32.4259 | 2.6364 | 0.81152 | 110 | 49.7379 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0304 | 39.1019
CID=-1857041439 | -12 | 17.5 | 30.96 | 4 | 11.5 | 2.3 | 1.7476 | 148.2918 | 9.1273 | 215.6398 | 416.8697 | 394.8346 | 29674.4388 | 0.89676 | 0.014129 | 5.1904 | 30.96 | 160.6946 | -12 | 17.5 | 4 | 11.5 | 185.2442 | 528.7968 | 35.7561 | 2.8546 | 0.83019 | 110 | 56.6602 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.4121 | 45.5079
CID=-1857041408 | -12 | 20 | 34.5972 | 4 | 14 | 2.8 | 1.7476 | 148.2918 | 9.1273 | 219.0933 | 418.5557 | 394.8346 | 30514.4569 | 0.94493 | 0.015557 | 4.7999 | 34.5972 | 166.0634 | -12 | 20 | 4 | 14 | 185.2442 | 571.7069 | 38.6861 | 3.0862 | 0.8432 | 110 | 62.3402 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.032 | 50.1624
CID=-1857041873 | -12 | 22.5 | 39.3197 | 4 | 16.5 | 3.3 | 1.7476 | 148.2918 | 9.1273 | 222.5675 | 420.2141 | 394.8346 | 31474.1507 | 1.0074 | 0.017399 | 4.4136 | 39.3197 | 173.5395 | -12 | 22.5 | 4 | 16.5 | 185.2442 | 617.2019 | 41.9353 | 3.3318 | 0.85731 | 110 | 69.6832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.8538 | 56.7855
CID=-1857041842 | -12 | 25 | 43.9596 | 4 | 19 | 3.8 | 1.7476 | 148.2918 | 9.1273 | 226.0633 | 421.8454 | 394.8346 | 32335.1276 | 1.0635 | 0.019295 | 4.083 | 43.9596 | 179.4868 | -12 | 25 | 4 | 19 | 185.2442 | 665.3809 | 45.0593 | 3.5919 | 0.86865 | 110 | 76.8891 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9272 | 62.9919
CID=1162106602 | -12 | 27.5 | 47.1454 | 4 | 21.5 | 4.3 | 1.7476 | 148.2918 | 9.1273 | 229.5813 | 423.4496 | 394.8346 | 32927.8148 | 1.0937 | 0.020784 | 3.8338 | 47.1454 | 180.7452 | -12 | 27.5 | 4 | 21.5 | 185.2442 | 716.3449 | 47.6646 | 3.867 | 0.87522 | 110 | 81.842 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.6206 | 65.6702
CID=1162106633 | -12 | 30 | 49.1245 | 4 | 24 | 4.8 | 1.7476 | 148.2918 | 9.1273 | 233.1226 | 425.027 | 394.8346 | 33370.1999 | 1.0993 | 0.021924 | 3.6187 | 49.1245 | 177.766 | -12 | 30 | 4 | 24 | 185.2442 | 770.1963 | 50.0909 | 4.1577 | 0.87888 | 110 | 84.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.3085 | 65.9405
CID=1162106664 | -12 | 32.5 | 51.2071 | 4 | 26.5 | 5.3 | 1.7476 | 148.2918 | 9.1273 | 236.688 | 426.5779 | 394.8346 | 33849.4523 | 1.1005 | 0.023156 | 3.3988 | 51.2071 | 174.0409 | -12 | 32.5 | 4 | 26.5 | 185.2442 | 827.0396 | 52.7592 | 4.4646 | 0.8824 | 110 | 88.1701 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.6126 | 65.8016
CID=1162106695 | -12 | 35 | 54.0209 | 4 | 29 | 5.8 | 1.7476 | 148.2918 | 9.1273 | 240.2788 | 428.1024 | 394.8346 | 34428.2216 | 1.1123 | 0.024713 | 3.1824 | 54.0209 | 171.9147 | -12 | 35 | 4 | 29 | 185.2442 | 886.981 | 55.6139 | 4.7882 | 0.88668 | 110 | 92.5655 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.4028 | 65.639
CID=1162106726 | -12 | 37.5 | 57.0486 | 4 | 31.5 | 6.3 | 1.7476 | 148.2918 | 9.1273 | 243.8959 | 429.6009 | 394.8346 | 34982.9155 | 1.126 | 0.02643 | 2.9792 | 57.0486 | 169.9616 | -12 | 37.5 | 4 | 31.5 | 185.2442 | 950.1287 | 58.5268 | 5.1291 | 0.89075 | 109.8341 | 97.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3639 | 47.9875 | 66.1098
CID=1162106757 | -12 | 40 | 60.9839 | 4 | 34 | 6.8 | 1.7476 | 148.2918 | 9.1273 | 247.5407 | 431.0734 | 394.8346 | 35592.667 | 1.1543 | 0.028581 | 2.7881 | 60.9839 | 170.0266 | -12 | 40 | 4 | 34 | 185.2442 | 1016.593 | 61.5116 | 5.4879 | 0.8953 | 109.1735 | 103.4905 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.8685 | 66.0993
CID=1162106788 | -12 | 42.5 | 63.5495 | 4 | 36.5 | 7.3 | 1.7476 | 148.2918 | 9.1273 | 251.2145 | 432.5204 | 394.8346 | 36083.9561 | 1.161 | 0.030314 | 2.6239 | 63.5495 | 166.7476 | -12 | 42.5 | 4 | 36.5 | 185.2442 | 1086.4865 | 64.2593 | 5.8652 | 0.89788 | 108.6613 | 107.5344 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1387 | 63.9602
CID=1162106819 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162106354 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162106385 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131515 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131484 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131453 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131422 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131391 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131360 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131329 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131298 | -12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131763 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051131732 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324247072 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324247103 | -9 | 2.5 | 8.1243 | 4 | -3.5 | 0 | 1.7455 | 148.4312 | 10.2212 | 195.3144 | 405.5712 | 396.6938 | 19585.4492 | 0.47037 | 0.0065746 | 11.6593 | 8.1243 | 94.723 | -9 | 2.5 | 4 | -3.5 | 208.6448 | 320.2635 | 14.5962 | 1.535 | 0.68025 | 109.6472 | 18.1456 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2097 | 5.8776 | 10.3709
CID=1324247134 | -9 | 5 | 11.0293 | 4 | -1 | 0 | 1.7455 | 148.4312 | 10.2212 | 198.6579 | 407.4201 | 396.6938 | 21546.6999 | 0.55452 | 0.0073549 | 9.9566 | 11.0293 | 109.815 | -9 | 5 | 4 | -1 | 208.6448 | 349.6586 | 18.4349 | 1.6759 | 0.7084 | 110 | 23.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9672 | 16.0914
CID=1324247165 | -9 | 7.5 | 13.7711 | 4 | 1.5 | 0.3 | 1.7455 | 148.4312 | 10.2212 | 202.0183 | 409.2404 | 396.6938 | 23023.6613 | 0.62218 | 0.0081953 | 8.7954 | 13.7711 | 121.1229 | -9 | 7.5 | 4 | 1.5 | 208.6448 | 381.0767 | 21.7109 | 1.8264 | 0.73193 | 110 | 28.5859 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3549 | 20.1873
CID=1324247196 | -9 | 10 | 16.8758 | 4 | 4 | 0.8 | 1.7455 | 148.4312 | 10.2212 | 205.396 | 411.0322 | 396.6938 | 24432.7302 | 0.69389 | 0.0091974 | 7.8657 | 16.8758 | 132.7402 | -9 | 10 | 4 | 4 | 208.6448 | 414.6075 | 24.8834 | 1.9871 | 0.75544 | 110 | 33.9407 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9222 | 24.8293
CID=1324247227 | -9 | 12.5 | 19.9489 | 4 | 6.5 | 1.3 | 1.7455 | 148.4312 | 10.2212 | 208.7918 | 412.7959 | 396.6938 | 25627.1967 | 0.75596 | 0.010247 | 7.1205 | 19.9489 | 142.0455 | -9 | 12.5 | 4 | 6.5 | 208.6448 | 450.3422 | 27.8826 | 2.1584 | 0.77581 | 110 | 39.0679 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.5321 | 29.3656
CID=1324247258 | -9 | 15 | 23.3626 | 4 | 9 | 1.8 | 1.7455 | 148.4312 | 10.2212 | 212.2062 | 414.5315 | 396.6938 | 26768.3584 | 0.81785 | 0.011448 | 6.4583 | 23.3626 | 150.883 | -9 | 15 | 4 | 9 | 208.6448 | 488.3739 | 30.9682 | 2.3407 | 0.79549 | 110 | 44.621 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3102 | 34.4149
CID=1324247289 | -9 | 17.5 | 27.7375 | 4 | 11.5 | 2.3 | 1.7455 | 148.4312 | 10.2212 | 215.6398 | 416.2392 | 396.6938 | 28014.0061 | 0.8964 | 0.012997 | 5.8512 | 27.7375 | 162.2975 | -9 | 17.5 | 4 | 11.5 | 208.6448 | 528.7968 | 34.2513 | 2.5344 | 0.81684 | 110 | 51.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7558 | 40.7191
CID=1324246824 | -9 | 20 | 32.1748 | 4 | 14 | 2.8 | 1.7455 | 148.4312 | 10.2212 | 219.0933 | 417.9194 | 396.6938 | 29138.3192 | 0.96841 | 0.014636 | 5.3455 | 32.1748 | 171.9909 | -9 | 20 | 4 | 14 | 208.6448 | 571.7069 | 37.4125 | 2.7401 | 0.83476 | 110 | 58.561 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9978 | 47.3518
CID=1324246855 | -9 | 22.5 | 36.167 | 4 | 16.5 | 3.3 | 1.7455 | 148.4312 | 10.2212 | 222.5675 | 419.5721 | 396.6938 | 30027.211 | 1.024 | 0.016204 | 4.9298 | 36.167 | 178.2971 | -9 | 22.5 | 4 | 16.5 | 208.6448 | 617.2019 | 40.3705 | 2.9581 | 0.84821 | 110 | 64.7837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.6774 | 52.6566
CID=-1888991045 | -9 | 25 | 40.9982 | 4 | 19 | 3.8 | 1.7455 | 148.4312 | 10.2212 | 226.0633 | 421.1976 | 396.6938 | 30960.167 | 1.0906 | 0.018115 | 4.5388 | 40.9982 | 186.0823 | -9 | 25 | 4 | 19 | 208.6448 | 665.3809 | 43.4972 | 3.1891 | 0.86168 | 110 | 72.2898 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5308 | 59.4656
CID=-1888991014 | -9 | 27.5 | 46.0901 | 4 | 21.5 | 4.3 | 1.7455 | 148.4312 | 10.2212 | 229.5813 | 422.7961 | 396.6938 | 31862.121 | 1.1524 | 0.0202 | 4.1785 | 46.0901 | 192.5856 | -9 | 27.5 | 4 | 21.5 | 208.6448 | 716.3449 | 46.7282 | 3.4333 | 0.87314 | 110 | 80.2006 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.7566 | 66.4236
CID=-1888990983 | -9 | 30 | 51.2546 | 4 | 24 | 4.8 | 1.7455 | 148.4312 | 10.2212 | 233.1226 | 424.3678 | 396.6938 | 32671.2861 | 1.2154 | 0.022404 | 3.8786 | 51.2546 | 198.7966 | -9 | 30 | 4 | 24 | 208.6448 | 770.1963 | 49.7493 | 3.6914 | 0.88248 | 110 | 88.2441 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1758 | 73.3333
CID=-1888990952 | -9 | 32.5 | 53.5694 | 4 | 26.5 | 5.3 | 1.7455 | 148.4312 | 10.2212 | 236.688 | 425.913 | 396.6938 | 33098.2551 | 1.2298 | 0.023714 | 3.6734 | 53.5694 | 196.7827 | -9 | 32.5 | 4 | 26.5 | 208.6448 | 827.0396 | 52.0272 | 3.9639 | 0.88603 | 110 | 91.8594 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.425 | 73.7137
CID=-1888990921 | -9 | 35 | 55.403 | 4 | 29 | 5.8 | 1.7455 | 148.4312 | 10.2212 | 240.2788 | 427.4319 | 396.6938 | 33510.6324 | 1.2253 | 0.024915 | 3.4592 | 55.403 | 191.652 | -9 | 35 | 4 | 29 | 208.6448 | 886.981 | 54.554 | 4.2512 | 0.88861 | 110 | 94.7282 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.4523 | 73.3536
CID=-1888990890 | -9 | 37.5 | 58.1504 | 4 | 31.5 | 6.3 | 1.7455 | 148.4312 | 10.2212 | 243.8959 | 428.9247 | 396.6938 | 34029.8898 | 1.2353 | 0.026512 | 3.246 | 58.1504 | 188.7569 | -9 | 37.5 | 4 | 31.5 | 208.6448 | 950.1287 | 57.2742 | 4.5538 | 0.8921 | 110 | 99.0359 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9142 | 73.3866
CID=-1888990859 | -9 | 40 | 61.5297 | 4 | 34 | 6.8 | 1.7455 | 148.4312 | 10.2212 | 247.5407 | 430.3916 | 396.6938 | 34614.1204 | 1.2525 | 0.02843 | 3.0361 | 61.5297 | 186.8099 | -9 | 40 | 4 | 34 | 208.6448 | 1016.593 | 60.1767 | 4.8724 | 0.89588 | 110 | 104.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.0108 | 74.0486
CID=-1888990828 | -9 | 42.5 | 64.8221 | 4 | 36.5 | 7.3 | 1.7455 | 148.4312 | 10.2212 | 251.2145 | 431.833 | 396.6938 | 35144.9752 | 1.2658 | 0.030418 | 2.8407 | 64.8221 | 184.141 | -9 | 42.5 | 4 | 36.5 | 208.6448 | 1086.4865 | 63.1064 | 5.2074 | 0.89906 | 109.5391 | 109.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7868 | 55.1264 | 74.5178
CID=-1888991293 | -9 | 45 | 69.5049 | 4 | 39 | 7.8 | 1.7455 | 148.4312 | 10.2212 | 254.9187 | 433.2489 | 396.6938 | 35552.8119 | 1.0155 | 0.031284 | 2.2149 | 65.0043 | 143.9788 | -9 | 45 | 4 | 39 | 208.6448 | 1159.9242 | 74.7802 | 5.5593 | 0.89922 | 98.353 | 109.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.4822 | 74.5276
CID=-1888991262 | -9 | 47.5 | 71.2749 | 4 | 41.5 | 8.3 | 1.7455 | 148.4312 | 10.2212 | 258.655 | 434.6398 | 396.6938 | 36119.6991 | 1.3082 | 0.034478 | 2.5514 | 70.7774 | 180.5813 | -9 | 47.5 | 4 | 41.5 | 208.6448 | 1237.0237 | 67.9309 | 5.9289 | 0.90379 | 109.5196 | 118.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.7723 | 70.7774
CID=1130157182 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157213 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157244 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157275 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157306 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157337 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157368 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157399 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130156934 | -9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130156965 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083080935 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083080904 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083080873 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083080842 | -6 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083080811 | -6 | 7.5 | 11.4566 | 4 | 1.5 | 0.3 | 1.7436 | 148.523 | 11.416 | 202.0183 | 408.6791 | 398.5385 | 21126.9806 | 0.60361 | 0.0075188 | 10.354 | 11.4566 | 118.6213 | -6 | 7.5 | 4 | 1.5 | 234.2779 | 381.0767 | 20.4645 | 1.6266 | 0.71225 | 110 | 24.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.453 | 16.4601
CID=-2083080780 | -6 | 10 | 14.2437 | 4 | 4 | 0.8 | 1.7436 | 148.523 | 11.416 | 205.396 | 410.4654 | 398.5385 | 22561.483 | 0.67161 | 0.0083879 | 9.1069 | 14.2437 | 129.7163 | -6 | 10 | 4 | 4 | 234.2779 | 414.6075 | 23.7048 | 1.7697 | 0.73572 | 110 | 29.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.6696 | 20.8178
CID=-2083080749 | -6 | 12.5 | 17.4425 | 4 | 6.5 | 1.3 | 1.7436 | 148.523 | 11.416 | 208.7918 | 412.2236 | 398.5385 | 23930.1179 | 0.74573 | 0.0094328 | 8.1123 | 17.4425 | 141.4989 | -6 | 12.5 | 4 | 6.5 | 234.2779 | 450.3422 | 26.8663 | 1.9223 | 0.7594 | 110 | 34.8975 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2176 | 25.6674
CID=-2083080718 | -6 | 15 | 20.9098 | 4 | 9 | 1.8 | 1.7436 | 148.523 | 11.416 | 212.2062 | 413.9537 | 398.5385 | 25209.4686 | 0.82042 | 0.010614 | 7.311 | 20.9098 | 152.8713 | -6 | 15 | 4 | 9 | 234.2779 | 488.3739 | 29.9119 | 2.0846 | 0.78164 | 110 | 40.644 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7286 | 31.091
CID=-2083081183 | -6 | 17.5 | 24.2295 | 4 | 11.5 | 2.3 | 1.7436 | 148.523 | 11.416 | 215.6398 | 415.6561 | 398.5385 | 26270.5593 | 0.88164 | 0.011808 | 6.6552 | 24.2295 | 161.2515 | -6 | 17.5 | 4 | 11.5 | 234.2779 | 528.7968 | 32.8214 | 2.2571 | 0.80005 | 110 | 46.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.814 | 35.6449
CID=-2083081152 | -6 | 20 | 28.6695 | 4 | 14 | 2.8 | 1.7436 | 148.523 | 11.416 | 219.0933 | 417.3308 | 398.5385 | 27456.5249 | 0.96417 | 0.013401 | 6.0348 | 28.6695 | 173.0148 | -6 | 20 | 4 | 14 | 234.2779 | 571.7069 | 35.991 | 2.4403 | 0.8209 | 110 | 53.0624 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1569 | 42.1821
CID=1194057043 | -6 | 22.5 | 33.3413 | 4 | 16.5 | 3.3 | 1.7436 | 148.523 | 11.416 | 222.5675 | 418.9782 | 398.5385 | 28596.9671 | 1.0416 | 0.01514 | 5.4976 | 33.3413 | 183.2954 | -6 | 22.5 | 4 | 16.5 | 234.2779 | 617.2019 | 39.158 | 2.6345 | 0.83893 | 110 | 60.3824 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.5255 | 49.1571
CID=1194057140 | -6 | 25 | 38.5621 | 4 | 19 | 3.8 | 1.7436 | 148.523 | 11.416 | 226.0633 | 420.5983 | 398.5385 | 29697.5755 | 1.1221 | 0.017133 | 5.0189 | 38.5621 | 193.5383 | -6 | 25 | 4 | 19 | 234.2779 | 665.3809 | 42.3909 | 2.8401 | 0.85523 | 110 | 68.5064 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3432 | 56.7809
CID=1194057237 | -6 | 27.5 | 42.7255 | 4 | 21.5 | 4.3 | 1.7436 | 148.523 | 11.416 | 229.5813 | 422.1916 | 398.5385 | 30468.5725 | 1.1767 | 0.018866 | 4.6533 | 42.7255 | 198.815 | -6 | 27.5 | 4 | 21.5 | 234.2779 | 716.3449 | 45.2138 | 3.0577 | 0.86585 | 110 | 74.9722 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3062 | 62.1448
CID=1194057078 | -6 | 30 | 48.2015 | 4 | 24 | 4.8 | 1.7436 | 148.523 | 11.416 | 233.1226 | 423.758 | 398.5385 | 31369.0012 | 1.25 | 0.021121 | 4.2897 | 48.2015 | 206.7701 | -6 | 30 | 4 | 24 | 234.2779 | 770.1963 | 48.3304 | 3.2875 | 0.87721 | 110 | 83.4858 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4924 | 69.9107
CID=1194057167 | -6 | 32.5 | 53.7558 | 4 | 26.5 | 5.3 | 1.7436 | 148.523 | 11.416 | 236.688 | 425.298 | 398.5385 | 32209.1829 | 1.3167 | 0.023508 | 3.9645 | 53.7558 | 213.1147 | -6 | 32.5 | 4 | 26.5 | 234.2779 | 827.0396 | 51.4472 | 3.5302 | 0.8863 | 110 | 92.1508 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2611 | 77.2504
CID=1194057264 | -6 | 35 | 58.3652 | 4 | 29 | 5.8 | 1.7436 | 148.523 | 11.416 | 240.2788 | 426.8116 | 398.5385 | 32865.7233 | 1.3663 | 0.025673 | 3.7047 | 58.3652 | 216.2256 | -6 | 35 | 4 | 29 | 234.2779 | 886.981 | 54.223 | 3.786 | 0.89236 | 110 | 99.3732 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.2819 | 82.4485
CID=1194057361 | -6 | 37.5 | 61.0313 | 4 | 31.5 | 6.3 | 1.7436 | 148.523 | 11.416 | 243.8959 | 428.2991 | 398.5385 | 33301.6723 | 1.3836 | 0.02724 | 3.5058 | 61.0313 | 213.9608 | -6 | 37.5 | 4 | 31.5 | 234.2779 | 950.1287 | 56.5524 | 4.0556 | 0.89535 | 110 | 103.5651 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.1102 | 82.9524
CID=1194057202 | -6 | 40 | 63.0092 | 4 | 34 | 6.8 | 1.7436 | 148.523 | 11.416 | 247.5407 | 429.7609 | 398.5385 | 33706.7856 | 1.3762 | 0.028632 | 3.2979 | 63.0092 | 207.7993 | -6 | 40 | 4 | 34 | 234.2779 | 1016.593 | 59.1318 | 4.3393 | 0.89736 | 110 | 106.682 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.5036 | 82.5148
CID=1194056795 | -6 | 42.5 | 65.61 | 4 | 36.5 | 7.3 | 1.7436 | 148.523 | 11.416 | 251.2145 | 431.197 | 398.5385 | 34180.7615 | 1.3795 | 0.030337 | 3.0975 | 65.61 | 203.2301 | -6 | 42.5 | 4 | 36.5 | 234.2779 | 1086.4865 | 61.8148 | 4.6376 | 0.89976 | 110 | 110.7898 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.8837 | 81.3364
CID=1194056892 | -6 | 45 | 69.4042 | 4 | 39 | 7.8 | 1.7436 | 148.523 | 11.416 | 254.9187 | 432.6077 | 398.5385 | 34744.4177 | 1.3997 | 0.032601 | 2.8964 | 69.4042 | 201.0242 | -6 | 45 | 4 | 39 | 234.2779 | 1159.9242 | 64.7228 | 4.9511 | 0.90281 | 110 | 116.8012 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.269 | 82.5395
CID=-2019181074 | -6 | 47.5 | 73.0685 | 4 | 41.5 | 8.3 | 1.7436 | 148.523 | 11.416 | 258.655 | 433.9933 | 398.5385 | 35263.0786 | 1.4141 | 0.034942 | 2.7071 | 73.0685 | 197.8044 | -6 | 47.5 | 4 | 41.5 | 234.2779 | 1237.0237 | 67.6841 | 5.2802 | 0.90531 | 109.322 | 122.6273 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1967 | 82.9402
CID=-2019180977 | -6 | 50 | 78.0408 | 4 | 44 | 8.8 | 1.7436 | 148.523 | 11.416 | 262.425 | 435.3541 | 398.5385 | 35722.2242 | 1.1082 | 0.036298 | 2.0381 | 74.0091 | 150.8396 | -6 | 50 | 4 | 44 | 234.2779 | 1317.9055 | 81.0313 | 5.6254 | 0.90589 | 95.8314 | 124.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.7545 | 82.3271
CID=-2019180880 | -6 | 52.5 | 80.4617 | 4 | 46.5 | 9.3 | 1.7436 | 148.523 | 11.416 | 266.2308 | 436.6902 | 398.5385 | 36189.9086 | 1.461 | 0.039595 | 2.437 | 79.3179 | 193.2958 | -6 | 52.5 | 4 | 46.5 | 234.2779 | 1402.6932 | 72.3832 | 5.9873 | 0.90877 | 109.5619 | 132.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 81.6054 | 79.3179
CID=-2019181039 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180950 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180853 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180756 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180915 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019181322 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019181225 | -6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197513 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197610 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197707 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197548 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197637 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197734 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356197831 | -3 | 10 | 12.1349 | 4 | 4 | 0.8 | 1.7418 | 148.5658 | 12.7186 | 205.396 | 409.9411 | 400.3675 | 20823.4985 | 0.66226 | 0.0077527 | 10.6405 | 12.1349 | 129.1217 | -3 | 10 | 4 | 4 | 262.283 | 414.6075 | 22.7548 | 1.5808 | 0.71823 | 110 | 25.6703 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2395 | 17.0303
CID=1356197672 | -3 | 12.5 | 14.6156 | 4 | 6.5 | 1.3 | 1.7418 | 148.5658 | 12.7186 | 208.7918 | 411.6941 | 400.3675 | 22066.1262 | 0.71993 | 0.0085581 | 9.4366 | 14.6156 | 137.9213 | -3 | 12.5 | 4 | 6.5 | 262.283 | 450.3422 | 25.7057 | 1.717 | 0.73864 | 110 | 30.0635 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8059 | 21.4254
CID=1356197265 | -3 | 15 | 18.0158 | 4 | 9 | 1.8 | 1.7418 | 148.5658 | 12.7186 | 212.2062 | 413.4192 | 400.3675 | 23442.5766 | 0.80255 | 0.0096762 | 8.382 | 18.0158 | 151.0085 | -3 | 15 | 4 | 9 | 262.283 | 488.3739 | 28.8412 | 1.862 | 0.76331 | 110 | 35.8598 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5793 | 26.4523
CID=1356197362 | -3 | 17.5 | 21.7408 | 4 | 11.5 | 2.3 | 1.7418 | 148.5658 | 12.7186 | 215.6398 | 415.1165 | 400.3675 | 24744.635 | 0.88484 | 0.010952 | 7.5183 | 21.7408 | 163.4546 | -3 | 17.5 | 4 | 11.5 | 262.283 | 528.7968 | 31.9211 | 2.0161 | 0.7865 | 110 | 41.9984 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.3834 | 32.0983
CID=-1857040604 | -3 | 20 | 24.983 | 4 | 14 | 2.8 | 1.7418 | 148.5658 | 12.7186 | 219.0933 | 416.7863 | 400.3675 | 25753.9014 | 0.94514 | 0.012142 | 6.8579 | 24.983 | 171.3298 | -3 | 20 | 4 | 14 | 262.283 | 571.7069 | 34.7089 | 2.1797 | 0.80387 | 110 | 47.2185 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.1276 | 36.8384
CID=-1857040507 | -3 | 22.5 | 29.4535 | 4 | 16.5 | 3.3 | 1.7418 | 148.5658 | 12.7186 | 222.5675 | 418.4287 | 400.3675 | 26916.4411 | 1.0288 | 0.01377 | 6.2104 | 29.4535 | 182.9191 | -3 | 22.5 | 4 | 16.5 | 262.283 | 617.2019 | 37.8309 | 2.3532 | 0.82418 | 110 | 54.2962 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3536 | 43.5534
CID=-1857040410 | -3 | 25 | 34.6728 | 4 | 19 | 3.8 | 1.7418 | 148.5658 | 12.7186 | 226.0633 | 420.0439 | 400.3675 | 28102.3373 | 1.1213 | 0.01571 | 5.6369 | 34.6728 | 195.4458 | -3 | 25 | 4 | 19 | 262.283 | 665.3809 | 41.0362 | 2.5369 | 0.84344 | 110 | 62.4581 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2962 | 51.0495
CID=-1857040569 | -3 | 27.5 | 39.9329 | 4 | 21.5 | 4.3 | 1.7418 | 148.5658 | 12.7186 | 229.5813 | 421.6322 | 400.3675 | 29164.6865 | 1.2066 | 0.017751 | 5.1603 | 39.9329 | 206.0666 | -3 | 27.5 | 4 | 21.5 | 262.283 | 716.3449 | 44.1124 | 2.7312 | 0.85894 | 110 | 70.6355 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.9887 | 58.877
CID=-1857040480 | -3 | 30 | 44.7583 | 4 | 24 | 4.8 | 1.7418 | 148.5658 | 12.7186 | 233.1226 | 423.1938 | 400.3675 | 30024.586 | 1.2743 | 0.019738 | 4.7617 | 44.7583 | 213.1235 | -3 | 30 | 4 | 24 | 262.283 | 770.1963 | 47.0381 | 2.9365 | 0.87038 | 110 | 78.1303 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0589 | 65.4577
CID=-1857040383 | -3 | 32.5 | 50.1408 | 4 | 26.5 | 5.3 | 1.7418 | 148.5658 | 12.7186 | 236.688 | 424.7289 | 400.3675 | 30870.539 | 1.3473 | 0.022008 | 4.3983 | 50.1408 | 220.5333 | -3 | 32.5 | 4 | 26.5 | 262.283 | 827.0396 | 50.0235 | 3.1532 | 0.88063 | 110 | 86.507 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.3282 | 72.9534
CID=-1857040286 | -3 | 35 | 56.2593 | 4 | 29 | 5.8 | 1.7418 | 148.5658 | 12.7186 | 240.2788 | 426.2376 | 400.3675 | 31747.4436 | 1.4234 | 0.024643 | 4.0503 | 56.2593 | 227.8679 | -3 | 35 | 4 | 29 | 262.283 | 886.981 | 53.203 | 3.3818 | 0.88974 | 110 | 96.0697 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.2318 | 81.2868
CID=-1857040445 | -3 | 37.5 | 62.3387 | 4 | 31.5 | 6.3 | 1.7418 | 148.5658 | 12.7186 | 243.8959 | 427.7203 | 400.3675 | 32524.7328 | 1.4981 | 0.027391 | 3.7603 | 62.3387 | 234.4109 | -3 | 37.5 | 4 | 31.5 | 262.283 | 950.1287 | 56.1804 | 3.6225 | 0.8967 | 110 | 105.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.4207 | 89.2568
CID=-1857040852 | -3 | 40 | 65.8319 | 4 | 34 | 6.8 | 1.7418 | 148.5658 | 12.7186 | 247.5407 | 429.1772 | 400.3675 | 33007.7236 | 1.5267 | 0.029326 | 3.5442 | 65.8318 | 233.3233 | -3 | 40 | 4 | 34 | 262.283 | 1016.593 | 58.6422 | 3.8759 | 0.89995 | 110 | 111.1406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.004 | 91.6597
CID=-1857040755 | -3 | 42.5 | 68.4112 | 4 | 36.5 | 7.3 | 1.7418 | 148.5658 | 12.7186 | 251.2145 | 430.6085 | 400.3675 | 33414.6697 | 1.5347 | 0.031018 | 3.3461 | 68.4112 | 228.9098 | -3 | 42.5 | 4 | 36.5 | 262.283 | 1086.4865 | 61.0683 | 4.1424 | 0.90206 | 110 | 115.2257 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.8066 | 92.0158
CID=1162107623 | -3 | 45 | 70.9477 | 4 | 39 | 7.8 | 1.7418 | 148.5658 | 12.7186 | 254.9187 | 432.0144 | 400.3675 | 33840.5126 | 1.5342 | 0.032787 | 3.1452 | 70.9477 | 223.1476 | -3 | 45 | 4 | 39 | 262.283 | 1159.9242 | 63.6878 | 4.4224 | 0.90391 | 110 | 119.253 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.0122 | 91.8833
CID=1162107720 | -3 | 47.5 | 74.1798 | 4 | 41.5 | 8.3 | 1.7418 | 148.5658 | 12.7186 | 258.655 | 433.3951 | 400.3675 | 34339.2369 | 1.5446 | 0.034931 | 2.9507 | 74.1798 | 218.8845 | -3 | 47.5 | 4 | 41.5 | 262.283 | 1237.0237 | 66.4179 | 4.7164 | 0.906 | 110 | 124.3982 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57.2677 | 91.0918
CID=1162107817 | -3 | 50 | 78.2803 | 4 | 44 | 8.8 | 1.7418 | 148.5658 | 12.7186 | 262.425 | 434.7511 | 400.3675 | 34871.6532 | 1.5666 | 0.037555 | 2.7606 | 78.2803 | 216.1045 | -3 | 50 | 4 | 44 | 262.283 | 1317.9055 | 69.2912 | 5.0247 | 0.90826 | 110 | 130.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64.1843 | 92.3763
CID=1162107658 | -3 | 52.5 | 82.4593 | 4 | 46.5 | 9.3 | 1.7418 | 148.5658 | 12.7186 | 266.2308 | 436.0824 | 400.3675 | 35384.1185 | 1.5849 | 0.04037 | 2.5781 | 82.4593 | 212.5883 | -3 | 52.5 | 4 | 46.5 | 262.283 | 1402.6932 | 72.2648 | 5.348 | 0.91019 | 109.2998 | 137.6456 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8396 | 72.1709 | 92.7477
CID=1162107747 | -3 | 55 | 87.9096 | 4 | 49 | 9.8 | 1.7418 | 148.5658 | 12.7186 | 270.0745 | 437.3893 | 400.3675 | 35839.1471 | 1.2333 | 0.042163 | 1.9162 | 83.8581 | 160.6883 | -3 | 55 | 4 | 49 | 262.283 | 1491.5141 | 86.0361 | 5.6867 | 0.91076 | 95.4659 | 139.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.791 | 92.0281
CID=1162107844 | -3 | 57.5 | 90.3708 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162107941 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162107782 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162107375 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162107472 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130494 | -3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130397 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130300 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130459 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130370 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130273 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130176 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130335 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051130742 | 0 | 12.5 | 11.5897 | 4 | 6.5 | 1.3 | 1.7401 | 148.5582 | 14.1363 | 208.7918 | 411.2041 | 402.1796 | 19957.5051 | 0.6791 | 0.0076748 | 11.3316 | 11.5897 | 131.3297 | 0 | 12.5 | 4 | 6.5 | 292.8032 | 450.3422 | 24.3331 | 1.538 | 0.71344 | 110 | 24.6814 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.6527 | 15.5267
CID=-2051130645 | 0 | 15 | 14.9072 | 4 | 9 | 1.8 | 1.7401 | 148.5582 | 14.1363 | 212.2062 | 412.9246 | 402.1796 | 21556.8695 | 0.76821 | 0.008711 | 9.7898 | 14.9072 | 145.939 | 0 | 15 | 4 | 9 | 292.8032 | 488.3739 | 27.7118 | 1.6679 | 0.7409 | 110 | 30.5698 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8476 | 21.9668
CID=1324248093 | 0 | 17.5 | 18.425 | 4 | 11.5 | 2.3 | 1.7401 | 148.5582 | 14.1363 | 215.6398 | 414.6172 | 402.1796 | 22934.2154 | 0.85417 | 0.0098787 | 8.6479 | 18.4251 | 159.3375 | 0 | 17.5 | 4 | 11.5 | 292.8032 | 528.7968 | 30.868 | 1.806 | 0.76604 | 110 | 36.5436 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6303 | 27.2198
CID=1324248190 | 0 | 20 | 22.3101 | 4 | 14 | 2.8 | 1.7401 | 148.5582 | 14.1363 | 219.0933 | 416.2824 | 402.1796 | 24231.369 | 0.94421 | 0.01122 | 7.7486 | 22.3101 | 172.8723 | 0 | 20 | 4 | 14 | 292.8032 | 571.7069 | 33.8973 | 1.9525 | 0.78973 | 110 | 42.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4976 | 33.1226
CID=1324248287 | 0 | 22.5 | 26.6791 | 4 | 16.5 | 3.3 | 1.7401 | 148.5582 | 14.1363 | 222.5675 | 417.9202 | 402.1796 | 25469.9455 | 1.0382 | 0.012776 | 6.9893 | 26.6791 | 186.4672 | 0 | 22.5 | 4 | 16.5 | 292.8032 | 617.2019 | 36.9234 | 2.1079 | 0.81204 | 110 | 49.917 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.7099 | 39.6483
CID=1324248128 | 0 | 25 | 30.5188 | 4 | 19 | 3.8 | 1.7401 | 148.5582 | 14.1363 | 226.0633 | 419.5308 | 402.1796 | 26440.5156 | 1.1059 | 0.014237 | 6.3821 | 30.5188 | 194.7732 | 0 | 25 | 4 | 19 | 292.8032 | 665.3809 | 39.755 | 2.2725 | 0.82847 | 110 | 55.9687 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0491 | 44.9885
CID=1324248217 | 0 | 27.5 | 35.7415 | 4 | 21.5 | 4.3 | 1.7401 | 148.5582 | 14.1363 | 229.5813 | 421.1145 | 402.1796 | 27550.1203 | 1.2021 | 0.01621 | 5.8049 | 35.7415 | 207.475 | 0 | 27.5 | 4 | 21.5 | 292.8032 | 716.3449 | 42.8269 | 2.4465 | 0.84688 | 110 | 64.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.7183 | 52.7648
CID=1324248314 | 0 | 30 | 41.2857 | 4 | 24 | 4.8 | 1.7401 | 148.5582 | 14.1363 | 233.1226 | 422.6716 | 402.1796 | 28634.7988 | 1.2934 | 0.018379 | 5.2964 | 41.2857 | 218.6653 | 0 | 30 | 4 | 24 | 292.8032 | 770.1963 | 45.9309 | 2.6304 | 0.86239 | 110 | 72.7363 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.6284 | 60.943
CID=1324248411 | 0 | 32.5 | 47.4002 | 4 | 26.5 | 5.3 | 1.7401 | 148.5582 | 14.1363 | 236.688 | 424.2021 | 402.1796 | 29675.1864 | 1.3876 | 0.02084 | 4.8447 | 47.4002 | 229.6409 | 0 | 32.5 | 4 | 26.5 | 292.8032 | 827.0396 | 49.0776 | 2.8246 | 0.87571 | 110 | 82.2385 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9262 | 69.8742
CID=1324248252 | 0 | 35 | 52.1086 | 4 | 29 | 5.8 | 1.7401 | 148.5582 | 14.1363 | 240.2788 | 425.7063 | 402.1796 | 30385.8835 | 1.4487 | 0.022931 | 4.5011 | 52.1086 | 234.5481 | 0 | 35 | 4 | 29 | 292.8032 | 886.981 | 51.8226 | 3.0293 | 0.88383 | 110 | 89.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2143 | 76.0029
CID=1324247845 | 0 | 37.5 | 58.5209 | 4 | 31.5 | 6.3 | 1.7401 | 148.5582 | 14.1363 | 243.8959 | 427.1845 | 402.1796 | 31246.2985 | 1.5358 | 0.025725 | 4.154 | 58.5209 | 243.0945 | 0 | 37.5 | 4 | 31.5 | 292.8032 | 950.1287 | 54.8694 | 3.2449 | 0.89255 | 110 | 99.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0433 | 84.9985
CID=1324247942 | 0 | 40 | 65.0419 | 4 | 34 | 6.8 | 1.7401 | 148.5582 | 14.1363 | 247.5407 | 428.6369 | 402.1796 | 32057.8136 | 1.6138 | 0.028696 | 3.8369 | 65.0419 | 249.5599 | 0 | 40 | 4 | 34 | 292.8032 | 1016.593 | 57.9658 | 3.4719 | 0.89926 | 110 | 109.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5584 | 93.5253
CID=-1888990024 | 0 | 42.5 | 71.2674 | 4 | 36.5 | 7.3 | 1.7401 | 148.5582 | 14.1363 | 251.2145 | 430.0637 | 402.1796 | 32760.9452 | 1.6867 | 0.031708 | 3.5729 | 71.2674 | 254.6328 | 0 | 42.5 | 4 | 36.5 | 292.8032 | 1086.4865 | 60.8468 | 3.7106 | 0.90413 | 110 | 119.7612 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6283 | 101.9065
CID=-1888989927 | 0 | 45 | 74.0045 | 4 | 39 | 7.8 | 1.7401 | 148.5582 | 14.1363 | 254.9187 | 431.4651 | 402.1796 | 33132.3262 | 1.7022 | 0.033548 | 3.3872 | 74.0045 | 250.6672 | 0 | 45 | 4 | 39 | 292.8032 | 1159.9242 | 63.1077 | 3.9614 | 0.90589 | 110 | 124.1187 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.0942 | 101.9148
CID=-1888989830 | 0 | 47.5 | 76.1485 | 4 | 41.5 | 8.3 | 1.7401 | 148.5582 | 14.1363 | 258.655 | 432.8414 | 402.1796 | 33491.4543 | 1.6935 | 0.03526 | 3.1918 | 76.1485 | 243.0527 | 0 | 47.5 | 4 | 41.5 | 292.8032 | 1237.0237 | 65.606 | 4.2248 | 0.90713 | 110 | 127.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.0502 | 101.2467
CID=-1888989989 | 0 | 50 | 79.8139 | 4 | 44 | 8.8 | 1.7401 | 148.5582 | 14.1363 | 262.425 | 434.1928 | 402.1796 | 33977.2277 | 1.71 | 0.037684 | 2.9943 | 79.8139 | 238.9858 | 0 | 50 | 4 | 44 | 292.8032 | 1317.9055 | 68.3059 | 4.501 | 0.90901 | 110 | 133.4029 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57.491 | 102.1367
CID=-1888989900 | 0 | 52.5 | 83.4802 | 4 | 46.5 | 9.3 | 1.7401 | 148.5582 | 14.1363 | 266.2308 | 435.5196 | 402.1796 | 34470.1351 | 1.7228 | 0.040253 | 2.8056 | 83.4801 | 234.2123 | 0 | 52.5 | 4 | 46.5 | 292.8032 | 1402.6932 | 71.0765 | 4.7906 | 0.91061 | 110 | 139.2852 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.2952 | 101.6651
CID=-1888989803 | 0 | 55 | 87.4083 | 4 | 49 | 9.8 | 1.7401 | 148.5582 | 14.1363 | 270.0745 | 436.822 | 402.1796 | 34945.6885 | 1.7376 | 0.043094 | 2.6262 | 87.4084 | 229.5507 | 0 | 55 | 4 | 49 | 292.8032 | 1491.5141 | 73.9084 | 5.0939 | 0.91207 | 109.8632 | 145.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1397 | 72.7779 | 102.0387
CID=-1888989706 | 0 | 57.5 | 92.3089 | 4 | 51.5 | 10.3 | 1.7401 | 148.5582 | 14.1363 | 273.9586 | 438.1003 | 402.1796 | 35461.1279 | 1.7651 | 0.046547 | 2.4518 | 92.3089 | 226.322 | 0 | 57.5 | 4 | 51.5 | 292.8032 | 1584.4992 | 76.8654 | 5.4115 | 0.91358 | 109.226 | 153.5159 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82.0777 | 102.54
CID=-1888989865 | 0 | 60 | 97.5305 | 4 | 54 | 10.8 | 1.7401 | 148.5582 | 14.1363 | 277.8855 | 439.3549 | 402.1796 | 35914.8119 | 1.3827 | 0.048861 | 1.8249 | 94.1757 | 171.8647 | 0 | 60 | 4 | 54 | 292.8032 | 1681.7842 | 90.2399 | 5.7437 | 0.91407 | 95.3496 | 156.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.1756 | 100.8854
CID=-1888990272 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888990175 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158203 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158300 | 0 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158397 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158238 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158327 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158424 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158521 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158362 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130157955 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130158052 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083079914 | 3 | 15 | 9.7953 | 4 | 9 | 1.8 | 1.7385 | 148.4988 | 15.6766 | 212.2062 | 412.4664 | 403.9734 | 19535.1304 | 0.63543 | 0.0072873 | 12.4402 | 9.7953 | 121.855 | 3 | 15 | 4 | 9 | 325.9849 | 488.3739 | 25.3946 | 1.4981 | 0.69687 | 83.0346 | 21.356 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.4251 | 11.1654
CID=-2083079817 | 3 | 17.5 | 15.5154 | 4 | 11.5 | 2.3 | 1.7385 | 148.4988 | 15.6766 | 215.6398 | 414.1547 | 403.9734 | 21178.0838 | 0.83415 | 0.0089574 | 10.1253 | 15.5154 | 157.0989 | 3 | 17.5 | 4 | 11.5 | 325.9849 | 528.7968 | 29.8288 | 1.6222 | 0.74552 | 110 | 31.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.626 | 22.4048
CID=-2083079720 | 3 | 20 | 19.0191 | 4 | 14 | 2.8 | 1.7385 | 148.4988 | 15.6766 | 219.0933 | 415.8156 | 403.9734 | 22492.5587 | 0.9188 | 0.010141 | 8.9315 | 19.0191 | 169.8687 | 3 | 20 | 4 | 14 | 325.9849 | 571.7069 | 32.9154 | 1.7538 | 0.76993 | 110 | 37.5315 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0707 | 27.9674
CID=-2083079879 | 3 | 22.5 | 23.1031 | 4 | 16.5 | 3.3 | 1.7385 | 148.4988 | 15.6766 | 222.5675 | 417.4491 | 403.9734 | 23773.7924 | 1.0146 | 0.011564 | 7.9669 | 23.1031 | 184.0587 | 3 | 22.5 | 4 | 16.5 | 325.9849 | 617.2019 | 35.9647 | 1.8933 | 0.7941 | 110 | 44.203 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1238 | 34.0823
CID=-2083079790 | 3 | 25 | 27.473 | 4 | 19 | 3.8 | 1.7385 | 148.4988 | 15.6766 | 226.0633 | 419.0555 | 403.9734 | 24971.7928 | 1.1092 | 0.013145 | 7.1827 | 27.4729 | 197.3296 | 3 | 25 | 4 | 19 | 325.9849 | 665.3809 | 38.9305 | 2.0411 | 0.81566 | 110 | 51.174 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0916 | 40.8543
CID=-2083079693 | 3 | 27.5 | 31.2877 | 4 | 21.5 | 4.3 | 1.7385 | 148.4988 | 15.6766 | 229.5813 | 420.635 | 403.9734 | 25911.0411 | 1.1788 | 0.014622 | 6.5702 | 31.2877 | 205.5665 | 3 | 27.5 | 4 | 21.5 | 325.9849 | 716.3449 | 41.6634 | 2.1975 | 0.83145 | 110 | 57.1734 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.1927 | 46.3828
CID=-2083079596 | 3 | 30 | 36.7524 | 4 | 24 | 4.8 | 1.7385 | 148.4988 | 15.6766 | 233.1226 | 422.1878 | 403.9734 | 27033.633 | 1.2816 | 0.016705 | 5.9579 | 36.7524 | 218.9657 | 3 | 30 | 4 | 24 | 325.9849 | 770.1963 | 44.7471 | 2.3627 | 0.84999 | 110 | 65.694 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.1571 | 54.3477
CID=-2083079755 | 3 | 32.5 | 42.7785 | 4 | 26.5 | 5.3 | 1.7385 | 148.4988 | 15.6766 | 236.688 | 423.7141 | 403.9734 | 28143.564 | 1.3865 | 0.019072 | 5.4219 | 42.7785 | 231.9394 | 3 | 32.5 | 4 | 26.5 | 325.9849 | 827.0396 | 47.8629 | 2.537 | 0.86597 | 110 | 75.0545 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.4325 | 63.1245
CID=-2083080162 | 3 | 35 | 48.9321 | 4 | 29 | 5.8 | 1.7385 | 148.4988 | 15.6766 | 240.2788 | 425.2142 | 403.9734 | 29147.6359 | 1.4864 | 0.021593 | 4.9724 | 48.9321 | 243.3077 | 3 | 35 | 4 | 29 | 325.9849 | 886.981 | 50.8723 | 2.7209 | 0.87853 | 110 | 84.6234 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6165 | 72.2476
CID=-2083080065 | 3 | 37.5 | 54.711 | 4 | 31.5 | 6.3 | 1.7385 | 148.4988 | 15.6766 | 243.8959 | 426.6882 | 403.9734 | 29982.1617 | 1.5685 | 0.024102 | 4.5893 | 54.711 | 251.0857 | 3 | 37.5 | 4 | 31.5 | 325.9849 | 950.1287 | 53.7794 | 2.9146 | 0.88766 | 110 | 93.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.0856 | 80.3364
CID=1194053844 | 3 | 40 | 60.6836 | 4 | 34 | 6.8 | 1.7385 | 148.4988 | 15.6766 | 247.5407 | 428.1364 | 403.9734 | 30755.7561 | 1.6483 | 0.026804 | 4.249 | 60.6836 | 257.8443 | 3 | 40 | 4 | 34 | 325.9849 | 1016.593 | 56.6684 | 3.1185 | 0.89498 | 110 | 103.0178 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.953 | 88.4142
CID=1194053875 | 3 | 42.5 | 67.964 | 4 | 36.5 | 7.3 | 1.7385 | 148.4988 | 15.6766 | 251.2145 | 429.559 | 403.9734 | 31602.42 | 1.7422 | 0.030122 | 3.9158 | 67.964 | 266.1317 | 3 | 42.5 | 4 | 36.5 | 325.9849 | 1086.4865 | 59.7858 | 3.3329 | 0.90171 | 110 | 114.5168 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.6354 | 98.2926
CID=1194054038 | 3 | 45 | 74.6385 | 4 | 39 | 7.8 | 1.7385 | 148.4988 | 15.6766 | 254.9187 | 430.9562 | 403.9734 | 32323.3054 | 1.8217 | 0.033383 | 3.6379 | 74.6385 | 271.5287 | 3 | 45 | 4 | 39 | 325.9849 | 1159.9242 | 62.7017 | 3.5582 | 0.90627 | 110 | 125.1297 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9298 | 107.3472
CID=1194054069 | 3 | 47.5 | 79.9898 | 4 | 41.5 | 8.3 | 1.7385 | 148.4988 | 15.6766 | 258.655 | 432.3283 | 403.9734 | 32884.33 | 1.8761 | 0.036309 | 3.4083 | 79.9897 | 272.6255 | 3 | 47.5 | 4 | 41.5 | 325.9849 | 1237.0237 | 65.3714 | 3.7947 | 0.90909 | 110 | 133.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.1667 | 112.8128
CID=1194053968 | 3 | 50 | 83.3172 | 4 | 44 | 8.8 | 1.7385 | 148.4988 | 15.6766 | 262.425 | 433.6755 | 403.9734 | 33279.2984 | 1.8979 | 0.038596 | 3.2243 | 83.3173 | 268.6438 | 3 | 50 | 4 | 44 | 325.9849 | 1317.9055 | 67.7203 | 4.0428 | 0.91055 | 110 | 139.0235 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1496 | 113.4849
CID=1194053999 | 3 | 52.5 | 85.5018 | 4 | 46.5 | 9.3 | 1.7385 | 148.4988 | 15.6766 | 266.2308 | 434.9982 | 403.9734 | 33626.1626 | 1.8833 | 0.040553 | 3.0341 | 85.5018 | 259.4169 | 3 | 52.5 | 4 | 46.5 | 325.9849 | 1402.6932 | 70.2731 | 4.3029 | 0.91139 | 110 | 142.536 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.3888 | 112.6148
CID=1194054162 | 3 | 55 | 89.0999 | 4 | 49 | 9.8 | 1.7385 | 148.4988 | 15.6766 | 270.0745 | 436.2964 | 403.9734 | 34073.0592 | 1.8947 | 0.043227 | 2.8473 | 89.0999 | 253.6959 | 3 | 55 | 4 | 49 | 325.9849 | 1491.5141 | 72.951 | 4.5754 | 0.91263 | 110 | 148.3334 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.8924 | 112.3073
CID=1194054193 | 3 | 57.5 | 93.5201 | 4 | 51.5 | 10.3 | 1.7385 | 148.4988 | 15.6766 | 273.9586 | 437.5705 | 403.9734 | 34575.1029 | 1.9155 | 0.046428 | 2.6629 | 93.5201 | 249.0389 | 3 | 57.5 | 4 | 51.5 | 325.9849 | 1584.4992 | 75.7764 | 4.8607 | 0.9139 | 110 | 155.4748 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73.9935 | 113.0467
CID=1194053596 | 3 | 60 | 97.722 | 4 | 54 | 10.8 | 1.7385 | 148.4988 | 15.6766 | 277.8855 | 438.8208 | 403.9734 | 35025.094 | 1.9321 | 0.049746 | 2.4929 | 97.722 | 243.6082 | 3 | 60 | 4 | 54 | 325.9849 | 1681.7842 | 78.5788 | 5.1591 | 0.91491 | 109.846 | 162.2814 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2784 | 82.0539 | 113.39
CID=1194053627 | 3 | 62.5 | 103.3332 | 4 | 56.5 | 11.3 | 1.7385 | 148.4988 | 15.6766 | 281.8586 | 440.0476 | 403.9734 | 35534.8935 | 1.9691 | 0.053946 | 2.327 | 103.3332 | 240.4531 | 3 | 62.5 | 4 | 56.5 | 325.9849 | 1783.5096 | 81.5023 | 5.4711 | 0.916 | 109.228 | 171.3953 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.802 | 113.8644
CID=-2019184273 | 3 | 65 | 108.5153 | 4 | 59 | 11.8 | 1.7385 | 148.4988 | 15.6766 | 285.881 | 441.2512 | 403.9734 | 36002.9716 | 2.0086 | 0.058249 | 2.1859 | 108.5153 | 237.1983 | 3 | 65 | 4 | 59 | 325.9849 | 1889.8218 | 84.1758 | 5.7973 | 0.9168 | 108.9811 | 179.8339 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 105.0584 | 111.9723
CID=-2019184242 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019184079 | 3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019184048 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019184149 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019184118 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019183955 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019183924 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019184521 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019184490 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356194314 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356194345 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356194508 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356194539 | 6 | 20 | 16.2001 | 4 | 14 | 2.8 | 1.7371 | 148.3861 | 17.3476 | 219.0933 | 415.3827 | 405.7474 | 20821.8878 | 0.90305 | 0.0092329 | 10.4048 | 16.2001 | 168.5581 | 6 | 20 | 4 | 14 | 361.9781 | 571.7069 | 32.0775 | 1.5794 | 0.75059 | 110 | 32.7924 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5417 | 22.8585
CID=1356194438 | 6 | 22.5 | 19.4192 | 4 | 16.5 | 3.3 | 1.7371 | 148.3861 | 17.3476 | 222.5675 | 417.0123 | 405.7474 | 22001.6759 | 0.97863 | 0.010354 | 9.2314 | 19.4192 | 179.266 | 6 | 22.5 | 4 | 16.5 | 361.9781 | 617.2019 | 34.9683 | 1.7051 | 0.77249 | 110 | 38.194 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1644 | 28.6739
CID=1356194469 | 6 | 25 | 23.6695 | 4 | 19 | 3.8 | 1.7371 | 148.3861 | 17.3476 | 226.0633 | 418.6147 | 405.7474 | 23279.6654 | 1.0825 | 0.011848 | 8.2176 | 23.6695 | 194.507 | 6 | 25 | 4 | 19 | 361.9781 | 665.3809 | 37.9855 | 1.8382 | 0.79713 | 110 | 45.1146 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3537 | 34.9853
CID=1356194632 | 6 | 27.5 | 28.3821 | 4 | 21.5 | 4.3 | 1.7371 | 148.3861 | 17.3476 | 229.5813 | 420.1903 | 405.7474 | 24515.5769 | 1.1883 | 0.01356 | 7.3757 | 28.3821 | 209.3394 | 6 | 27.5 | 4 | 21.5 | 361.9781 | 716.3449 | 40.9867 | 1.979 | 0.81967 | 110 | 52.6095 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.739 | 42.0253
CID=1356194663 | 6 | 30 | 33.1234 | 4 | 24 | 4.8 | 1.7371 | 148.3861 | 17.3476 | 233.1226 | 421.7392 | 405.7474 | 25592.7827 | 1.2846 | 0.015363 | 6.6949 | 33.1234 | 221.7564 | 6 | 30 | 4 | 24 | 361.9781 | 770.1963 | 43.8657 | 2.1277 | 0.83817 | 110 | 60.0424 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.1012 | 49.1455
CID=1356194066 | 6 | 32.5 | 37.8546 | 4 | 26.5 | 5.3 | 1.7371 | 148.3861 | 17.3476 | 236.688 | 423.2616 | 405.7474 | 26547.3662 | 1.369 | 0.017246 | 6.1138 | 37.8546 | 231.4355 | 6 | 32.5 | 4 | 26.5 | 361.9781 | 827.0396 | 46.7087 | 2.2848 | 0.85323 | 110 | 67.4072 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7427 | 55.9665
CID=1356194097 | 6 | 35 | 44.0455 | 4 | 29 | 5.8 | 1.7371 | 148.3861 | 17.3476 | 240.2788 | 424.7577 | 405.7474 | 27606.6358 | 1.4829 | 0.019709 | 5.5709 | 44.0455 | 245.3715 | 6 | 35 | 4 | 29 | 361.9781 | 886.981 | 49.7292 | 2.4504 | 0.86884 | 110 | 77.0226 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.991 | 65.1
CID=-1857043803 | 6 | 37.5 | 50.4819 | 4 | 31.5 | 6.3 | 1.7371 | 148.3861 | 17.3476 | 243.8959 | 426.2278 | 405.7474 | 28627.9224 | 1.5887 | 0.022375 | 5.0935 | 50.4819 | 257.1273 | 6 | 37.5 | 4 | 31.5 | 361.9781 | 950.1287 | 52.7641 | 2.6248 | 0.88121 | 110 | 87.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.3835 | 74.5803
CID=-1857043772 | 6 | 40 | 57.5622 | 4 | 34 | 6.8 | 1.7371 | 148.3861 | 17.3476 | 247.5407 | 427.6721 | 405.7474 | 29612.0574 | 1.698 | 0.025397 | 4.6667 | 57.5622 | 268.6272 | 6 | 40 | 4 | 34 | 361.9781 | 1016.593 | 55.8424 | 2.8084 | 0.89139 | 110 | 98.1127 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2032 | 84.9212
CID=-1857043609 | 6 | 42.5 | 62.8139 | 4 | 36.5 | 7.3 | 1.7371 | 148.3861 | 17.3476 | 251.2145 | 429.0909 | 405.7474 | 30266.857 | 1.7654 | 0.027907 | 4.3431 | 62.8139 | 272.8048 | 6 | 42.5 | 4 | 36.5 | 361.9781 | 1086.4865 | 58.5304 | 3.0015 | 0.89717 | 110 | 106.374 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7881 | 91.8398
CID=-1857043578 | 6 | 45 | 70.3199 | 4 | 39 | 7.8 | 1.7371 | 148.3861 | 17.3476 | 254.9187 | 430.4842 | 405.7474 | 31096.8954 | 1.8691 | 0.031384 | 4.0091 | 70.3199 | 281.9213 | 6 | 45 | 4 | 39 | 361.9781 | 1159.9242 | 61.5402 | 3.2044 | 0.90347 | 110 | 118.2553 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.4962 | 102.1436
CID=-1857043679 | 6 | 47.5 | 77.673 | 4 | 41.5 | 8.3 | 1.7371 | 148.3861 | 17.3476 | 258.655 | 431.8524 | 405.7474 | 31862.2443 | 1.956 | 0.034987 | 3.7041 | 77.673 | 287.7087 | 6 | 47.5 | 4 | 41.5 | 361.9781 | 1237.0237 | 64.5887 | 3.4174 | 0.90795 | 110 | 129.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.1636 | 112.1825
CID=-1857043648 | 6 | 50 | 85.2577 | 4 | 44 | 8.8 | 1.7371 | 148.3861 | 17.3476 | 262.425 | 433.1958 | 405.7474 | 32562.5806 | 2.049 | 0.038879 | 3.4445 | 85.2577 | 293.6704 | 6 | 50 | 4 | 44 | 361.9781 | 1317.9055 | 67.4849 | 3.6408 | 0.9113 | 110 | 142.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3056 | 122.2097
CID=-1857043485 | 6 | 52.5 | 89.2122 | 4 | 46.5 | 9.3 | 1.7371 | 148.3861 | 17.3476 | 266.2308 | 434.5145 | 405.7474 | 32973.6103 | 2.0783 | 0.041531 | 3.2502 | 89.2122 | 289.9604 | 6 | 52.5 | 4 | 46.5 | 361.9781 | 1402.6932 | 69.91 | 3.8751 | 0.91266 | 110 | 148.5146 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.1646 | 124.2598
CID=-1857043454 | 6 | 55 | 92.4785 | 4 | 49 | 9.8 | 1.7371 | 148.3861 | 17.3476 | 270.0745 | 435.8088 | 405.7474 | 33345.5229 | 2.0902 | 0.04406 | 3.0664 | 92.4785 | 283.5777 | 6 | 55 | 4 | 49 | 361.9781 | 1491.5141 | 72.3577 | 4.1205 | 0.91363 | 110 | 153.7901 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.3101 | 124.6468
CID=-1857044051 | 6 | 57.5 | 95.5957 | 4 | 51.5 | 10.3 | 1.7371 | 148.3861 | 17.3476 | 273.9586 | 437.0791 | 405.7474 | 33733.9924 | 2.0888 | 0.046687 | 2.8796 | 95.5957 | 275.2753 | 6 | 57.5 | 4 | 51.5 | 361.9781 | 1584.4992 | 74.9819 | 4.3773 | 0.91442 | 110 | 158.835 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66.4309 | 124.7604
CID=-1857044020 | 6 | 60 | 99.5762 | 4 | 54 | 10.8 | 1.7371 | 148.3861 | 17.3476 | 277.8855 | 438.3255 | 405.7474 | 34181.6234 | 2.1024 | 0.04987 | 2.6996 | 99.5762 | 268.816 | 6 | 60 | 4 | 54 | 361.9781 | 1681.7842 | 77.6828 | 4.6461 | 0.9153 | 110 | 165.2902 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 75.0155 | 124.137
CID=1162104424 | 6 | 62.5 | 104.3095 | 4 | 56.5 | 11.3 | 1.7371 | 148.3861 | 17.3476 | 281.8586 | 439.5483 | 405.7474 | 34654.5185 | 2.1235 | 0.053616 | 2.5221 | 104.3096 | 263.079 | 6 | 62.5 | 4 | 56.5 | 361.9781 | 1783.5096 | 80.5203 | 4.9271 | 0.91617 | 110 | 172.9837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 83.3904 | 125.2286
CID=1162104455 | 6 | 65 | 108.7817 | 4 | 59 | 11.8 | 1.7371 | 148.3861 | 17.3476 | 285.881 | 440.748 | 405.7474 | 35084.8958 | 2.1389 | 0.057512 | 2.3569 | 108.7817 | 256.3854 | 6 | 65 | 4 | 59 | 361.9781 | 1889.8218 | 83.3512 | 5.2208 | 0.91684 | 109.6648 | 180.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 7.7007 | 92.0266 | 125.5368
CID=1162104618 | 6 | 67.5 | 114.5622 | 4 | 61.5 | 12.3 | 1.7371 | 148.3861 | 17.3476 | 289.9569 | 441.9247 | 405.7474 | 35559.8163 | 2.177 | 0.062342 | 2.2003 | 114.5622 | 252.0733 | 6 | 67.5 | 4 | 61.5 | 361.9781 | 2000.8736 | 86.2176 | 5.5276 | 0.91753 | 109.1686 | 189.7034 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 104.302 | 124.8224
CID=1162104649 | 6 | 69.99 | 120.2301 | 4 | 63.99 | 12.798 | 1.7371 | 148.3861 | 17.3476 | 294.074 | 443.0743 | 405.7474 | 35978.5349 | 1.7308 | 0.065687 | 1.6571 | 116.6407 | 193.2819 | 6 | 69.99 | 4 | 63.99 | 361.9781 | 2116.3519 | 98.2332 | 5.8466 | 0.91774 | 95.3496 | 193.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 116.6406 | 123.8195
CID=1162104548 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162104579 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162104742 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162104773 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162104176 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162104207 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051133693 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051133662 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051133499 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051133468 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051133569 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051133538 | 9 | 22.5 | 16.2621 | 4 | 16.5 | 3.3 | 1.7357 | 148.2186 | 19.1581 | 222.5675 | 416.6065 | 407.5003 | 20267.5805 | 0.9545 | 0.0093367 | 10.8545 | 16.2621 | 176.518 | 9 | 22.5 | 4 | 16.5 | 400.9358 | 617.2019 | 34.0686 | 1.5394 | 0.75104 | 110 | 32.8981 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.8546 | 22.6697
CID=-2051133375 | 9 | 25 | 19.7604 | 4 | 19 | 3.8 | 1.7357 | 148.2186 | 19.1581 | 226.0633 | 418.2053 | 407.5003 | 21510.8773 | 1.04 | 0.010555 | 9.549 | 19.7604 | 188.6914 | 9 | 25 | 4 | 19 | 400.9358 | 665.3809 | 37.0357 | 1.6596 | 0.77463 | 110 | 38.7574 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.2198 | 29.301
CID=-2051133344 | 9 | 27.5 | 24.1729 | 4 | 21.5 | 4.3 | 1.7357 | 148.2186 | 19.1581 | 229.5813 | 419.7772 | 407.5003 | 22798.0763 | 1.1482 | 0.012121 | 8.4507 | 24.1729 | 204.2779 | 9 | 27.5 | 4 | 21.5 | 400.9358 | 716.3449 | 40.0922 | 1.7867 | 0.79976 | 110 | 45.9225 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4687 | 35.877
CID=-2051133941 | 9 | 30 | 29.0647 | 4 | 24 | 4.8 | 1.7357 | 148.2186 | 19.1581 | 233.1226 | 421.3224 | 407.5003 | 24017.7258 | 1.263 | 0.013916 | 7.5773 | 29.0647 | 220.2329 | 9 | 30 | 4 | 24 | 400.9358 | 770.1963 | 43.0546 | 1.921 | 0.82257 | 110 | 53.6847 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.9305 | 43.1989
CID=-2051133910 | 9 | 32.5 | 34.2413 | 4 | 26.5 | 5.3 | 1.7357 | 148.2186 | 19.1581 | 236.688 | 422.8412 | 407.5003 | 25147.3286 | 1.3746 | 0.01589 | 6.8573 | 34.2413 | 234.8035 | 9 | 32.5 | 4 | 26.5 | 400.9358 | 827.0396 | 45.9522 | 2.0628 | 0.84201 | 110 | 61.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2579 | 51.2247
CID=1324244894 | 9 | 35 | 38.8172 | 4 | 29 | 5.8 | 1.7357 | 148.2186 | 19.1581 | 240.2788 | 424.3337 | 407.5003 | 26039.3543 | 1.4575 | 0.017757 | 6.2788 | 38.8172 | 243.727 | 9 | 35 | 4 | 29 | 400.9358 | 886.981 | 48.6833 | 2.2123 | 0.85594 | 110 | 68.9026 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0505 | 57.5838
CID=1324244925 | 9 | 37.5 | 45.2971 | 4 | 31.5 | 6.3 | 1.7357 | 148.2186 | 19.1581 | 243.8959 | 425.8002 | 407.5003 | 27105.863 | 1.5797 | 0.020362 | 5.7056 | 45.2971 | 258.4475 | 9 | 37.5 | 4 | 31.5 | 400.9358 | 950.1287 | 51.7152 | 2.3698 | 0.87152 | 110 | 78.9676 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6818 | 66.9124
CID=1324245088 | 9 | 40 | 52.1309 | 4 | 34 | 6.8 | 1.7357 | 148.2186 | 19.1581 | 247.5407 | 427.2409 | 407.5003 | 28139.0481 | 1.6967 | 0.023217 | 5.2061 | 52.1309 | 271.399 | 9 | 40 | 4 | 34 | 400.9358 | 1016.593 | 54.7511 | 2.5356 | 0.88386 | 110 | 89.612 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2008 | 77.061
CID=1324245119 | 9 | 42.5 | 59.2479 | 4 | 36.5 | 7.3 | 1.7357 | 148.2186 | 19.1581 | 251.2145 | 428.656 | 407.5003 | 29088.5914 | 1.8125 | 0.026314 | 4.7811 | 59.2479 | 283.2676 | 9 | 42.5 | 4 | 36.5 | 400.9358 | 1086.4865 | 57.7116 | 2.7099 | 0.89339 | 110 | 100.7599 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9216 | 87.5743
CID=1324245018 | 9 | 45 | 66.0937 | 4 | 39 | 7.8 | 1.7357 | 148.2186 | 19.1581 | 254.9187 | 430.0457 | 407.5003 | 29898.9914 | 1.9113 | 0.029469 | 4.4125 | 66.0937 | 291.6357 | 9 | 45 | 4 | 39 | 400.9358 | 1159.9242 | 60.6106 | 2.893 | 0.90018 | 110 | 111.555 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.7915 | 97.396
CID=1324245049 | 9 | 47.5 | 72.7123 | 4 | 41.5 | 8.3 | 1.7357 | 148.2186 | 19.1581 | 258.655 | 431.4103 | 407.5003 | 30614.2739 | 1.9983 | 0.032704 | 4.0905 | 72.7123 | 297.432 | 9 | 47.5 | 4 | 41.5 | 400.9358 | 1237.0237 | 63.4446 | 3.0853 | 0.90509 | 110 | 122.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.4856 | 105.939
CID=1324245212 | 9 | 50 | 80.7532 | 4 | 44 | 8.8 | 1.7357 | 148.2186 | 19.1581 | 262.425 | 432.7501 | 407.5003 | 31390.8296 | 2.1038 | 0.036665 | 3.7796 | 80.7532 | 305.213 | 9 | 50 | 4 | 44 | 400.9358 | 1317.9055 | 66.4438 | 3.2871 | 0.90945 | 110 | 134.9083 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3087 | 117.1977
CID=1324245243 | 9 | 52.5 | 88.3044 | 4 | 46.5 | 9.3 | 1.7357 | 148.2186 | 19.1581 | 266.2308 | 434.0651 | 407.5003 | 32079.97 | 2.1925 | 0.040655 | 3.5075 | 88.3044 | 309.7263 | 9 | 52.5 | 4 | 46.5 | 400.9358 | 1402.6932 | 69.361 | 3.4985 | 0.91237 | 110 | 147.0504 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.6486 | 126.9601
CID=1324244646 | 9 | 55 | 90.9481 | 4 | 49 | 9.8 | 1.7357 | 148.2186 | 19.1581 | 270.0745 | 435.3559 | 407.5003 | 32395.1183 | 2.1978 | 0.042873 | 3.3209 | 90.9481 | 302.0328 | 9 | 55 | 4 | 49 | 400.9358 | 1491.5141 | 71.6528 | 3.7201 | 0.91319 | 110 | 151.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.9361 | 126.9601
CID=1324244677 | 9 | 57.5 | 94.2611 | 4 | 51.5 | 10.3 | 1.7357 | 148.2186 | 19.1581 | 273.9586 | 436.6225 | 407.5003 | 32748.3702 | 2.2071 | 0.045513 | 3.1269 | 94.261 | 294.744 | 9 | 57.5 | 4 | 51.5 | 400.9358 | 1584.4992 | 74.1451 | 3.952 | 0.9141 | 110 | 156.6738 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5619 | 126.9602
CID=-1888993223 | 9 | 60 | 97.2373 | 4 | 54 | 10.8 | 1.7357 | 148.2186 | 19.1581 | 277.8855 | 437.8652 | 407.5003 | 33087.7721 | 2.2022 | 0.048182 | 2.9354 | 97.2373 | 285.4317 | 9 | 60 | 4 | 54 | 400.9358 | 1681.7842 | 76.7506 | 4.1946 | 0.9148 | 110 | 161.4954 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.5145 | 126.9601
CID=-1888993192 | 9 | 62.5 | 100.9221 | 4 | 56.5 | 11.3 | 1.7357 | 148.2186 | 19.1581 | 281.8586 | 439.0844 | 407.5003 | 33483.7519 | 2.208 | 0.051353 | 2.7489 | 100.9221 | 277.4228 | 9 | 62.5 | 4 | 56.5 | 400.9358 | 1783.5096 | 79.454 | 4.4484 | 0.91557 | 110 | 167.4759 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.8839 | 126.9602
CID=-1888993029 | 9 | 65 | 105.7526 | 4 | 59 | 11.8 | 1.7357 | 148.2186 | 19.1581 | 285.881 | 440.2804 | 407.5003 | 33997.3091 | 2.2301 | 0.055284 | 2.5647 | 105.7526 | 271.2205 | 9 | 65 | 4 | 59 | 400.9358 | 1889.8218 | 82.2957 | 4.7135 | 0.9164 | 110 | 175.3326 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 84.545 | 126.9602
CID=-1888992998 | 9 | 67.5 | 110.2177 | 4 | 61.5 | 12.3 | 1.7357 | 148.2186 | 19.1581 | 289.9569 | 441.4534 | 407.5003 | 34448.7693 | 2.2395 | 0.059335 | 2.3884 | 110.2177 | 263.2388 | 9 | 67.5 | 4 | 61.5 | 400.9358 | 2000.8736 | 85.2036 | 4.9905 | 0.91703 | 109.6287 | 182.6103 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 93.4753 | 126.9601
CID=-1888993099 | 9 | 69.99 | 114.8082 | 4 | 63.99 | 12.798 | 1.7357 | 148.2186 | 19.1581 | 294.074 | 442.5993 | 407.5003 | 34882.9618 | 2.2463 | 0.063764 | 2.2193 | 114.8082 | 254.7901 | 9 | 69.99 | 4 | 63.99 | 400.9358 | 2116.3519 | 88.183 | 5.2785 | 0.91756 | 108.9378 | 190.1055 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 102.6563 | 126.9602
CID=-1888993068 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888992905 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888992874 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888993471 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888993440 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155004 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155035 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155198 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155229 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155128 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155159 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155322 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130155353 | 12 | 25 | 13.7516 | 4 | 19 | 3.8 | 1.7345 | 147.9949 | 21.1172 | 226.0633 | 417.8241 | 409.2305 | 19548.2815 | 0.89775 | 0.0087047 | 11.9578 | 13.7516 | 164.439 | 12 | 25 | 4 | 19 | 443.0145 | 665.3809 | 35.1839 | 1.5019 | 0.73178 | 89.6669 | 28.5517 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.795 | 16.7083
CID=1130154756 | 12 | 27.5 | 20.4579 | 4 | 21.5 | 4.3 | 1.7345 | 147.9949 | 21.1172 | 229.5813 | 419.3925 | 409.2305 | 21129.9147 | 1.1217 | 0.010872 | 9.85 | 20.4579 | 201.5099 | 12 | 27.5 | 4 | 21.5 | 443.0145 | 716.3449 | 39.1926 | 1.617 | 0.77893 | 110 | 39.9043 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.1128 | 29.8031
CID=1130154787 | 12 | 30 | 24.8829 | 4 | 24 | 4.8 | 1.7345 | 147.9949 | 21.1172 | 233.1226 | 420.9344 | 409.2305 | 22369.5483 | 1.2301 | 0.012467 | 8.7063 | 24.8829 | 216.6375 | 12 | 30 | 4 | 24 | 443.0145 | 770.1963 | 42.1972 | 1.7385 | 0.80337 | 110 | 47.0587 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0293 | 36.7366
CID=-2083083113 | 12 | 32.5 | 29.9757 | 4 | 26.5 | 5.3 | 1.7345 | 147.9949 | 21.1172 | 236.688 | 422.4497 | 409.2305 | 23570.4648 | 1.352 | 0.014357 | 7.782 | 29.9757 | 233.2718 | 12 | 32.5 | 4 | 26.5 | 443.0145 | 827.0396 | 45.1604 | 1.8668 | 0.82631 | 110 | 55.1166 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.6766 | 44.2749
CID=-2083083082 | 12 | 35 | 35.3688 | 4 | 29 | 5.8 | 1.7345 | 147.9949 | 21.1172 | 240.2788 | 423.9389 | 409.2305 | 24697.182 | 1.4701 | 0.016437 | 7.0225 | 35.3688 | 248.3778 | 12 | 35 | 4 | 29 | 443.0145 | 886.981 | 48.0662 | 2.0021 | 0.8457 | 110 | 63.5417 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.1723 | 52.5653
CID=-2083082919 | 12 | 37.5 | 40.0799 | 4 | 31.5 | 6.3 | 1.7345 | 147.9949 | 21.1172 | 243.8959 | 425.402 | 409.2305 | 25588.0197 | 1.5587 | 0.018386 | 6.4297 | 40.0799 | 257.7008 | 12 | 37.5 | 4 | 31.5 | 443.0145 | 950.1287 | 50.76 | 2.1447 | 0.85933 | 110 | 70.8638 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8063 | 59.3536
CID=-2083082888 | 12 | 40 | 46.3647 | 4 | 34 | 6.8 | 1.7345 | 147.9949 | 21.1172 | 247.5407 | 426.8393 | 409.2305 | 26604.2511 | 1.6767 | 0.020972 | 5.8473 | 46.3647 | 271.1077 | 12 | 40 | 4 | 34 | 443.0145 | 1016.593 | 53.7165 | 2.2947 | 0.87369 | 110 | 80.6277 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0173 | 68.7122
CID=-2083082989 | 12 | 42.5 | 53.6552 | 4 | 36.5 | 7.3 | 1.7345 | 147.9949 | 21.1172 | 251.2145 | 428.251 | 409.2305 | 27621.9231 | 1.8114 | 0.024043 | 5.3346 | 53.6552 | 286.2268 | 12 | 42.5 | 4 | 36.5 | 443.0145 | 1086.4865 | 56.7059 | 2.4525 | 0.88616 | 110 | 91.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0083 | 79.3022
CID=-2083082958 | 12 | 45 | 61.0037 | 4 | 39 | 7.8 | 1.7345 | 147.9949 | 21.1172 | 254.9187 | 429.6374 | 409.2305 | 28577.6548 | 1.9323 | 0.027289 | 4.8877 | 61.0037 | 298.1691 | 12 | 45 | 4 | 39 | 443.0145 | 1159.9242 | 59.6777 | 2.6183 | 0.89533 | 110 | 103.5216 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.8335 | 90.1739
CID=-2083082795 | 12 | 47.5 | 69.1129 | 4 | 41.5 | 8.3 | 1.7345 | 147.9949 | 21.1172 | 258.655 | 430.9986 | 409.2305 | 29508.6441 | 2.058 | 0.030987 | 4.4837 | 69.1129 | 309.8846 | 12 | 47.5 | 4 | 41.5 | 443.0145 | 1237.0237 | 62.7045 | 2.7923 | 0.90259 | 110 | 116.3388 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2059 | 102.0198
CID=-2083082764 | 12 | 50 | 75.0427 | 4 | 44 | 8.8 | 1.7345 | 147.9949 | 21.1172 | 262.425 | 432.335 | 409.2305 | 30123.9535 | 2.1341 | 0.034049 | 4.175 | 75.0427 | 313.3005 | 12 | 50 | 4 | 44 | 443.0145 | 1317.9055 | 65.3758 | 2.9749 | 0.90651 | 110 | 125.7746 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.3372 | 109.7483
CID=-2083083361 | 12 | 52.5 | 83.4712 | 4 | 46.5 | 9.3 | 1.7345 | 147.9949 | 21.1172 | 266.2308 | 433.6467 | 409.2305 | 30903.6355 | 2.2512 | 0.038265 | 3.8566 | 83.4712 | 321.9186 | 12 | 52.5 | 4 | 46.5 | 443.0145 | 1402.6932 | 68.3367 | 3.1662 | 0.91061 | 110 | 139.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5194 | 121.423
CID=-2083083330 | 12 | 55 | 88.8873 | 4 | 49 | 9.8 | 1.7345 | 147.9949 | 21.1172 | 270.0745 | 434.934 | 409.2305 | 31432.5022 | 2.3011 | 0.041508 | 3.6025 | 88.8873 | 320.2181 | 12 | 55 | 4 | 49 | 443.0145 | 1491.5141 | 71.0053 | 3.3667 | 0.91256 | 110 | 147.9906 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8145 | 126.9602
CID=1194063569 | 12 | 57.5 | 91.7701 | 4 | 51.5 | 10.3 | 1.7345 | 147.9949 | 21.1172 | 273.9586 | 436.1972 | 409.2305 | 31765.6095 | 2.3072 | 0.043897 | 3.401 | 91.7701 | 312.1062 | 12 | 57.5 | 4 | 51.5 | 443.0145 | 1584.4992 | 73.3752 | 3.5766 | 0.91343 | 110 | 152.6451 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5802 | 126.9601
CID=1194063666 | 12 | 60 | 94.9229 | 4 | 54 | 10.8 | 1.7345 | 147.9949 | 21.1172 | 277.8855 | 437.4365 | 409.2305 | 32118.6012 | 2.3086 | 0.046557 | 3.1944 | 94.9229 | 303.2213 | 12 | 60 | 4 | 54 | 443.0145 | 1681.7842 | 75.9208 | 3.7962 | 0.91426 | 110 | 157.7453 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.8856 | 126.9602
CID=1194063631 | 12 | 62.5 | 98.5401 | 4 | 56.5 | 11.3 | 1.7345 | 147.9949 | 21.1172 | 281.8586 | 438.6523 | 409.2305 | 32492.2826 | 2.3122 | 0.049605 | 2.9887 | 98.5401 | 294.5114 | 12 | 62.5 | 4 | 56.5 | 443.0145 | 1783.5096 | 78.6065 | 4.0258 | 0.91509 | 110 | 163.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70.1201 | 126.9601
CID=1194063472 | 12 | 65 | 101.5682 | 4 | 59 | 11.8 | 1.7345 | 147.9949 | 21.1172 | 285.881 | 439.8448 | 409.2305 | 32836.1811 | 2.2992 | 0.052602 | 2.7922 | 101.5682 | 283.6036 | 12 | 65 | 4 | 59 | 443.0145 | 1889.8218 | 81.3506 | 4.2658 | 0.91569 | 110 | 168.5257 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 76.1762 | 126.9602
CID=1194063445 | 12 | 67.5 | 105.795 | 4 | 61.5 | 12.3 | 1.7345 | 147.9949 | 21.1172 | 289.9569 | 441.0144 | 409.2305 | 33286.2732 | 2.3118 | 0.056391 | 2.6063 | 105.795 | 275.7366 | 12 | 67.5 | 4 | 61.5 | 443.0145 | 2000.8736 | 84.1355 | 4.5165 | 0.9164 | 110 | 175.4017 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 84.6298 | 126.9602
CID=1194063542 | 12 | 69.99 | 110.8354 | 4 | 63.99 | 12.798 | 1.7345 | 147.9949 | 21.1172 | 294.074 | 442.1569 | 409.2305 | 33787.5097 | 2.3289 | 0.060867 | 2.4197 | 110.8354 | 268.1899 | 12 | 69.99 | 4 | 63.99 | 443.0145 | 2116.3519 | 87.0971 | 4.7772 | 0.9171 | 109.6961 | 183.6181 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.7107 | 126.9601
CID=1194063507 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194063348 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194063321 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194063418 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174548 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174451 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174486 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174645 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174672 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174575 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174610 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174769 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174796 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019174699 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356204039 | 15 | 30 | 21.2198 | 4 | 24 | 4.8 | 1.7333 | 147.7132 | 23.2347 | 233.1226 | 420.5719 | 410.9364 | 20764.2114 | 1.2064 | 0.011217 | 10.1089 | 21.2198 | 214.5091 | 15 | 30 | 4 | 24 | 488.3739 | 770.1963 | 41.4503 | 1.5771 | 0.78348 | 110 | 41.15 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3198 | 30.1197
CID=1356204136 | 15 | 32.5 | 25.3031 | 4 | 26.5 | 5.3 | 1.7333 | 147.7132 | 23.2347 | 236.688 | 422.0841 | 410.9364 | 21884.9096 | 1.3038 | 0.012733 | 8.9785 | 25.3031 | 227.1846 | 15 | 32.5 | 4 | 26.5 | 488.3739 | 827.0396 | 44.3031 | 1.6935 | 0.80546 | 110 | 47.7292 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0742 | 37.5319
CID=1356204101 | 15 | 35 | 30.4993 | 4 | 29 | 5.8 | 1.7333 | 147.7132 | 23.2347 | 240.2788 | 423.5701 | 410.9364 | 23071.9004 | 1.4321 | 0.014686 | 8.0131 | 30.4993 | 244.3925 | 15 | 35 | 4 | 29 | 488.3739 | 886.981 | 47.2349 | 1.8162 | 0.8284 | 110 | 55.9381 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.7101 | 45.2884
CID=1356203942 | 15 | 37.5 | 36.1858 | 4 | 31.5 | 6.3 | 1.7333 | 147.7132 | 23.2347 | 243.8959 | 425.03 | 410.9364 | 24218.8562 | 1.5605 | 0.016897 | 7.2035 | 36.1858 | 260.6646 | 15 | 37.5 | 4 | 31.5 | 488.3739 | 950.1287 | 50.1654 | 1.9455 | 0.84827 | 110 | 64.8129 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.4587 | 53.9129
CID=1356203915 | 15 | 40 | 42.3902 | 4 | 34 | 6.8 | 1.7333 | 147.7132 | 23.2347 | 247.5407 | 426.4641 | 410.9364 | 25295.7928 | 1.694 | 0.019393 | 6.5297 | 42.3902 | 276.7934 | 15 | 40 | 4 | 34 | 488.3739 | 1016.593 | 53.0492 | 2.0816 | 0.86506 | 110 | 74.4514 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4735 | 63.3068
CID=1356204012 | 15 | 42.5 | 47.6625 | 4 | 36.5 | 7.3 | 1.7333 | 147.7132 | 23.2347 | 251.2145 | 427.8727 | 410.9364 | 26129.3804 | 1.787 | 0.021685 | 5.9883 | 47.6625 | 285.4184 | 15 | 42.5 | 4 | 36.5 | 488.3739 | 1086.4865 | 55.7682 | 2.2247 | 0.87621 | 110 | 82.6467 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7682 | 70.5569
CID=1356203977 | 15 | 45 | 55.1417 | 4 | 39 | 7.8 | 1.7333 | 147.7132 | 23.2347 | 254.9187 | 429.2559 | 410.9364 | 27127.8259 | 1.9281 | 0.024884 | 5.4555 | 55.1417 | 300.8235 | 15 | 45 | 4 | 39 | 488.3739 | 1159.9242 | 58.7424 | 2.3751 | 0.88825 | 110 | 94.3192 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.93 | 81.3534
CID=1356203818 | 15 | 47.5 | 62.792 | 4 | 41.5 | 8.3 | 1.7333 | 147.7132 | 23.2347 | 258.655 | 430.614 | 410.9364 | 28088.7233 | 2.057 | 0.028311 | 4.9885 | 62.792 | 313.2398 | 15 | 47.5 | 4 | 41.5 | 488.3739 | 1237.0237 | 61.7188 | 2.5329 | 0.89715 | 110 | 106.3395 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.6346 | 92.9494
CID=1356203791 | 15 | 50 | 70.9472 | 4 | 44 | 8.8 | 1.7333 | 147.7132 | 23.2347 | 262.425 | 431.9472 | 410.9364 | 28988.6318 | 2.1902 | 0.032111 | 4.5847 | 70.9472 | 325.2744 | 15 | 50 | 4 | 44 | 488.3739 | 1317.9055 | 64.6507 | 2.6986 | 0.90391 | 110 | 119.2521 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.943 | 104.9514
CID=1356203888 | 15 | 52.5 | 78.9541 | 4 | 46.5 | 9.3 | 1.7333 | 147.7132 | 23.2347 | 266.2308 | 433.2557 | 410.9364 | 29773.9532 | 2.3078 | 0.036061 | 4.2297 | 78.9541 | 333.9483 | 15 | 52.5 | 4 | 46.5 | 488.3739 | 1402.6932 | 67.5496 | 2.8722 | 0.9086 | 110 | 132.0259 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2093 | 116.6989
CID=-1857034078 | 15 | 55 | 86.2121 | 4 | 49 | 9.8 | 1.7333 | 147.7132 | 23.2347 | 270.0745 | 434.5399 | 410.9364 | 30433.9506 | 2.4018 | 0.039938 | 3.9244 | 86.2121 | 338.3289 | 15 | 55 | 4 | 49 | 488.3739 | 1491.5141 | 70.3458 | 3.054 | 0.91165 | 110 | 143.6792 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8297 | 125.5944
CID=-1857033981 | 15 | 57.5 | 89.3321 | 4 | 51.5 | 10.3 | 1.7333 | 147.7132 | 23.2347 | 273.9586 | 435.7999 | 410.9364 | 30786.3008 | 2.4119 | 0.04235 | 3.6983 | 89.3321 | 330.377 | 15 | 57.5 | 4 | 51.5 | 488.3739 | 1584.4992 | 72.7295 | 3.2444 | 0.9127 | 110 | 148.708 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.704 | 126.9601
CID=-1857034016 | 15 | 60 | 92.5748 | 4 | 54 | 10.8 | 1.7333 | 147.7132 | 23.2347 | 277.8855 | 437.0361 | 410.9364 | 31154.8776 | 2.4219 | 0.044969 | 3.4808 | 92.5748 | 322.2368 | 15 | 60 | 4 | 54 | 488.3739 | 1681.7842 | 75.1741 | 3.4436 | 0.91365 | 110 | 153.9459 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.1896 | 126.9601
CID=-1857034175 | 15 | 62.5 | 95.4613 | 4 | 56.5 | 11.3 | 1.7333 | 147.7132 | 23.2347 | 281.8586 | 438.2486 | 410.9364 | 31484.2569 | 2.4131 | 0.04761 | 3.2629 | 95.4613 | 311.4829 | 15 | 62.5 | 4 | 56.5 | 488.3739 | 1783.5096 | 77.7547 | 3.6519 | 0.91439 | 110 | 158.6173 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.9624 | 126.9602
CID=-1857034202 | 15 | 65 | 99.114 | 4 | 59 | 11.8 | 1.7333 | 147.7132 | 23.2347 | 285.881 | 439.4379 | 410.9364 | 31867.7437 | 2.4105 | 0.050782 | 3.0415 | 99.114 | 301.4503 | 15 | 65 | 4 | 59 | 488.3739 | 1889.8218 | 80.5215 | 3.8696 | 0.91521 | 110 | 164.5398 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71.2677 | 126.9602
CID=-1857034105 | 15 | 67.5 | 102.9649 | 4 | 61.5 | 12.3 | 1.7333 | 147.7132 | 23.2347 | 289.9569 | 440.6043 | 410.9364 | 32271.7741 | 2.4092 | 0.054281 | 2.8307 | 102.9649 | 291.4594 | 15 | 67.5 | 4 | 61.5 | 488.3739 | 2000.8736 | 83.3505 | 4.097 | 0.91594 | 110 | 170.7962 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 78.9695 | 126.9602
CID=-1857034140 | 15 | 69.99 | 106.3098 | 4 | 63.99 | 12.798 | 1.7333 | 147.7132 | 23.2347 | 294.074 | 441.7436 | 410.9364 | 32661.842 | 2.3983 | 0.057802 | 2.6363 | 106.3098 | 280.2675 | 15 | 69.99 | 4 | 63.99 | 488.3739 | 2116.3519 | 86.1627 | 4.3335 | 0.91648 | 109.7779 | 176.2401 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4585 | 85.6595 | 126.9602
CID=-1857034299 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857034326 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857034229 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114149 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114246 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114211 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114052 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114025 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114122 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162114087 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162113928 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162113901 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162113998 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051123968 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051123871 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051123906 | 18 | 32.5 | 22.5858 | 4 | 26.5 | 5.3 | 1.7322 | 147.3721 | 25.5211 | 236.688 | 421.7412 | 412.6163 | 20552.4659 | 1.3209 | 0.011763 | 10.2893 | 22.5858 | 232.3915 | 18 | 32.5 | 4 | 26.5 | 537.1767 | 827.0396 | 43.8589 | 1.5396 | 0.79126 | 110 | 43.3679 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.839 | 32.3325
CID=-2051124065 | 18 | 35 | 25.6725 | 4 | 29 | 5.8 | 1.7322 | 147.3721 | 25.5211 | 240.2788 | 423.2242 | 412.6163 | 21405.2988 | 1.3801 | 0.012993 | 9.2644 | 25.6725 | 237.8402 | 18 | 35 | 4 | 29 | 537.1767 | 886.981 | 46.4263 | 1.6512 | 0.80727 | 110 | 48.3178 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.112 | 38.233
CID=-2051124092 | 18 | 37.5 | 31.1271 | 4 | 31.5 | 6.3 | 1.7322 | 147.3721 | 25.5211 | 243.8959 | 424.6812 | 412.6163 | 22614.6414 | 1.5161 | 0.015061 | 8.2179 | 31.1271 | 255.7985 | 18 | 37.5 | 4 | 31.5 | 537.1767 | 950.1287 | 49.4103 | 1.7687 | 0.83084 | 110 | 56.9219 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9579 | 46.2963
CID=-2051123995 | 18 | 40 | 37.1162 | 4 | 34 | 6.8 | 1.7322 | 147.3721 | 25.5211 | 247.5407 | 426.1123 | 412.6163 | 23756.5729 | 1.6588 | 0.017413 | 7.3774 | 37.1162 | 273.8195 | 18 | 40 | 4 | 34 | 537.1767 | 1016.593 | 52.3218 | 1.8925 | 0.85108 | 110 | 66.2596 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0416 | 55.1907
CID=-2051124030 | 18 | 42.5 | 43.4063 | 4 | 36.5 | 7.3 | 1.7322 | 147.3721 | 25.5211 | 251.2145 | 427.5179 | 412.6163 | 24814.9738 | 1.7972 | 0.019985 | 6.6826 | 43.4063 | 290.0669 | 18 | 42.5 | 4 | 36.5 | 537.1767 | 1086.4865 | 55.1759 | 2.0226 | 0.86741 | 110 | 76.0296 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9546 | 64.858
CID=-2051124189 | 18 | 45 | 48.678 | 4 | 39 | 7.8 | 1.7322 | 147.3721 | 25.5211 | 254.9187 | 428.8982 | 412.6163 | 25628.8179 | 1.894 | 0.022324 | 6.1357 | 48.678 | 298.6728 | 18 | 45 | 4 | 39 | 537.1767 | 1159.9242 | 57.8367 | 2.1593 | 0.87808 | 110 | 84.2278 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0409 | 72.3151
CID=-2051124216 | 18 | 47.5 | 56.1207 | 4 | 41.5 | 8.3 | 1.7322 | 147.3721 | 25.5211 | 258.655 | 430.2533 | 412.6163 | 26610.2167 | 2.0351 | 0.025573 | 5.5831 | 56.1207 | 313.3305 | 18 | 47.5 | 4 | 41.5 | 537.1767 | 1237.0237 | 60.7893 | 2.3028 | 0.88956 | 110 | 95.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.9027 | 83.3388
CID=-2051124119 | 18 | 50 | 64.6119 | 4 | 44 | 8.8 | 1.7322 | 147.3721 | 25.5211 | 262.425 | 431.5835 | 412.6163 | 27590.9885 | 2.1925 | 0.029385 | 5.0966 | 64.6119 | 329.2993 | 18 | 50 | 4 | 44 | 537.1767 | 1317.9055 | 63.7652 | 2.4534 | 0.89887 | 110 | 109.2122 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7506 | 95.4733
CID=1324254619 | 18 | 52.5 | 72.9158 | 4 | 46.5 | 9.3 | 1.7322 | 147.3721 | 25.5211 | 266.2308 | 432.8891 | 412.6163 | 28484.9905 | 2.3297 | 0.033332 | 4.6771 | 72.9158 | 341.033 | 18 | 52.5 | 4 | 46.5 | 537.1767 | 1402.6932 | 66.6924 | 2.6112 | 0.90522 | 110 | 122.3843 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.0197 | 107.8119
CID=1324254716 | 18 | 55 | 82.1043 | 4 | 49 | 9.8 | 1.7322 | 147.3721 | 25.5211 | 270.0745 | 434.1702 | 412.6163 | 29365.113 | 2.4731 | 0.037849 | 4.2936 | 82.1043 | 352.5231 | 18 | 55 | 4 | 49 | 537.1767 | 1491.5141 | 69.684 | 2.7766 | 0.91004 | 110 | 137.0757 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9579 | 121.2507
CID=1324254681 | 18 | 57.5 | 87.3219 | 4 | 51.5 | 10.3 | 1.7322 | 147.3721 | 25.5211 | 273.9586 | 435.4273 | 412.6163 | 29852.2601 | 2.5294 | 0.041023 | 4.0165 | 87.3219 | 350.7276 | 18 | 57.5 | 4 | 51.5 | 537.1767 | 1584.4992 | 72.2272 | 2.9497 | 0.91204 | 110 | 145.4668 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.6837 | 126.9601
CID=1324254522 | 18 | 60 | 90.053 | 4 | 54 | 10.8 | 1.7322 | 147.3721 | 25.5211 | 277.8855 | 436.6604 | 412.6163 | 30188.517 | 2.5293 | 0.043357 | 3.7841 | 90.053 | 340.7732 | 18 | 60 | 4 | 54 | 537.1767 | 1681.7842 | 74.6051 | 3.1308 | 0.91292 | 110 | 149.8715 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1459 | 126.9601
CID=1324254495 | 18 | 62.5 | 93.2761 | 4 | 56.5 | 11.3 | 1.7322 | 147.3721 | 25.5211 | 281.8586 | 437.87 | 412.6163 | 30535.6499 | 2.5302 | 0.046059 | 3.547 | 93.2761 | 330.8485 | 18 | 62.5 | 4 | 56.5 | 537.1767 | 1783.5096 | 77.1468 | 3.3202 | 0.91384 | 110 | 155.08 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59.592 | 126.9601
CID=1324254592 | 18 | 65 | 96.2087 | 4 | 59 | 11.8 | 1.7322 | 147.3721 | 25.5211 | 285.881 | 439.0563 | 412.6163 | 30881.1232 | 2.5241 | 0.048821 | 3.325 | 96.2088 | 319.8928 | 18 | 65 | 4 | 59 | 537.1767 | 1889.8218 | 79.7072 | 3.5181 | 0.91457 | 110 | 159.8283 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.4574 | 126.9601
CID=1324254557 | 18 | 67.5 | 99.5556 | 4 | 61.5 | 12.3 | 1.7322 | 147.3721 | 25.5211 | 289.9569 | 440.2196 | 412.6163 | 31245.435 | 2.511 | 0.051976 | 3.0937 | 99.5556 | 307.9948 | 18 | 67.5 | 4 | 61.5 | 537.1767 | 2000.8736 | 82.4921 | 3.7248 | 0.9153 | 110 | 165.2566 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.1509 | 126.9602
CID=1324254398 | 18 | 69.99 | 103.4419 | 4 | 63.99 | 12.798 | 1.7322 | 147.3721 | 25.5211 | 294.074 | 441.3558 | 412.6163 | 31659.583 | 2.503 | 0.055623 | 2.8684 | 103.4419 | 296.7124 | 18 | 69.99 | 4 | 63.99 | 537.1767 | 2116.3519 | 85.39 | 3.9398 | 0.91602 | 110 | 171.5721 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79.9236 | 126.9602
CID=1324254371 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324254468 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983498 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983401 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983436 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983595 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983622 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983525 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983560 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983719 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983746 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888983649 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130164729 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130164826 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130164791 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130164632 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130164605 | 21 | 35 | 19.0293 | 4 | 29 | 5.8 | 1.7312 | 146.9698 | 27.9878 | 240.2788 | 422.8982 | 414.2684 | 19635.7682 | 1.241 | 0.010779 | 11.347 | 19.0293 | 215.9262 | 21 | 35 | 4 | 29 | 589.5892 | 886.981 | 45.0322 | 1.5044 | 0.76999 | 90.2054 | 37.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.5732 | 24.4855
CID=1130164702 | 21 | 37.5 | 26.4186 | 4 | 31.5 | 6.3 | 1.7312 | 146.9698 | 27.9878 | 243.8959 | 424.3523 | 414.2684 | 21015.5319 | 1.4788 | 0.013384 | 9.5369 | 26.4186 | 251.9516 | 21 | 37.5 | 4 | 31.5 | 589.5892 | 950.1287 | 48.6197 | 1.6115 | 0.81083 | 110 | 49.5037 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0444 | 38.7928
CID=1130164667 | 21 | 40 | 31.9169 | 4 | 34 | 6.8 | 1.7312 | 146.9698 | 27.9878 | 247.5407 | 425.7807 | 414.2684 | 22190.3598 | 1.6169 | 0.015504 | 8.4464 | 31.9169 | 269.5844 | 21 | 40 | 4 | 34 | 589.5892 | 1016.593 | 51.572 | 1.7242 | 0.83381 | 110 | 58.1578 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5838 | 47.2501
CID=1130164508 | 21 | 42.5 | 38.0943 | 4 | 36.5 | 7.3 | 1.7312 | 146.9698 | 27.9878 | 251.2145 | 427.1835 | 414.2684 | 23310.7493 | 1.7676 | 0.017963 | 7.5659 | 38.0943 | 288.2163 | 21 | 42.5 | 4 | 36.5 | 589.5892 | 1086.4865 | 54.475 | 1.8428 | 0.85392 | 110 | 67.7797 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8198 | 56.3689
CID=1130164481 | 21 | 45 | 44.6648 | 4 | 39 | 7.8 | 1.7312 | 146.9698 | 27.9878 | 254.9187 | 428.5609 | 414.2684 | 24378.6609 | 1.915 | 0.020684 | 6.832 | 44.6648 | 305.1489 | 21 | 45 | 4 | 39 | 589.5892 | 1159.9242 | 57.3483 | 1.9673 | 0.87018 | 110 | 77.9849 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9995 | 66.3301
CID=1130164578 | 21 | 47.5 | 51.3791 | 4 | 41.5 | 8.3 | 1.7312 | 146.9698 | 27.9878 | 258.655 | 429.9132 | 414.2684 | 25337.3808 | 2.0538 | 0.023595 | 6.2203 | 51.3791 | 319.5946 | 21 | 47.5 | 4 | 41.5 | 589.5892 | 1237.0237 | 60.161 | 2.0981 | 0.88268 | 110 | 88.4385 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2319 | 76.5263
CID=-2083073388 | 21 | 50 | 57.659 | 4 | 44 | 8.8 | 1.7312 | 146.9698 | 27.9878 | 262.425 | 431.2407 | 414.2684 | 26149.9258 | 2.1662 | 0.026497 | 5.7047 | 57.6589 | 328.9272 | 21 | 50 | 4 | 44 | 589.5892 | 1317.9055 | 62.9049 | 2.2353 | 0.89151 | 110 | 98.2646 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9299 | 85.388
CID=-2083073291 | 21 | 52.5 | 66.1385 | 4 | 46.5 | 9.3 | 1.7312 | 146.9698 | 27.9878 | 266.2308 | 432.5434 | 414.2684 | 27084.2128 | 2.3265 | 0.030391 | 5.2074 | 66.1385 | 344.4122 | 21 | 52.5 | 4 | 46.5 | 589.5892 | 1402.6932 | 65.8382 | 2.3791 | 0.90021 | 110 | 111.6258 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.5049 | 97.772
CID=-2083073326 | 21 | 55 | 74.8139 | 4 | 49 | 9.8 | 1.7312 | 146.9698 | 27.9878 | 270.0745 | 433.8218 | 414.2684 | 27993.4443 | 2.4729 | 0.034577 | 4.7662 | 74.8139 | 356.5815 | 21 | 55 | 4 | 49 | 589.5892 | 1491.5141 | 68.7887 | 2.5298 | 0.90637 | 110 | 125.4094 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.7568 | 110.8709
CID=-2083073485 | 21 | 57.5 | 84.0892 | 4 | 51.5 | 10.3 | 1.7312 | 146.9698 | 27.9878 | 273.9586 | 435.076 | 414.2684 | 28848.6244 | 2.6254 | 0.039246 | 4.3807 | 84.0892 | 368.3673 | 21 | 57.5 | 4 | 51.5 | 589.5892 | 1584.4992 | 71.7108 | 2.6875 | 0.91086 | 110 | 140.264 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.7196 | 124.4588
CID=-2083073512 | 21 | 60 | 87.6666 | 4 | 54 | 10.8 | 1.7312 | 146.9698 | 27.9878 | 277.8855 | 436.3063 | 414.2684 | 29259.362 | 2.6451 | 0.041849 | 4.115 | 87.6666 | 360.7453 | 21 | 60 | 4 | 54 | 589.5892 | 1681.7842 | 74.1282 | 2.8525 | 0.91216 | 110 | 146.0222 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.373 | 126.9601
CID=-2083073415 | 21 | 62.5 | 90.8454 | 4 | 56.5 | 11.3 | 1.7312 | 146.9698 | 27.9878 | 281.8586 | 437.513 | 414.2684 | 29594.4825 | 2.6477 | 0.044453 | 3.8591 | 90.8453 | 350.583 | 21 | 62.5 | 4 | 56.5 | 589.5892 | 1783.5096 | 76.6144 | 3.025 | 0.91316 | 110 | 151.151 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7306 | 126.9601
CID=-2083073450 | 21 | 65 | 93.7194 | 4 | 59 | 11.8 | 1.7312 | 146.9698 | 27.9878 | 285.881 | 438.6964 | 414.2684 | 29934.2087 | 2.6429 | 0.047103 | 3.6205 | 93.7194 | 339.3088 | 21 | 65 | 4 | 59 | 589.5892 | 1889.8218 | 79.1166 | 3.2053 | 0.91396 | 110 | 155.7973 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.4786 | 126.9602
CID=-2083073609 | 21 | 67.5 | 96.9967 | 4 | 61.5 | 12.3 | 1.7312 | 146.9698 | 27.9878 | 289.9569 | 439.8569 | 414.2684 | 30286.3859 | 2.6344 | 0.050129 | 3.3763 | 96.9967 | 327.4894 | 21 | 67.5 | 4 | 61.5 | 589.5892 | 2000.8736 | 81.7945 | 3.3937 | 0.91475 | 110 | 161.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.0331 | 126.9602
CID=-2083073636 | 21 | 69.99 | 100.5574 | 4 | 63.99 | 12.798 | 1.7312 | 146.9698 | 27.9878 | 294.074 | 440.9902 | 414.2684 | 30669.1351 | 2.6274 | 0.05351 | 3.1405 | 100.5574 | 315.8016 | 21 | 69.99 | 4 | 63.99 | 589.5892 | 2116.3519 | 84.5549 | 3.5895 | 0.9155 | 110 | 166.8835 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.1546 | 126.9602
CID=-2083073539 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060370 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060401 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060432 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060463 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060246 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060277 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060308 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060339 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060122 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194060153 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177747 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177716 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177685 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177654 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177871 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177840 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177809 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019177778 | 24 | 40 | 27.2945 | 4 | 34 | 6.8 | 1.7302 | 146.5045 | 30.6472 | 247.5407 | 425.4661 | 415.8906 | 20652.6946 | 1.5846 | 0.013833 | 9.7735 | 27.2945 | 266.7617 | 24 | 40 | 4 | 34 | 645.7808 | 1016.593 | 50.8992 | 1.5742 | 0.81486 | 110 | 50.8917 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.4516 | 39.1373
CID=-2019177995 | 24 | 42.5 | 32.3605 | 4 | 36.5 | 7.3 | 1.7302 | 146.5045 | 30.6472 | 251.2145 | 426.8662 | 415.8906 | 21714.5928 | 1.7078 | 0.015847 | 8.6904 | 32.3605 | 281.226 | 24 | 42.5 | 4 | 36.5 | 645.7808 | 1086.4865 | 53.7345 | 1.6824 | 0.83544 | 110 | 58.8512 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.6006 | 48.1204
CID=-2019177964 | 24 | 45 | 38.6099 | 4 | 39 | 7.8 | 1.7302 | 146.5045 | 30.6472 | 254.9187 | 428.241 | 415.8906 | 22819.7885 | 1.8632 | 0.018374 | 7.768 | 38.6099 | 299.9226 | 24 | 45 | 4 | 39 | 645.7808 | 1159.9242 | 56.6262 | 1.7962 | 0.85537 | 110 | 68.5807 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7334 | 57.4863
CID=1356200840 | 24 | 47.5 | 45.3639 | 4 | 41.5 | 8.3 | 1.7302 | 146.5045 | 30.6472 | 258.655 | 429.5907 | 415.8906 | 23882.5114 | 2.0191 | 0.02121 | 6.9985 | 45.3639 | 317.4798 | 24 | 47.5 | 4 | 41.5 | 645.7808 | 1237.0237 | 59.5002 | 1.9155 | 0.87166 | 110 | 79.0715 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.8929 | 67.8348
CID=1356200871 | 24 | 50 | 52.622 | 4 | 44 | 8.8 | 1.7302 | 146.5045 | 30.6472 | 262.425 | 430.9154 | 415.8906 | 24881.9167 | 2.1784 | 0.024378 | 6.3529 | 52.622 | 334.3046 | 24 | 50 | 4 | 44 | 645.7808 | 1317.9055 | 62.3383 | 2.0408 | 0.88462 | 110 | 90.3789 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2397 | 79.0043
CID=1356200902 | 24 | 52.5 | 58.6035 | 4 | 46.5 | 9.3 | 1.7302 | 146.5045 | 30.6472 | 266.2308 | 432.2155 | 415.8906 | 25635.8 | 2.2866 | 0.027238 | 5.8394 | 58.6035 | 342.2075 | 24 | 52.5 | 4 | 46.5 | 645.7808 | 1402.6932 | 65.007 | 2.1721 | 0.89264 | 110 | 99.7474 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.8629 | 87.3441
CID=1356200933 | 24 | 55 | 67.1738 | 4 | 49 | 9.8 | 1.7302 | 146.5045 | 30.6472 | 270.0745 | 433.4912 | 415.8906 | 26565.8667 | 2.4505 | 0.031252 | 5.3194 | 67.1738 | 357.3209 | 24 | 55 | 4 | 49 | 645.7808 | 1491.5141 | 67.9442 | 2.3096 | 0.90108 | 110 | 113.2647 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4237 | 99.9239
CID=1356200716 | 24 | 57.5 | 76.9795 | 4 | 51.5 | 10.3 | 1.7302 | 146.5045 | 30.6472 | 273.9586 | 434.7427 | 415.8906 | 27514.8084 | 2.6326 | 0.035985 | 4.8538 | 76.9796 | 373.6469 | 24 | 57.5 | 4 | 51.5 | 645.7808 | 1584.4992 | 70.9279 | 2.4536 | 0.90759 | 110 | 128.8675 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.2609 | 113.6981
CID=1356200747 | 24 | 60 | 85.9725 | 4 | 54 | 10.8 | 1.7302 | 146.5045 | 30.6472 | 277.8855 | 435.9703 | 415.8906 | 28329.7484 | 2.7803 | 0.040668 | 4.463 | 85.9725 | 383.6936 | 24 | 60 | 4 | 54 | 645.7808 | 1681.7842 | 73.8044 | 2.6043 | 0.91157 | 110 | 143.2936 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.9849 | 126.9601
CID=1356200778 | 24 | 62.5 | 88.7168 | 4 | 56.5 | 11.3 | 1.7302 | 146.5045 | 30.6472 | 281.8586 | 437.1743 | 415.8906 | 28685.4362 | 2.7773 | 0.043023 | 4.1959 | 88.7168 | 372.2428 | 24 | 62.5 | 4 | 56.5 | 645.7808 | 1783.5096 | 76.1917 | 2.7618 | 0.91251 | 110 | 147.7155 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4735 | 126.9601
CID=1356200809 | 24 | 65 | 91.3961 | 4 | 59 | 11.8 | 1.7302 | 146.5045 | 30.6472 | 285.881 | 438.355 | 415.8906 | 29023.4534 | 2.7718 | 0.045512 | 3.9428 | 91.396 | 360.3552 | 24 | 65 | 4 | 59 | 645.7808 | 1889.8218 | 78.6187 | 2.9264 | 0.91332 | 110 | 152.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.832 | 126.9601
CID=1356200592 | 24 | 67.5 | 94.2511 | 4 | 61.5 | 12.3 | 1.7302 | 146.5045 | 30.6472 | 289.9569 | 439.5127 | 415.8906 | 29339.2822 | 2.7532 | 0.048258 | 3.6787 | 94.2511 | 346.7255 | 24 | 67.5 | 4 | 61.5 | 645.7808 | 2000.8736 | 81.24 | 3.0984 | 0.91409 | 110 | 156.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.542 | 126.9602
CID=1356200623 | 24 | 69.99 | 97.8217 | 4 | 63.99 | 12.798 | 1.7302 | 146.5045 | 30.6472 | 294.074 | 440.6434 | 415.8906 | 29705.6817 | 2.753 | 0.051536 | 3.4283 | 97.8218 | 335.3579 | 24 | 69.99 | 4 | 63.99 | 645.7808 | 2116.3519 | 83.9109 | 3.2772 | 0.91493 | 110 | 162.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68.6833 | 126.9601
CID=-1857037277 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037246 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037215 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037184 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037401 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037370 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037339 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037308 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037525 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857037494 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110950 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110981 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111012 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111043 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110826 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110857 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110888 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110919 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110702 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162110733 | 27 | 42.5 | 28.7369 | 4 | 36.5 | 7.3 | 1.7292 | 145.9744 | 33.5123 | 251.2145 | 426.563 | 417.481 | 20399.4628 | 1.7186 | 0.014486 | 9.9437 | 28.7369 | 285.7507 | 27 | 42.5 | 4 | 36.5 | 705.9244 | 1086.4865 | 53.2978 | 1.5391 | 0.82118 | 110 | 53.1686 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.346 | 41.1277
CID=-2051127167 | 27 | 45 | 32.7085 | 4 | 39 | 7.8 | 1.7292 | 145.9744 | 33.5123 | 254.9187 | 427.9352 | 417.481 | 21237.4004 | 1.8004 | 0.016172 | 8.948 | 32.7085 | 292.6764 | 27 | 45 | 4 | 39 | 705.9244 | 1159.9242 | 55.9083 | 1.6431 | 0.8367 | 110 | 59.3947 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5416 | 48.8753
CID=-2051127136 | 27 | 47.5 | 39.32 | 4 | 41.5 | 8.3 | 1.7292 | 145.9744 | 33.5123 | 258.655 | 429.2823 | 417.481 | 22373.486 | 1.969 | 0.018872 | 7.9535 | 39.32 | 312.7307 | 27 | 47.5 | 4 | 41.5 | 705.9244 | 1237.0237 | 58.8479 | 1.7523 | 0.85731 | 110 | 69.6837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0626 | 58.5775
CID=-2051127105 | 27 | 50 | 46.5251 | 4 | 44 | 8.8 | 1.7292 | 145.9744 | 33.5123 | 262.425 | 430.6045 | 417.481 | 23443.487 | 2.145 | 0.021927 | 7.1489 | 46.5251 | 332.6016 | 27 | 50 | 4 | 44 | 705.9244 | 1317.9055 | 61.7279 | 1.8669 | 0.87401 | 110 | 80.8771 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.8529 | 69.1973
CID=-2051127074 | 27 | 52.5 | 54.0322 | 4 | 46.5 | 9.3 | 1.7292 | 145.9744 | 33.5123 | 266.2308 | 431.902 | 417.481 | 24437.1385 | 2.3147 | 0.025258 | 6.4795 | 54.0322 | 350.1029 | 27 | 52.5 | 4 | 46.5 | 705.9244 | 1402.6932 | 64.5624 | 1.987 | 0.8867 | 110 | 92.5831 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.4146 | 80.6498
CID=-2051127291 | 27 | 55 | 60.5308 | 4 | 49 | 9.8 | 1.7292 | 145.9744 | 33.5123 | 270.0745 | 433.1751 | 417.481 | 25228.7664 | 2.4403 | 0.028387 | 5.9427 | 60.5308 | 359.7146 | 27 | 55 | 4 | 49 | 705.9244 | 1491.5141 | 67.2538 | 2.1129 | 0.89482 | 110 | 102.7773 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.1505 | 89.9111
CID=-2051127260 | 27 | 57.5 | 68.8607 | 4 | 51.5 | 10.3 | 1.7292 | 145.9744 | 33.5123 | 273.9586 | 434.4241 | 417.481 | 26110.8107 | 2.6009 | 0.032411 | 5.421 | 68.8606 | 373.291 | 27 | 57.5 | 4 | 51.5 | 705.9244 | 1584.4992 | 70.1285 | 2.2446 | 0.9024 | 110 | 115.9386 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.5589 | 102.1624
CID=-2051127229 | 27 | 60 | 78.4786 | 4 | 54 | 10.8 | 1.7292 | 145.9744 | 33.5123 | 277.8855 | 435.6491 | 417.481 | 26993.9669 | 2.7848 | 0.03719 | 4.9536 | 78.4786 | 388.7523 | 27 | 60 | 4 | 54 | 705.9244 | 1681.7842 | 73.0443 | 2.3824 | 0.90836 | 110 | 131.2648 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7067 | 116.2504
CID=-2051127198 | 27 | 62.5 | 86.2694 | 4 | 56.5 | 11.3 | 1.7292 | 145.9744 | 33.5123 | 281.8586 | 436.8505 | 417.481 | 27717.5637 | 2.9037 | 0.041505 | 4.5649 | 86.2694 | 393.8098 | 27 | 62.5 | 4 | 56.5 | 705.9244 | 1783.5096 | 75.8361 | 2.5265 | 0.91167 | 110 | 143.7715 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5787 | 126.9601
CID=-2051127415 | 27 | 65 | 89.1273 | 4 | 59 | 11.8 | 1.7292 | 145.9744 | 33.5123 | 285.881 | 438.0286 | 417.481 | 28072.2831 | 2.9023 | 0.043993 | 4.2853 | 89.1273 | 381.9402 | 27 | 65 | 4 | 59 | 705.9244 | 1889.8218 | 78.2518 | 2.6771 | 0.91264 | 110 | 148.3777 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.2946 | 126.9601
CID=-2051127384 | 27 | 67.5 | 91.7088 | 4 | 61.5 | 12.3 | 1.7292 | 145.9744 | 33.5123 | 289.9569 | 439.1838 | 417.481 | 28419.2199 | 2.8832 | 0.046537 | 4.0092 | 91.7088 | 367.6755 | 27 | 67.5 | 4 | 61.5 | 705.9244 | 2000.8736 | 80.7711 | 2.8344 | 0.91341 | 110 | 152.546 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.4575 | 126.9602
CID=1324251420 | 27 | 69.99 | 95.1241 | 4 | 63.99 | 12.798 | 1.7292 | 145.9744 | 33.5123 | 294.074 | 440.3118 | 417.481 | 28777.7217 | 2.8834 | 0.049644 | 3.7407 | 95.1241 | 355.8355 | 27 | 69.99 | 4 | 63.99 | 705.9244 | 2116.3519 | 83.3738 | 2.998 | 0.91431 | 110 | 158.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.2881 | 126.9602
CID=1324251451 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251482 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251513 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251296 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251327 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251358 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251389 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251172 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324251203 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986697 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986666 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986635 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986604 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986821 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986790 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986759 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986728 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986945 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888986914 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130161530 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130161561 | 30 | 45 | 26.2326 | 4 | 39 | 7.8 | 1.7283 | 145.3777 | 36.5977 | 254.9187 | 427.6403 | 419.0371 | 19411.5701 | 1.7034 | 0.013832 | 10.657 | 26.2326 | 279.5603 | 30 | 45 | 4 | 39 | 770.1963 | 1159.9242 | 54.9701 | 1.506 | 0.80995 | 110 | 49.2085 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2285 | 35.2368
CID=1130161592 | 30 | 47.5 | 33.4247 | 4 | 41.5 | 8.3 | 1.7283 | 145.3777 | 36.5977 | 258.655 | 428.9849 | 419.0371 | 20831.0885 | 1.9165 | 0.01664 | 9.1958 | 33.4247 | 307.3681 | 30 | 47.5 | 4 | 41.5 | 770.1963 | 1237.0237 | 58.1364 | 1.6061 | 0.83922 | 110 | 60.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.3626 | 49.4867
CID=1130161623 | 30 | 50 | 40.1799 | 4 | 44 | 8.8 | 1.7283 | 145.3777 | 36.5977 | 262.425 | 430.3047 | 419.0371 | 21952.0876 | 2.0923 | 0.019445 | 8.1553 | 40.1799 | 327.6811 | 30 | 50 | 4 | 44 | 770.1963 | 1317.9055 | 61.0663 | 1.7111 | 0.85959 | 110 | 71.0191 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.758 | 59.6018
CID=1130161406 | 30 | 52.5 | 47.4919 | 4 | 46.5 | 9.3 | 1.7283 | 145.3777 | 36.5977 | 266.2308 | 431.5997 | 419.0371 | 22992.7284 | 2.2742 | 0.022604 | 7.3173 | 47.4918 | 347.5134 | 30 | 52.5 | 4 | 46.5 | 770.1963 | 1402.6932 | 63.9378 | 1.8212 | 0.87589 | 110 | 82.3811 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.5286 | 70.4551
CID=1130161437 | 30 | 55 | 55.2363 | 4 | 49 | 9.8 | 1.7283 | 145.3777 | 36.5977 | 270.0745 | 432.8703 | 419.0371 | 23991.9486 | 2.4523 | 0.026098 | 6.6134 | 55.2363 | 365.2987 | 30 | 55 | 4 | 49 | 770.1963 | 1491.5141 | 66.79 | 1.9365 | 0.88838 | 110 | 94.4673 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2091 | 82.2635
CID=1130161468 | 30 | 57.5 | 63.5401 | 4 | 51.5 | 10.3 | 1.7283 | 145.3777 | 36.5977 | 273.9586 | 434.1168 | 419.0371 | 24927.7312 | 2.633 | 0.030006 | 6.0119 | 63.5401 | 381.9984 | 30 | 57.5 | 4 | 51.5 | 770.1963 | 1584.4992 | 69.6289 | 2.0573 | 0.89787 | 110 | 107.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0207 | 95.0594
CID=1130161499 | 30 | 60 | 70.2361 | 4 | 54 | 10.8 | 1.7283 | 145.3777 | 36.5977 | 277.8855 | 435.3393 | 419.0371 | 25630.1812 | 2.7508 | 0.033502 | 5.5282 | 70.2361 | 388.2819 | 30 | 60 | 4 | 54 | 770.1963 | 1681.7842 | 72.3208 | 2.1836 | 0.90341 | 110 | 118.1222 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.1156 | 104.3567
CID=1130161282 | 30 | 62.5 | 79.9309 | 4 | 56.5 | 11.3 | 1.7283 | 145.3777 | 36.5977 | 281.8586 | 436.5383 | 419.0371 | 26501.0415 | 2.9377 | 0.03844 | 5.0418 | 79.9309 | 402.993 | 30 | 62.5 | 4 | 56.5 | 770.1963 | 1783.5096 | 75.2431 | 2.3157 | 0.90907 | 110 | 133.5904 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2449 | 118.617
CID=1130161313 | 30 | 65 | 87.1409 | 4 | 59 | 11.8 | 1.7283 | 145.3777 | 36.5977 | 285.881 | 437.7139 | 419.0371 | 27141.4127 | 3.0496 | 0.042641 | 4.66 | 87.1409 | 406.0726 | 30 | 65 | 4 | 59 | 770.1963 | 1889.8218 | 77.9484 | 2.4537 | 0.91198 | 110 | 145.1752 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.3217 | 126.9601
CID=-2083076587 | 30 | 67.5 | 89.8689 | 4 | 61.5 | 12.3 | 1.7283 | 145.3777 | 36.5977 | 289.9569 | 438.8665 | 419.0371 | 27499.7213 | 3.0348 | 0.045175 | 4.3589 | 89.8689 | 391.7316 | 30 | 67.5 | 4 | 61.5 | 770.1963 | 2000.8736 | 80.4349 | 2.5979 | 0.91287 | 110 | 149.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.7777 | 126.9602
CID=-2083076556 | 30 | 69.99 | 92.8516 | 4 | 63.99 | 12.798 | 1.7283 | 145.3777 | 36.5977 | 294.074 | 439.9919 | 419.0371 | 27858.1997 | 3.024 | 0.048004 | 4.0698 | 92.8516 | 377.8871 | 30 | 69.99 | 4 | 63.99 | 770.1963 | 2116.3519 | 82.9854 | 2.7478 | 0.91373 | 110 | 154.3935 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.743 | 126.9602
CID=-2083076525 | -18 | -5 | 9.775 | 4 | -11 | 0 | 1.7524 | 147.8757 | 7.2169 | 185.3801 | 401.7246 | 391.078 | 22679.942 | 0.44732 | 0.0067892 | 9.4131 | 9.775 | 92.0129 | -18 | -5 | 4 | -11 | 144.6004 | 243.3424 | 10.9376 | 1.6829 | 0.69668 | 110 | 21.3177 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5498 | 11.5167
CID=-2083076494 | -18 | -2.5 | 12.3596 | 4 | -8.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 188.676 | 403.6805 | 391.078 | 24318.7443 | 0.50801 | 0.0075242 | 8.3193 | 12.3596 | 102.8232 | -18 | -2.5 | 4 | -8.5 | 144.6004 | 267.1911 | 14.5044 | 1.8478 | 0.72017 | 110 | 26.0751 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.577 | 14.6204
CID=-2083076711 | -18 | 0 | 15.3325 | 4 | -6 | 0 | 1.7524 | 147.8757 | 7.2169 | 191.9873 | 405.6071 | 391.078 | 25862.3817 | 0.57198 | 0.0084248 | 7.4271 | 15.3325 | 113.8757 | -18 | 0 | 4 | -6 | 144.6004 | 292.8032 | 17.9896 | 2.0249 | 0.74415 | 110 | 31.3047 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.7893 | 18.1802
CID=-2083076680 | -18 | 2.5 | 17.9722 | 4 | -3.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 195.3144 | 407.5045 | 391.078 | 27058.8433 | 0.61866 | 0.0092884 | 6.7388 | 17.9722 | 121.1102 | -18 | 2.5 | 4 | -3.5 | 144.6004 | 320.2635 | 21.1213 | 2.2148 | 0.76302 | 110 | 35.7867 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8511 | 21.3458
CID=-2083076649 | -18 | 5 | 21.7178 | 4 | -1 | 0 | 1.7524 | 147.8757 | 7.2169 | 198.6579 | 409.3731 | 391.078 | 28467.9954 | 0.6838 | 0.010507 | 6.0585 | 21.7178 | 131.5778 | -18 | 5 | 4 | -1 | 144.6004 | 349.6586 | 24.7421 | 2.4181 | 0.78637 | 110 | 41.961 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5588 | 25.7708
CID=-2083076618 | -18 | 7.5 | 25.7573 | 4 | 1.5 | 0.3 | 1.7524 | 147.8757 | 7.2169 | 202.0183 | 411.2128 | 391.078 | 29746.4895 | 0.74685 | 0.011868 | 5.4819 | 25.7573 | 141.1991 | -18 | 7.5 | 4 | 1.5 | 144.6004 | 381.0767 | 28.3308 | 2.6354 | 0.80768 | 110 | 48.4527 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.097 | 30.644
CID=-2083076835 | -18 | 10 | 30.2408 | 4 | 4 | 0.8 | 1.7524 | 147.8757 | 7.2169 | 205.396 | 413.024 | 391.078 | 30988.7907 | 0.80761 | 0.01342 | 4.9588 | 30.2408 | 149.9584 | -18 | 10 | 4 | 4 | 144.6004 | 414.6075 | 32.1074 | 2.8673 | 0.82737 | 110 | 55.5326 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0916 | 35.9571
CID=-2083076804 | -18 | 12.5 | 33.7706 | 4 | 6.5 | 1.3 | 1.7524 | 147.8757 | 7.2169 | 208.7918 | 414.8068 | 391.078 | 31848.1697 | 0.84912 | 0.014746 | 4.5833 | 33.7706 | 154.7825 | -18 | 12.5 | 4 | 6.5 | 144.6004 | 450.3422 | 35.2035 | 3.1144 | 0.84042 | 110 | 61.0521 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2624 | 39.94
CID=1194061391 | -18 | 15 | 38.5128 | 4 | 9 | 1.8 | 1.7524 | 147.8757 | 7.2169 | 212.2062 | 416.5615 | 391.078 | 32821.9114 | 0.90724 | 0.016505 | 4.2136 | 38.5128 | 162.2794 | -18 | 15 | 4 | 9 | 144.6004 | 488.3739 | 38.6519 | 3.3774 | 0.8551 | 110 | 68.4298 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.7059 | 45.4484
CID=1194061488 | -18 | 17.5 | 43.0768 | 4 | 11.5 | 2.3 | 1.7524 | 147.8757 | 7.2169 | 215.6398 | 418.2881 | 391.078 | 33814.4505 | 0.95855 | 0.018281 | 3.9039 | 43.0769 | 168.166 | -18 | 17.5 | 4 | 11.5 | 144.6004 | 528.7968 | 41.8886 | 3.657 | 0.86666 | 110 | 75.5179 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3419 | 50.6552
CID=1194061585 | -18 | 20 | 44.578 | 4 | 14 | 2.8 | 1.7524 | 147.8757 | 7.2169 | 219.0933 | 419.9871 | 391.078 | 34195.7151 | 0.96966 | 0.019136 | 3.741 | 44.578 | 166.7658 | -18 | 20 | 4 | 14 | 144.6004 | 571.7069 | 43.6911 | 3.9537 | 0.87 | 110 | 77.8501 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3788 | 51.6444
CID=1194061426 | -18 | 22.5 | 45.2714 | 4 | 16.5 | 3.3 | 1.7524 | 147.8757 | 7.2169 | 222.5675 | 421.6585 | 391.078 | 34442.2028 | 0.96542 | 0.01976 | 3.5935 | 45.2714 | 162.6841 | -18 | 22.5 | 4 | 16.5 | 144.6004 | 617.2019 | 45.3961 | 4.2683 | 0.87147 | 110 | 78.9277 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.5651 | 51.5068
CID=1194061267 | -18 | 25 | 46.4134 | 4 | 19 | 3.8 | 1.7524 | 147.8757 | 7.2169 | 226.0633 | 423.3026 | 391.078 | 34764.339 | 0.961 | 0.020566 | 3.4167 | 46.4134 | 158.5786 | -18 | 25 | 4 | 19 | 144.6004 | 665.3809 | 47.5776 | 4.6015 | 0.87379 | 110 | 80.7034 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9668 | 51.5623
CID=1194061364 | -18 | 27.5 | 47.8111 | 4 | 21.5 | 4.3 | 1.7524 | 147.8757 | 7.2169 | 229.5813 | 424.9196 | 391.078 | 35156.5688 | 0.95545 | 0.021498 | 3.2273 | 47.8111 | 154.3017 | -18 | 27.5 | 4 | 21.5 | 144.6004 | 716.3449 | 50.085 | 4.954 | 0.87649 | 110 | 82.878 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.6287 | 51.8719
CID=1194061461 | -18 | 30 | 49.161 | 4 | 24 | 4.8 | 1.7524 | 147.8757 | 7.2169 | 233.1226 | 426.5097 | 391.078 | 35520.6775 | 0.95033 | 0.022459 | 3.0534 | 49.1609 | 150.1095 | -18 | 30 | 4 | 24 | 144.6004 | 770.1963 | 52.5546 | 5.3264 | 0.87894 | 110 | 84.98 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.9637 | 51.8934
CID=1194061302 | -18 | 32.5 | 50.6167 | 4 | 26.5 | 5.3 | 1.7524 | 147.8757 | 7.2169 | 236.688 | 428.0733 | 391.078 | 35935.4953 | 0.94041 | 0.023505 | 2.8684 | 50.6167 | 145.1903 | -18 | 32.5 | 4 | 26.5 | 144.6004 | 827.0396 | 55.3884 | 5.7195 | 0.88143 | 109.1875 | 87.2491 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.2998 | 51.389
CID=1194061143 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194061240 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176726 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176629 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176532 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176691 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176850 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176753 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176656 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176815 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176974 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019176877 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356201861 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356201958 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356202055 | -18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356201896 | -15 | -5 | 0 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356201737 | -15 | -2.5 | 10.0917 | 4 | -8.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 188.676 | 402.9994 | 392.9623 | 22178.477 | 0.48518 | 0.0069088 | 9.8215 | 10.0917 | 99.1156 | -15 | -2.5 | 4 | -8.5 | 163.9401 | 267.1911 | 12.8024 | 1.6298 | 0.6997 | 110 | 21.9135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.9292 | 11.8126
CID=1356201834 | -15 | 0 | 12.7985 | 4 | -6 | 0 | 1.7499 | 148.1062 | 8.1279 | 191.9873 | 404.9188 | 392.9623 | 23790.479 | 0.54901 | 0.0076889 | 8.6212 | 12.7985 | 110.3382 | -15 | 0 | 4 | -6 | 163.9401 | 292.8032 | 16.3807 | 1.786 | 0.7239 | 110 | 26.8618 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7776 | 15.1388
CID=1356201931 | -15 | 2.5 | 15.8928 | 4 | -3.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 195.3144 | 406.8092 | 392.9623 | 25322.7115 | 0.61849 | 0.0086366 | 7.6917 | 15.8928 | 122.2435 | -15 | 2.5 | 4 | -3.5 | 163.9401 | 320.2635 | 19.7609 | 1.9535 | 0.74833 | 110 | 32.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.9172 | 18.8847
CID=1356201772 | -15 | 5 | 19.4127 | 4 | -1 | 0 | 1.7499 | 148.1062 | 8.1279 | 198.6579 | 408.6707 | 392.9623 | 26772.1018 | 0.68686 | 0.0097591 | 6.8749 | 19.4127 | 133.4598 | -15 | 5 | 4 | -1 | 163.9401 | 349.6586 | 23.2653 | 2.1328 | 0.77244 | 110 | 38.1833 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3095 | 23.1137
CID=1356201613 | -15 | 7.5 | 22.5231 | 4 | 1.5 | 0.3 | 1.7499 | 148.1062 | 8.1279 | 202.0183 | 410.5034 | 392.9623 | 27895.2186 | 0.73913 | 0.01082 | 6.2662 | 22.5231 | 141.1332 | -15 | 7.5 | 4 | 1.5 | 163.9401 | 381.0767 | 26.3333 | 2.3245 | 0.79092 | 110 | 43.2666 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.7669 | 26.7752
CID=1356201710 | -15 | 10 | 26.9448 | 4 | 4 | 0.8 | 1.7499 | 148.1062 | 8.1279 | 205.396 | 412.3077 | 392.9623 | 29220.2094 | 0.81282 | 0.012312 | 5.6582 | 26.9448 | 152.4577 | -15 | 10 | 4 | 4 | 163.9401 | 414.6075 | 29.8835 | 2.529 | 0.81327 | 110 | 50.3381 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7699 | 32.0031
CID=-1857036256 | -15 | 12.5 | 31.5604 | 4 | 6.5 | 1.3 | 1.7499 | 148.1062 | 8.1279 | 208.7918 | 414.0836 | 392.9623 | 30435.0163 | 0.87799 | 0.013928 | 5.1235 | 31.5604 | 161.7005 | -15 | 12.5 | 4 | 6.5 | 163.9401 | 450.3422 | 33.5043 | 2.747 | 0.83248 | 110 | 57.6002 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.601 | 37.5469
CID=-1857036159 | -15 | 15 | 35.4382 | 4 | 9 | 1.8 | 1.7499 | 148.1062 | 8.1279 | 212.2062 | 415.8315 | 392.9623 | 31345.0888 | 0.92693 | 0.015385 | 4.7279 | 35.4382 | 167.5488 | -15 | 15 | 4 | 9 | 163.9401 | 488.3739 | 36.5803 | 2.979 | 0.84592 | 110 | 63.6497 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8508 | 41.9673
CID=-1857036062 | -15 | 17.5 | 40.4643 | 4 | 11.5 | 2.3 | 1.7499 | 148.1062 | 8.1279 | 215.6398 | 417.5513 | 392.9623 | 32346.9703 | 0.98688 | 0.017264 | 4.3247 | 40.4643 | 174.9969 | -15 | 17.5 | 4 | 11.5 | 163.9401 | 528.7968 | 40.124 | 3.2255 | 0.86032 | 110 | 71.4607 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.3412 | 47.8386
CID=-1857036221 | -15 | 20 | 45.4884 | 4 | 14 | 2.8 | 1.7499 | 148.1062 | 8.1279 | 219.0933 | 419.2435 | 392.9623 | 33236.2126 | 1.0466 | 0.019221 | 4.0002 | 45.4884 | 181.9634 | -15 | 20 | 4 | 14 | 163.9401 | 571.7069 | 43.3534 | 3.4873 | 0.87192 | 110 | 79.265 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.1691 | 53.5948
CID=-1857036380 | -15 | 22.5 | 49.8499 | 4 | 16.5 | 3.3 | 1.7499 | 148.1062 | 8.1279 | 222.5675 | 420.9082 | 392.9623 | 34105.7848 | 1.0952 | 0.021045 | 3.7436 | 49.8499 | 186.6181 | -15 | 22.5 | 4 | 16.5 | 163.9401 | 617.2019 | 46.1744 | 3.7648 | 0.88014 | 110 | 86.0536 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0585 | 58.447
CID=-1857036283 | -15 | 25 | 51.0623 | 4 | 19 | 3.8 | 1.7499 | 148.1062 | 8.1279 | 226.0633 | 422.5457 | 392.9623 | 34404.8849 | 1.0989 | 0.021893 | 3.5919 | 51.0623 | 183.4112 | -15 | 25 | 4 | 19 | 163.9401 | 665.3809 | 47.9377 | 4.0587 | 0.88216 | 110 | 87.9442 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8402 | 58.803
CID=-1857036186 | -15 | 27.5 | 51.7706 | 4 | 21.5 | 4.3 | 1.7499 | 148.1062 | 8.1279 | 229.5813 | 424.156 | 392.9623 | 34640.4495 | 1.0908 | 0.022607 | 3.4423 | 51.7705 | 178.2123 | -15 | 27.5 | 4 | 21.5 | 163.9401 | 716.3449 | 49.7631 | 4.3696 | 0.8833 | 110 | 89.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.3546 | 58.5759
CID=-1857036345 | -15 | 30 | 52.5599 | 4 | 24 | 4.8 | 1.7499 | 148.1062 | 8.1279 | 233.1226 | 425.7396 | 392.9623 | 34892.3231 | 1.0775 | 0.023384 | 3.2768 | 52.5599 | 172.2266 | -15 | 30 | 4 | 24 | 163.9401 | 770.1963 | 51.9017 | 4.698 | 0.88452 | 110 | 90.2819 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.422 | 57.9392
CID=-1857036504 | -15 | 32.5 | 54.1696 | 4 | 26.5 | 5.3 | 1.7499 | 148.1062 | 8.1279 | 236.688 | 427.2966 | 392.9623 | 35275.6194 | 1.0734 | 0.024495 | 3.0966 | 54.1696 | 167.742 | -15 | 32.5 | 4 | 26.5 | 163.9401 | 827.0396 | 54.397 | 5.0448 | 0.8869 | 110 | 92.798 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.4958 | 58.3942
CID=-1857036407 | -15 | 35 | 56.2234 | 4 | 29 | 5.8 | 1.7499 | 148.1062 | 8.1279 | 240.2788 | 428.8272 | 392.9623 | 35700.6276 | 1.0759 | 0.025825 | 2.9217 | 56.2234 | 164.266 | -15 | 35 | 4 | 29 | 163.9401 | 886.981 | 57.0029 | 5.4104 | 0.88969 | 110 | 96.0135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0343 | 58.9531
CID=1162111971 | -15 | 37.5 | 56.284 | 4 | 31.5 | 6.3 | 1.7499 | 148.1062 | 8.1279 | 243.8959 | 430.3317 | 392.9623 | 35975.3625 | 1.0355 | 0.026474 | 2.7426 | 56.284 | 154.363 | -15 | 37.5 | 4 | 31.5 | 163.9401 | 950.1287 | 59.8406 | 5.7956 | 0.88977 | 108.8907 | 96.1084 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.3815 | 56.5848
CID=1162112068 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162112165 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162112006 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111847 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111944 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162112041 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111882 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111723 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162111820 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051126146 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051126049 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051125952 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051126111 | -15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051126270 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051126173 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051126076 | -12 | 0 | 10.6627 | 4 | -6 | 0 | 1.7476 | 148.2918 | 9.1273 | 191.9873 | 404.2823 | 394.8346 | 21830.8156 | 0.53287 | 0.0070924 | 10.1374 | 10.6627 | 108.092 | -12 | 0 | 4 | -6 | 185.2442 | 292.8032 | 14.9622 | 1.5806 | 0.70504 | 110 | 22.9779 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4538 | 12.3991
CID=-2051126235 | -12 | 2.5 | 13.2162 | 4 | -3.5 | 0 | 1.7476 | 148.2918 | 9.1273 | 195.3144 | 406.166 | 394.8346 | 23275.9456 | 0.59172 | 0.0078524 | 8.933 | 13.2162 | 118.0598 | -12 | 2.5 | 4 | -3.5 | 185.2442 | 320.2635 | 18.2908 | 1.7289 | 0.72739 | 110 | 27.6053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9439 | 15.6403
CID=-2051126394 | -12 | 5 | 16.4908 | 4 | -1 | 0 | 1.7476 | 148.2918 | 9.1273 | 198.6579 | 408.021 | 394.8346 | 24821.378 | 0.66739 | 0.0088637 | 7.9393 | 16.4908 | 130.9256 | -12 | 5 | 4 | -1 | 185.2442 | 349.6586 | 21.6558 | 1.8876 | 0.75269 | 110 | 33.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3298 | 19.5445
CID=-2051126297 | -12 | 7.5 | 20.1239 | 4 | 1.5 | 0.3 | 1.7476 | 148.2918 | 9.1273 | 202.0183 | 409.8472 | 394.8346 | 26236.1051 | 0.74165 | 0.010035 | 7.1061 | 20.1239 | 143.002 | -12 | 7.5 | 4 | 1.5 | 185.2442 | 381.0767 | 25.0137 | 2.0572 | 0.77689 | 110 | 39.3558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5649 | 23.9769
CID=1324252441 | -12 | 10 | 23.3531 | 4 | 4 | 0.8 | 1.7476 | 148.2918 | 9.1273 | 205.396 | 411.6451 | 394.8346 | 27351.0452 | 0.79765 | 0.011146 | 6.4705 | 23.3531 | 151.1054 | -12 | 10 | 4 | 4 | 185.2442 | 414.6075 | 28.0231 | 2.2382 | 0.79544 | 110 | 44.6058 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.993 | 27.8065
CID=1324252538 | -12 | 12.5 | 27.9572 | 4 | 6.5 | 1.3 | 1.7476 | 148.2918 | 9.1273 | 208.7918 | 413.4146 | 394.8346 | 28680.7564 | 0.87617 | 0.012714 | 5.8305 | 27.9572 | 163.0042 | -12 | 12.5 | 4 | 6.5 | 185.2442 | 450.3422 | 31.5293 | 2.4311 | 0.81781 | 110 | 51.9391 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1391 | 33.2299
CID=1324252635 | -12 | 15 | 32.8341 | 4 | 9 | 1.8 | 1.7476 | 148.2918 | 9.1273 | 212.2062 | 415.1561 | 394.8346 | 29880.5708 | 0.95106 | 0.014434 | 5.29 | 32.834 | 173.6905 | -12 | 15 | 4 | 9 | 185.2442 | 488.3739 | 34.9842 | 2.6364 | 0.83715 | 110 | 59.5908 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0304 | 39.1019
CID=1324252476 | -12 | 17.5 | 38.234 | 4 | 11.5 | 2.3 | 1.7476 | 148.2918 | 9.1273 | 215.6398 | 416.8697 | 394.8346 | 31056.2224 | 1.0235 | 0.016389 | 4.7971 | 38.234 | 183.4136 | -12 | 17.5 | 4 | 11.5 | 185.2442 | 528.7968 | 38.62 | 2.8546 | 0.85431 | 110 | 67.9967 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.4121 | 45.5079
CID=1324252317 | -12 | 20 | 42.3798 | 4 | 14 | 2.8 | 1.7476 | 148.2918 | 9.1273 | 219.0933 | 418.5557 | 394.8346 | 31855.8152 | 1.072 | 0.018028 | 4.4452 | 42.3798 | 188.387 | -12 | 20 | 4 | 14 | 185.2442 | 571.7069 | 41.5906 | 3.0862 | 0.86504 | 110 | 74.4353 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.032 | 50.1624
CID=1324252414 | -12 | 22.5 | 48.0526 | 4 | 16.5 | 3.3 | 1.7476 | 148.2918 | 9.1273 | 222.5675 | 420.2141 | 394.8346 | 32785.8496 | 1.1411 | 0.020233 | 4.0908 | 48.0526 | 196.5716 | -12 | 22.5 | 4 | 16.5 | 185.2442 | 617.2019 | 44.945 | 3.3318 | 0.87694 | 110 | 83.2539 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.8538 | 56.7855
CID=1324252511 | -12 | 25 | 53.4757 | 4 | 19 | 3.8 | 1.7476 | 148.2918 | 9.1273 | 226.0633 | 421.8454 | 394.8346 | 33700.7881 | 1.2016 | 0.022451 | 3.7922 | 53.4757 | 202.7926 | -12 | 25 | 4 | 19 | 185.2442 | 665.3809 | 48.1077 | 3.5919 | 0.88589 | 110 | 91.713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9272 | 62.9919
CID=1324252352 | -12 | 27.5 | 56.4078 | 4 | 21.5 | 4.3 | 1.7476 | 148.2918 | 9.1273 | 229.5813 | 423.4496 | 394.8346 | 34233.6837 | 1.2312 | 0.023923 | 3.6071 | 56.4078 | 203.468 | -12 | 27.5 | 4 | 21.5 | 185.2442 | 716.3449 | 50.2477 | 3.867 | 0.88993 | 110 | 96.3025 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.6206 | 65.6702
CID=1324252193 | -12 | 30 | 57.5325 | 4 | 24 | 4.8 | 1.7476 | 148.2918 | 9.1273 | 233.1226 | 425.027 | 394.8346 | 34495.4058 | 1.2314 | 0.024837 | 3.4612 | 57.5325 | 199.1319 | -12 | 30 | 4 | 24 | 185.2442 | 770.1963 | 52.0253 | 4.1577 | 0.89135 | 110 | 98.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.3085 | 65.9405
CID=1324252290 | -12 | 32.5 | 58.5044 | 4 | 26.5 | 5.3 | 1.7476 | 148.2918 | 9.1273 | 236.688 | 426.5779 | 394.8346 | 34742.4304 | 1.2245 | 0.025741 | 3.3099 | 58.5044 | 193.6459 | -12 | 32.5 | 4 | 26.5 | 185.2442 | 827.0396 | 53.963 | 4.4646 | 0.89253 | 110 | 99.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.6126 | 65.8016
CID=-1888985676 | -12 | 35 | 59.83 | 4 | 29 | 5.8 | 1.7476 | 148.2918 | 9.1273 | 240.2788 | 428.1024 | 394.8346 | 35063.8616 | 1.2134 | 0.02682 | 3.1346 | 59.83 | 187.5404 | -12 | 35 | 4 | 29 | 185.2442 | 886.981 | 56.3388 | 4.7882 | 0.89405 | 110 | 101.6749 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.4028 | 65.639
CID=-1888985579 | -12 | 37.5 | 61.5792 | 4 | 31.5 | 6.3 | 1.7476 | 148.2918 | 9.1273 | 243.8959 | 429.6009 | 394.8346 | 35422.4635 | 1.2104 | 0.028112 | 2.9669 | 61.5792 | 182.6998 | -12 | 37.5 | 4 | 31.5 | 185.2442 | 950.1287 | 58.7696 | 5.1291 | 0.89593 | 110 | 104.4279 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.9875 | 66.1098
CID=-1888985482 | -12 | 40 | 63.5416 | 4 | 34 | 6.8 | 1.7476 | 148.2918 | 9.1273 | 247.5407 | 431.0734 | 394.8346 | 35811.8501 | 1.2056 | 0.029555 | 2.7946 | 63.5416 | 177.5762 | -12 | 40 | 4 | 34 | 185.2442 | 1016.593 | 61.4407 | 5.4879 | 0.89788 | 109.9612 | 107.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3235 | 55.8685 | 66.0993
CID=-1888985641 | -12 | 42.5 | 63.7548 | 4 | 36.5 | 7.3 | 1.7476 | 148.2918 | 9.1273 | 251.2145 | 432.5204 | 394.8346 | 36098.7375 | 1.1653 | 0.030394 | 2.625 | 63.7548 | 167.3554 | -12 | 42.5 | 4 | 36.5 | 185.2442 | 1086.4865 | 64.2433 | 5.8652 | 0.89808 | 108.7038 | 107.8586 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1387 | 63.9602
CID=-1888985800 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888985703 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888985606 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888985765 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888985924 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888985827 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162551 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162648 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162745 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162586 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162427 | -12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162524 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162621 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162462 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130162303 | -9 | 2.5 | 9.2476 | 4 | -3.5 | 0 | 1.7455 | 148.4312 | 10.2212 | 195.3144 | 405.5712 | 396.6938 | 20326.4706 | 0.51524 | 0.0068147 | 11.22 | 9.2476 | 103.7578 | -9 | 2.5 | 4 | -3.5 | 208.6448 | 320.2635 | 15.5187 | 1.535 | 0.69155 | 110 | 20.3169 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.8776 | 10.3709
CID=1130162400 | -9 | 5 | 13.5604 | 4 | -1 | 0 | 1.7455 | 148.4312 | 10.2212 | 198.6579 | 407.4201 | 396.6938 | 22753.7839 | 0.63684 | 0.0080011 | 9.3004 | 13.5604 | 126.117 | -9 | 5 | 4 | -1 | 208.6448 | 349.6586 | 20.1288 | 1.6759 | 0.73022 | 110 | 28.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9672 | 16.0914
CID=-2083075566 | -9 | 7.5 | 16.9792 | 4 | 1.5 | 0.3 | 1.7455 | 148.4312 | 10.2212 | 202.0183 | 409.2404 | 396.6938 | 24279.5828 | 0.71623 | 0.0090663 | 8.212 | 16.9792 | 139.4334 | -9 | 7.5 | 4 | 1.5 | 208.6448 | 381.0767 | 23.5256 | 1.8264 | 0.75617 | 110 | 34.1157 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3549 | 20.1873
CID=-2083075469 | -9 | 10 | 20.8526 | 4 | 4 | 0.8 | 1.7455 | 148.4312 | 10.2212 | 205.396 | 411.0322 | 396.6938 | 25716.7592 | 0.80035 | 0.010322 | 7.3422 | 20.8526 | 153.1045 | -9 | 10 | 4 | 4 | 208.6448 | 414.6075 | 26.8151 | 1.9871 | 0.7813 | 110 | 40.5504 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9222 | 24.8293
CID=-2083075372 | -9 | 12.5 | 24.6572 | 4 | 6.5 | 1.3 | 1.7455 | 148.4312 | 10.2212 | 208.7918 | 412.7959 | 396.6938 | 26941.7166 | 0.86998 | 0.011619 | 6.6298 | 24.6572 | 163.4718 | -9 | 12.5 | 4 | 6.5 | 208.6448 | 450.3422 | 29.9887 | 2.1584 | 0.80224 | 110 | 46.698 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.5321 | 29.3656
CID=-2083075531 | -9 | 15 | 28.8888 | 4 | 9 | 1.8 | 1.7455 | 148.4312 | 10.2212 | 212.2062 | 414.5315 | 396.6938 | 28114.4976 | 0.94277 | 0.013101 | 6.0207 | 28.8888 | 173.9303 | -9 | 15 | 4 | 9 | 208.6448 | 488.3739 | 33.1579 | 2.3407 | 0.82183 | 110 | 53.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3102 | 34.4149
CID=-2083075690 | -9 | 17.5 | 34.2283 | 4 | 11.5 | 2.3 | 1.7455 | 148.4312 | 10.2212 | 215.6398 | 416.2392 | 396.6938 | 29361.2778 | 1.0304 | 0.014987 | 5.4502 | 34.2283 | 186.5497 | -9 | 17.5 | 4 | 11.5 | 208.6448 | 528.7968 | 36.5918 | 2.5344 | 0.84197 | 110 | 61.7655 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7558 | 40.7191
CID=-2083075593 | -9 | 20 | 39.7633 | 4 | 14 | 2.8 | 1.7455 | 148.4312 | 10.2212 | 219.0933 | 417.9194 | 396.6938 | 30509.8777 | 1.1076 | 0.017016 | 4.947 | 39.7633 | 196.7082 | -9 | 20 | 4 | 14 | 208.6448 | 571.7069 | 40.0916 | 2.7401 | 0.85849 | 110 | 70.3721 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9978 | 47.3518
CID=-2083075496 | -9 | 22.5 | 44.4118 | 4 | 16.5 | 3.3 | 1.7455 | 148.4312 | 10.2212 | 222.5675 | 419.5721 | 396.6938 | 31374.8076 | 1.1663 | 0.018847 | 4.5727 | 44.4118 | 203.0832 | -9 | 22.5 | 4 | 16.5 | 208.6448 | 617.2019 | 43.0841 | 2.9581 | 0.86964 | 110 | 77.5918 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.6774 | 52.6566
CID=-2083075655 | -9 | 25 | 50.2319 | 4 | 19 | 3.8 | 1.7455 | 148.4312 | 10.2212 | 226.0633 | 421.1976 | 396.6938 | 32311.1313 | 1.2343 | 0.021142 | 4.1928 | 50.2319 | 210.6116 | -9 | 25 | 4 | 19 | 208.6448 | 665.3809 | 46.4862 | 3.1891 | 0.88079 | 110 | 86.6491 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5308 | 59.4656
CID=-2083075814 | -9 | 27.5 | 56.2569 | 4 | 21.5 | 4.3 | 1.7455 | 148.4312 | 10.2212 | 229.5813 | 422.7961 | 396.6938 | 33148.6521 | 1.3067 | 0.023606 | 3.8816 | 56.2569 | 218.3646 | -9 | 27.5 | 4 | 21.5 | 208.6448 | 716.3449 | 49.6365 | 3.4333 | 0.88974 | 110 | 96.0659 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.7566 | 66.4236
CID=-2083075717 | -9 | 30 | 62.2939 | 4 | 24 | 4.8 | 1.7455 | 148.4312 | 10.2212 | 233.1226 | 424.3678 | 396.6938 | 34081.4196 | 1.3744 | 0.026186 | 3.6088 | 62.2939 | 224.8091 | -9 | 30 | 4 | 24 | 208.6448 | 770.1963 | 52.6994 | 3.6914 | 0.89666 | 110 | 105.5541 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1758 | 73.3333
CID=1194058192 | -9 | 32.5 | 63.6415 | 4 | 26.5 | 5.3 | 1.7455 | 148.4312 | 10.2212 | 236.688 | 425.913 | 396.6938 | 34349.8309 | 1.3797 | 0.027242 | 3.4687 | 63.6415 | 220.7527 | -9 | 32.5 | 4 | 26.5 | 208.6448 | 827.0396 | 54.4117 | 3.9639 | 0.89797 | 110 | 107.6798 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.425 | 73.7137
CID=1194058223 | -9 | 35 | 64.3783 | 4 | 29 | 5.8 | 1.7455 | 148.4312 | 10.2212 | 240.2788 | 427.4319 | 396.6938 | 34553.1098 | 1.3719 | 0.028132 | 3.3333 | 64.3783 | 214.5916 | -9 | 35 | 4 | 29 | 208.6448 | 886.981 | 56.1446 | 4.2512 | 0.89866 | 110 | 108.8431 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.4523 | 73.3536
CID=1194058386 | -9 | 37.5 | 65.7685 | 4 | 31.5 | 6.3 | 1.7455 | 148.4312 | 10.2212 | 243.8959 | 428.9247 | 396.6938 | 34833.5585 | 1.3658 | 0.029308 | 3.173 | 65.7685 | 208.6837 | -9 | 37.5 | 4 | 31.5 | 208.6448 | 950.1287 | 58.29 | 4.5538 | 0.8999 | 110 | 111.0404 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9142 | 73.3866
CID=1194058417 | -9 | 40 | 67.7891 | 4 | 34 | 6.8 | 1.7455 | 148.4312 | 10.2212 | 247.5407 | 430.3916 | 396.6938 | 35210.3514 | 1.3622 | 0.030784 | 2.9971 | 67.7891 | 203.1692 | -9 | 40 | 4 | 34 | 208.6448 | 1016.593 | 60.7863 | 4.8724 | 0.90157 | 110 | 114.2396 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.0108 | 74.0486
CID=1194058068 | -9 | 42.5 | 69.67 | 4 | 36.5 | 7.3 | 1.7455 | 148.4312 | 10.2212 | 251.2145 | 431.833 | 396.6938 | 35549.4284 | 1.3594 | 0.032287 | 2.8386 | 69.67 | 197.7629 | -9 | 42.5 | 4 | 36.5 | 208.6448 | 1086.4865 | 63.1908 | 5.2074 | 0.903 | 110 | 117.2231 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.1264 | 74.5178
CID=1194058099 | -9 | 45 | 72.0162 | 4 | 39 | 7.8 | 1.7455 | 148.4312 | 10.2212 | 254.9187 | 433.2489 | 396.6938 | 35552.8119 | 1.0155 | 0.031284 | 2.2149 | 65.0043 | 143.9788 | -9 | 45 | 4 | 39 | 208.6448 | 1159.9242 | 74.7802 | 5.5593 | 0.89922 | 98.353 | 109.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.4822 | 74.5276
CID=1194058262 | -9 | 47.5 | 71.0261 | 4 | 41.5 | 8.3 | 1.7455 | 148.4312 | 10.2212 | 258.655 | 434.6398 | 396.6938 | 36119.6991 | 1.3082 | 0.034478 | 2.5514 | 70.7774 | 180.5813 | -9 | 47.5 | 4 | 41.5 | 208.6448 | 1237.0237 | 67.9309 | 5.9289 | 0.90379 | 109.5196 | 118.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.7723 | 70.7774
CID=1194058293 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194057944 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194057975 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179925 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179894 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179731 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179700 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180049 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180018 | -9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179855 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019179824 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180173 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019180142 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356198662 | -6 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1356198693 | -6 | 7.5 | 13.9583 | 4 | 1.5 | 0.3 | 1.7436 | 148.523 | 11.416 | 202.0183 | 408.6791 | 398.5385 | 22271.1653 | 0.68638 | 0.0081679 | 9.6636 | 13.9583 | 134.8874 | -6 | 7.5 | 4 | 1.5 | 234.2779 | 381.0767 | 22.0556 | 1.6266 | 0.73344 | 110 | 28.915 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.453 | 16.4601
CID=1356198856 | -6 | 10 | 17.5308 | 4 | 4 | 0.8 | 1.7436 | 148.523 | 11.416 | 205.396 | 410.4654 | 398.5385 | 23773.1315 | 0.76972 | 0.0092915 | 8.4802 | 17.5308 | 148.6647 | -6 | 10 | 4 | 4 | 234.2779 | 414.6075 | 25.4725 | 1.7697 | 0.76001 | 110 | 35.046 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.6696 | 20.8178
CID=1356198887 | -6 | 12.5 | 21.5549 | 4 | 6.5 | 1.3 | 1.7436 | 148.523 | 11.416 | 208.7918 | 412.2236 | 398.5385 | 25207.3326 | 0.86018 | 0.010608 | 7.5721 | 21.5549 | 163.2166 | -6 | 12.5 | 4 | 6.5 | 234.2779 | 450.3422 | 28.6988 | 1.9223 | 0.78543 | 110 | 41.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2176 | 25.6674
CID=1356198538 | -6 | 15 | 26.0004 | 4 | 9 | 1.8 | 1.7436 | 148.523 | 11.416 | 212.2062 | 413.9537 | 398.5385 | 26542.9161 | 0.94751 | 0.012114 | 6.7904 | 26.0004 | 176.5521 | -6 | 15 | 4 | 9 | 234.2779 | 488.3739 | 31.9862 | 2.0846 | 0.80884 | 110 | 48.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7286 | 31.091
CID=1356198569 | -6 | 17.5 | 29.9372 | 4 | 11.5 | 2.3 | 1.7436 | 148.523 | 11.416 | 215.6398 | 415.6561 | 398.5385 | 27592.4432 | 1.0145 | 0.013533 | 6.1979 | 29.9372 | 185.5479 | -6 | 17.5 | 4 | 11.5 | 234.2779 | 528.7968 | 34.9269 | 2.2571 | 0.82615 | 110 | 55.0561 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.814 | 35.6449
CID=1356198732 | -6 | 20 | 35.4258 | 4 | 14 | 2.8 | 1.7436 | 148.523 | 11.416 | 219.0933 | 417.3308 | 398.5385 | 28831.2819 | 1.1067 | 0.015493 | 5.6057 | 35.4257 | 198.5876 | -6 | 20 | 4 | 14 | 234.2779 | 571.7069 | 38.2938 | 2.4403 | 0.84588 | 110 | 63.6303 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1569 | 42.1821
CID=1356198763 | -6 | 22.5 | 41.2492 | 4 | 16.5 | 3.3 | 1.7436 | 148.523 | 11.416 | 222.5675 | 418.9782 | 398.5385 | 29964.9485 | 1.1949 | 0.017645 | 5.0973 | 41.2492 | 210.2614 | -6 | 22.5 | 4 | 16.5 | 234.2779 | 617.2019 | 41.6469 | 2.6345 | 0.8623 | 110 | 72.6795 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.5255 | 49.1571
CID=1356198414 | -6 | 25 | 47.6715 | 4 | 19 | 3.8 | 1.7436 | 148.523 | 11.416 | 226.0633 | 420.5983 | 398.5385 | 31079.9299 | 1.2805 | 0.020085 | 4.6329 | 47.6715 | 220.8573 | -6 | 25 | 4 | 19 | 234.2779 | 665.3809 | 45.1636 | 2.8401 | 0.87622 | 110 | 82.6607 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3432 | 56.7809
CID=1356198445 | -6 | 27.5 | 52.4352 | 4 | 21.5 | 4.3 | 1.7436 | 148.523 | 11.416 | 229.5813 | 422.1916 | 398.5385 | 31819.4182 | 1.3358 | 0.022081 | 4.3042 | 52.4352 | 225.6926 | -6 | 27.5 | 4 | 21.5 | 234.2779 | 716.3449 | 48.0188 | 3.0577 | 0.88433 | 110 | 90.0871 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3062 | 62.1448
CID=-1857039455 | -6 | 30 | 59.0561 | 4 | 24 | 4.8 | 1.7436 | 148.523 | 11.416 | 233.1226 | 423.758 | 398.5385 | 32700.1457 | 1.416 | 0.024797 | 3.9663 | 59.0561 | 234.232 | -6 | 30 | 4 | 24 | 234.2779 | 770.1963 | 51.2749 | 3.2875 | 0.89317 | 110 | 100.4585 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4924 | 69.9107
CID=-1857039424 | -6 | 32.5 | 65.5031 | 4 | 26.5 | 5.3 | 1.7436 | 148.523 | 11.416 | 236.688 | 425.298 | 398.5385 | 33539.5135 | 1.4893 | 0.027577 | 3.68 | 65.5031 | 241.0496 | -6 | 32.5 | 4 | 26.5 | 234.2779 | 827.0396 | 54.3597 | 3.5302 | 0.89967 | 110 | 110.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2611 | 77.2504
CID=-1857039261 | -6 | 35 | 70.4068 | 4 | 29 | 5.8 | 1.7436 | 148.523 | 11.416 | 240.2788 | 426.8116 | 398.5385 | 34228.9997 | 1.5433 | 0.029941 | 3.469 | 70.4068 | 244.2441 | -6 | 35 | 4 | 29 | 234.2779 | 886.981 | 56.8686 | 3.786 | 0.90353 | 110 | 118.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.2819 | 82.4485
CID=-1857039230 | -6 | 37.5 | 71.9919 | 4 | 31.5 | 6.3 | 1.7436 | 148.523 | 11.416 | 243.8959 | 428.2991 | 398.5385 | 34504.16 | 1.5475 | 0.031217 | 3.3242 | 71.9919 | 239.3146 | -6 | 37.5 | 4 | 31.5 | 234.2779 | 950.1287 | 58.7248 | 4.0556 | 0.90462 | 110 | 120.9135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.1102 | 82.9524
CID=-1857039579 | -6 | 40 | 72.762 | 4 | 34 | 6.8 | 1.7436 | 148.523 | 11.416 | 247.5407 | 429.7609 | 398.5385 | 34703.109 | 1.5355 | 0.032256 | 3.1865 | 72.762 | 231.8583 | -6 | 40 | 4 | 34 | 234.2779 | 1016.593 | 60.5774 | 4.3393 | 0.90512 | 110 | 122.1393 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.5036 | 82.5148
CID=-1857039548 | -6 | 42.5 | 73.4732 | 4 | 36.5 | 7.3 | 1.7436 | 148.523 | 11.416 | 251.2145 | 431.197 | 398.5385 | 34896.0026 | 1.5155 | 0.033332 | 3.0387 | 73.4732 | 223.2654 | -6 | 42.5 | 4 | 36.5 | 234.2779 | 1086.4865 | 62.6547 | 4.6376 | 0.90557 | 110 | 123.2722 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.8837 | 81.3364
CID=-1857039385 | -6 | 45 | 75.9718 | 4 | 39 | 7.8 | 1.7436 | 148.523 | 11.416 | 254.9187 | 432.6077 | 398.5385 | 35290.1845 | 1.5162 | 0.035168 | 2.8663 | 75.9718 | 217.7564 | -6 | 45 | 4 | 39 | 234.2779 | 1159.9242 | 65.2089 | 4.9511 | 0.90704 | 110 | 127.2576 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.269 | 82.5395
CID=-1857039354 | -6 | 47.5 | 78.0043 | 4 | 41.5 | 8.3 | 1.7436 | 148.523 | 11.416 | 258.655 | 433.9933 | 398.5385 | 35616.8479 | 1.5128 | 0.036923 | 2.7129 | 78.0044 | 211.6168 | -6 | 47.5 | 4 | 41.5 | 234.2779 | 1237.0237 | 67.6369 | 5.2802 | 0.90812 | 110 | 130.5061 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.1967 | 82.9402
CID=-1857039703 | -6 | 50 | 80.1839 | 4 | 44 | 8.8 | 1.7436 | 148.523 | 11.416 | 262.425 | 435.3541 | 398.5385 | 35722.2242 | 1.1082 | 0.036298 | 2.0381 | 74.0091 | 150.8396 | -6 | 50 | 4 | 44 | 234.2779 | 1317.9055 | 81.0313 | 5.6254 | 0.90589 | 95.8314 | 124.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.7545 | 82.3271
CID=-1857039672 | -6 | 52.5 | 79.8898 | 4 | 46.5 | 9.3 | 1.7436 | 148.523 | 11.416 | 266.2308 | 436.6902 | 398.5385 | 36189.9086 | 1.461 | 0.039595 | 2.437 | 79.3179 | 193.2958 | -6 | 52.5 | 4 | 46.5 | 234.2779 | 1402.6932 | 72.3832 | 5.9873 | 0.90877 | 109.5619 | 132.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 81.6054 | 79.3179
CID=1162108772 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108803 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108966 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108997 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108648 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108679 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108842 | -6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108873 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108524 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162108555 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051129345 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051129314 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051129151 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051129120 | -3 | 10 | 14.5826 | 4 | 4 | 0.8 | 1.7418 | 148.5658 | 12.7186 | 205.396 | 409.9411 | 400.3675 | 21887.1543 | 0.74515 | 0.0084002 | 9.9627 | 14.5826 | 145.2826 | -3 | 10 | 4 | 4 | 262.283 | 414.6075 | 24.1836 | 1.5808 | 0.73838 | 110 | 30.006 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2395 | 17.0303
CID=-2051129469 | -3 | 12.5 | 18.0205 | 4 | 6.5 | 1.3 | 1.7418 | 148.5658 | 12.7186 | 208.7918 | 411.6941 | 400.3675 | 23272.9172 | 0.82437 | 0.0095051 | 8.7639 | 18.0205 | 157.9301 | -3 | 12.5 | 4 | 6.5 | 262.283 | 450.3422 | 27.4307 | 1.717 | 0.76334 | 110 | 35.8677 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8059 | 21.4254
CID=-2051129438 | -3 | 15 | 22.234 | 4 | 9 | 1.8 | 1.7418 | 148.5658 | 12.7186 | 212.2062 | 413.4192 | 400.3675 | 24707.6203 | 0.92152 | 0.010895 | 7.7986 | 22.234 | 173.3943 | -3 | 15 | 4 | 9 | 262.283 | 488.3739 | 30.6465 | 1.862 | 0.7893 | 110 | 42.7986 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5793 | 26.4523
CID=-2051129275 | -3 | 17.5 | 26.9196 | 4 | 11.5 | 2.3 | 1.7418 | 148.5658 | 12.7186 | 215.6398 | 415.1165 | 400.3675 | 26042.0073 | 1.0193 | 0.012494 | 6.9945 | 26.9196 | 188.2881 | -3 | 17.5 | 4 | 11.5 | 262.283 | 528.7968 | 33.8478 | 2.0161 | 0.81315 | 110 | 50.2981 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.3834 | 32.0983
CID=-2051129244 | -3 | 20 | 30.9107 | 4 | 14 | 2.8 | 1.7418 | 148.5658 | 12.7186 | 219.0933 | 416.7863 | 400.3675 | 27065.3915 | 1.0883 | 0.013952 | 6.3823 | 30.9107 | 197.2826 | -3 | 20 | 4 | 14 | 262.283 | 571.7069 | 36.7259 | 2.1797 | 0.83 | 110 | 56.583 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.1276 | 36.8384
CID=-2051129593 | -3 | 22.5 | 36.5035 | 4 | 16.5 | 3.3 | 1.7418 | 148.5658 | 12.7186 | 222.5675 | 418.4287 | 400.3675 | 28277.737 | 1.1862 | 0.015974 | 5.7779 | 36.5035 | 210.9125 | -3 | 22.5 | 4 | 16.5 | 262.283 | 617.2019 | 39.9779 | 2.3532 | 0.84924 | 110 | 65.307 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3536 | 43.5534
CID=-2051129562 | -3 | 25 | 42.8612 | 4 | 19 | 3.8 | 1.7418 | 148.5658 | 12.7186 | 226.0633 | 420.0439 | 400.3675 | 29452.3024 | 1.2891 | 0.018331 | 5.2424 | 42.8612 | 224.6964 | -3 | 25 | 4 | 19 | 262.283 | 665.3809 | 43.3159 | 2.5369 | 0.86617 | 110 | 75.1829 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2962 | 51.0495
CID=1324249242 | -3 | 27.5 | 49.405 | 4 | 21.5 | 4.3 | 1.7418 | 148.5658 | 12.7186 | 229.5813 | 421.6322 | 400.3675 | 30537.7064 | 1.3798 | 0.020851 | 4.7698 | 49.405 | 235.6532 | -3 | 27.5 | 4 | 21.5 | 262.283 | 716.3449 | 46.7057 | 2.7312 | 0.87937 | 110 | 85.3601 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.9887 | 58.877
CID=1324249273 | -3 | 30 | 55.108 | 4 | 24 | 4.8 | 1.7418 | 148.5658 | 12.7186 | 233.1226 | 423.1938 | 400.3675 | 31386.7482 | 1.452 | 0.023203 | 4.4067 | 55.108 | 242.8464 | -3 | 30 | 4 | 24 | 262.283 | 770.1963 | 49.6998 | 2.9365 | 0.88821 | 110 | 94.2665 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0589 | 65.4577
CID=1324249436 | -3 | 32.5 | 61.5471 | 4 | 26.5 | 5.3 | 1.7418 | 148.5658 | 12.7186 | 236.688 | 424.7289 | 400.3675 | 32231.1743 | 1.5263 | 0.025913 | 4.0592 | 61.5471 | 249.8291 | -3 | 32.5 | 4 | 26.5 | 262.283 | 827.0396 | 52.8946 | 3.1532 | 0.89589 | 110 | 104.3773 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.3282 | 72.9534
CID=1324249467 | -3 | 35 | 68.7731 | 4 | 29 | 5.8 | 1.7418 | 148.5658 | 12.7186 | 240.2788 | 426.2376 | 400.3675 | 33042.9531 | 1.6136 | 0.029026 | 3.7561 | 68.7731 | 258.3201 | -3 | 35 | 4 | 29 | 262.283 | 886.981 | 56.0215 | 3.3818 | 0.90233 | 110 | 115.7997 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.2318 | 81.2868
CID=1324249118 | -3 | 37.5 | 75.7978 | 4 | 31.5 | 6.3 | 1.7418 | 148.5658 | 12.7186 | 243.8959 | 427.7203 | 400.3675 | 33910.446 | 1.6908 | 0.032217 | 3.4904 | 75.7978 | 264.5632 | -3 | 37.5 | 4 | 31.5 | 262.283 | 950.1287 | 59.0622 | 3.6225 | 0.90694 | 110 | 126.9797 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.4207 | 89.2568
CID=1324249149 | -3 | 40 | 78.7458 | 4 | 34 | 6.8 | 1.7418 | 148.5658 | 12.7186 | 247.5407 | 429.1772 | 400.3675 | 34306.4578 | 1.7177 | 0.034068 | 3.3336 | 78.7458 | 262.5058 | -3 | 40 | 4 | 34 | 262.283 | 1016.593 | 61.0557 | 3.8759 | 0.90849 | 110 | 131.6925 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.004 | 91.6597
CID=1324249312 | -3 | 42.5 | 80.2135 | 4 | 36.5 | 7.3 | 1.7418 | 148.5658 | 12.7186 | 251.2145 | 430.6085 | 400.3675 | 34549.054 | 1.7182 | 0.03546 | 3.1949 | 80.2135 | 256.2734 | -3 | 42.5 | 4 | 36.5 | 262.283 | 1086.4865 | 62.9215 | 4.1424 | 0.9092 | 110 | 134.0432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.8066 | 92.0158
CID=1324249343 | -3 | 45 | 81.4155 | 4 | 39 | 7.8 | 1.7418 | 148.5658 | 12.7186 | 254.9187 | 432.0144 | 400.3675 | 34773.0011 | 1.709 | 0.036827 | 3.0531 | 81.4155 | 248.5732 | -3 | 45 | 4 | 39 | 262.283 | 1159.9242 | 64.9139 | 4.4224 | 0.90974 | 110 | 135.9706 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.0122 | 91.8833
CID=1324248994 | -3 | 47.5 | 82.6358 | 4 | 41.5 | 8.3 | 1.7418 | 148.5658 | 12.7186 | 258.655 | 433.3951 | 400.3675 | 35015.0157 | 1.69 | 0.038281 | 2.8982 | 82.6358 | 239.4985 | -3 | 47.5 | 4 | 41.5 | 262.283 | 1237.0237 | 67.184 | 4.7164 | 0.91027 | 110 | 137.929 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57.2677 | 91.0918
CID=1324249025 | -3 | 50 | 85.3283 | 4 | 44 | 8.8 | 1.7418 | 148.5658 | 12.7186 | 262.425 | 434.7511 | 400.3675 | 35386.3624 | 1.6922 | 0.040424 | 2.7356 | 85.3283 | 233.4226 | -3 | 50 | 4 | 44 | 262.283 | 1317.9055 | 69.705 | 5.0247 | 0.91133 | 110 | 142.2568 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 64.1843 | 92.3763
CID=-1888988875 | -3 | 52.5 | 87.6035 | 4 | 46.5 | 9.3 | 1.7418 | 148.5658 | 12.7186 | 266.2308 | 436.0824 | 400.3675 | 35705.9709 | 1.6902 | 0.042523 | 2.588 | 87.6035 | 226.7161 | -3 | 52.5 | 4 | 46.5 | 262.283 | 1402.6932 | 72.1426 | 5.348 | 0.91214 | 110 | 145.9205 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.1709 | 92.7477
CID=-1888988844 | -3 | 55 | 89.9689 | 4 | 49 | 9.8 | 1.7418 | 148.5658 | 12.7186 | 270.0745 | 437.3893 | 400.3675 | 35839.1471 | 1.2333 | 0.042163 | 1.9162 | 83.8581 | 160.6883 | -3 | 55 | 4 | 49 | 262.283 | 1491.5141 | 86.0361 | 5.6867 | 0.91076 | 95.4659 | 139.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.791 | 92.0281
CID=-1888988681 | -3 | 57.5 | 89.4574 | 4 | 51.5 | 10.3 | 1.7418 | 148.5658 | 12.7186 | 273.9586 | 438.6721 | 400.3675 | 36239.4688 | 1.6267 | 0.045541 | 2.3224 | 88.544 | 205.6311 | -3 | 57.5 | 4 | 51.5 | 262.283 | 1584.4992 | 76.8958 | 6.0412 | 0.91245 | 109.5992 | 147.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.1977 | 88.544
CID=-1888988650 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888988999 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888988968 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888988805 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888988774 | -3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888989123 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888989092 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130159352 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130159383 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130159546 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130159577 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130159228 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130159259 | 0 | 12.5 | 13.5582 | 4 | 6.5 | 1.3 | 1.7401 | 148.5582 | 14.1363 | 208.7918 | 411.2041 | 402.1796 | 20844.6276 | 0.75309 | 0.0081928 | 10.7417 | 13.5582 | 145.6378 | 0 | 12.5 | 4 | 6.5 | 292.8032 | 450.3422 | 25.4155 | 1.538 | 0.7302 | 110 | 28.2106 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.6527 | 15.5267
CID=1130159422 | 0 | 15 | 18.437 | 4 | 9 | 1.8 | 1.7401 | 148.5582 | 14.1363 | 212.2062 | 412.9246 | 402.1796 | 22769.3178 | 0.88254 | 0.0097035 | 9.0936 | 18.437 | 167.6592 | 0 | 15 | 4 | 9 | 292.8032 | 488.3739 | 29.3384 | 1.6679 | 0.76612 | 110 | 36.5635 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8476 | 21.9668
CID=1130159453 | 0 | 17.5 | 22.8224 | 4 | 11.5 | 2.3 | 1.7401 | 148.5582 | 14.1363 | 215.6398 | 414.6172 | 402.1796 | 24189.0892 | 0.98416 | 0.011163 | 8.0441 | 22.8224 | 183.5853 | 0 | 17.5 | 4 | 11.5 | 292.8032 | 528.7968 | 32.5881 | 1.806 | 0.79257 | 110 | 43.7503 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6303 | 27.2198
CID=1130159104 | 0 | 20 | 27.7164 | 4 | 14 | 2.8 | 1.7401 | 148.5582 | 14.1363 | 219.0933 | 416.2824 | 402.1796 | 25525.3718 | 1.0916 | 0.012847 | 7.2106 | 27.7163 | 199.8522 | 0 | 20 | 4 | 14 | 292.8032 | 571.7069 | 35.7219 | 1.9525 | 0.81675 | 110 | 51.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4976 | 33.1226
CID=1130159135 | 0 | 22.5 | 33.1637 | 4 | 16.5 | 3.3 | 1.7401 | 148.5582 | 14.1363 | 222.5675 | 417.9202 | 402.1796 | 26800.7917 | 1.1958 | 0.014778 | 6.4762 | 33.1637 | 214.7737 | 0 | 22.5 | 4 | 16.5 | 292.8032 | 617.2019 | 38.9685 | 2.1079 | 0.83831 | 110 | 60.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.7099 | 39.6483
CID=-2083078765 | 0 | 25 | 37.7537 | 4 | 19 | 3.8 | 1.7401 | 148.5582 | 14.1363 | 226.0633 | 419.5308 | 402.1796 | 27765.4328 | 1.2721 | 0.016523 | 5.9342 | 37.7537 | 224.0363 | 0 | 25 | 4 | 19 | 292.8032 | 665.3809 | 41.81 | 2.2725 | 0.85294 | 110 | 67.2504 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0491 | 44.9885
CID=-2083078734 | 0 | 27.5 | 44.2532 | 4 | 21.5 | 4.3 | 1.7401 | 148.5582 | 14.1363 | 229.5813 | 421.1145 | 402.1796 | 28929.2603 | 1.3804 | 0.018963 | 5.3837 | 44.2532 | 238.2469 | 0 | 27.5 | 4 | 21.5 | 292.8032 | 716.3449 | 45.0707 | 2.4465 | 0.86929 | 110 | 77.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.7183 | 52.7648
CID=-2083078571 | 0 | 30 | 51.1144 | 4 | 24 | 4.8 | 1.7401 | 148.5582 | 14.1363 | 233.1226 | 422.6716 | 402.1796 | 30001.495 | 1.4831 | 0.021631 | 4.9052 | 51.1144 | 250.7268 | 0 | 30 | 4 | 24 | 292.8032 | 770.1963 | 48.3387 | 2.6304 | 0.88225 | 110 | 88.0254 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.6284 | 60.943
CID=-2083078540 | 0 | 32.5 | 58.6372 | 4 | 26.5 | 5.3 | 1.7401 | 148.5582 | 14.1363 | 236.688 | 424.2021 | 402.1796 | 31057.5011 | 1.583 | 0.024644 | 4.4677 | 58.6372 | 261.9761 | 0 | 32.5 | 4 | 26.5 | 292.8032 | 827.0396 | 51.7487 | 2.8246 | 0.89268 | 110 | 99.8004 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9262 | 69.8742
CID=-2083078889 | 0 | 35 | 64.0558 | 4 | 29 | 5.8 | 1.7401 | 148.5582 | 14.1363 | 240.2788 | 425.7063 | 402.1796 | 31743.3986 | 1.6458 | 0.027067 | 4.1597 | 64.0558 | 266.4531 | 0 | 35 | 4 | 29 | 292.8032 | 886.981 | 54.5147 | 3.0293 | 0.89836 | 110 | 108.3337 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2143 | 76.0029
CID=-2083078858 | 0 | 37.5 | 71.7597 | 4 | 31.5 | 6.3 | 1.7401 | 148.5582 | 14.1363 | 243.8959 | 427.1845 | 402.1796 | 32585.5747 | 1.7387 | 0.030416 | 3.8351 | 71.7597 | 275.2053 | 0 | 37.5 | 4 | 31.5 | 292.8032 | 950.1287 | 57.709 | 3.2449 | 0.90446 | 110 | 120.5442 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0433 | 84.9985
CID=-2083078695 | 0 | 40 | 79.2836 | 4 | 34 | 6.8 | 1.7401 | 148.5582 | 14.1363 | 247.5407 | 428.6369 | 402.1796 | 33346.7239 | 1.8263 | 0.033864 | 3.5621 | 79.2835 | 282.412 | 0 | 40 | 4 | 34 | 292.8032 | 1016.593 | 60.7135 | 3.4719 | 0.90876 | 110 | 132.5535 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5584 | 93.5253
CID=-2083078664 | 0 | 42.5 | 86.587 | 4 | 36.5 | 7.3 | 1.7401 | 148.5582 | 14.1363 | 251.2145 | 430.0637 | 402.1796 | 34170.0867 | 1.9075 | 0.037405 | 3.3258 | 86.587 | 287.9689 | 0 | 42.5 | 4 | 36.5 | 292.8032 | 1086.4865 | 63.5789 | 3.7106 | 0.91179 | 110 | 144.2829 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6283 | 101.9065
CID=-2083079013 | 0 | 45 | 87.9596 | 4 | 39 | 7.8 | 1.7401 | 148.5582 | 14.1363 | 254.9187 | 431.4651 | 402.1796 | 34383.6388 | 1.9089 | 0.038869 | 3.1958 | 87.9597 | 281.1026 | 0 | 45 | 4 | 39 | 292.8032 | 1159.9242 | 65.3444 | 3.9614 | 0.91226 | 110 | 146.4946 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.0942 | 101.9148
CID=-2083078982 | 0 | 47.5 | 88.6976 | 4 | 41.5 | 8.3 | 1.7401 | 148.5582 | 14.1363 | 258.655 | 432.8414 | 402.1796 | 34549.8535 | 1.8967 | 0.04017 | 3.0691 | 88.6976 | 272.224 | 0 | 47.5 | 4 | 41.5 | 292.8032 | 1237.0237 | 67.1435 | 4.2248 | 0.9125 | 110 | 147.6845 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.0502 | 101.2467
CID=1194050525 | 0 | 50 | 90.9753 | 4 | 44 | 8.8 | 1.7401 | 148.5582 | 14.1363 | 262.425 | 434.1928 | 402.1796 | 34844.7942 | 1.8986 | 0.042169 | 2.9165 | 90.9753 | 265.3331 | 0 | 50 | 4 | 44 | 292.8032 | 1317.9055 | 69.3662 | 4.501 | 0.9132 | 110 | 151.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57.491 | 102.1367
CID=1194050622 | 0 | 52.5 | 92.5726 | 4 | 46.5 | 9.3 | 1.7401 | 148.5582 | 14.1363 | 266.2308 | 435.5196 | 402.1796 | 35111.9301 | 1.8798 | 0.04401 | 2.7606 | 92.5727 | 255.5587 | 0 | 52.5 | 4 | 46.5 | 292.8032 | 1402.6932 | 71.7493 | 4.7906 | 0.91365 | 110 | 153.9424 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.2952 | 101.6651
CID=1194050587 | 0 | 55 | 94.7235 | 4 | 49 | 9.8 | 1.7401 | 148.5582 | 14.1363 | 270.0745 | 436.822 | 402.1796 | 35412.3923 | 1.8709 | 0.046205 | 2.6092 | 94.7235 | 247.1498 | 0 | 55 | 4 | 49 | 292.8032 | 1491.5141 | 74.2023 | 5.0939 | 0.91421 | 110 | 157.4225 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.7779 | 102.0387
CID=1194050428 | 0 | 57.5 | 97.4245 | 4 | 51.5 | 10.3 | 1.7401 | 148.5582 | 14.1363 | 273.9586 | 438.1003 | 402.1796 | 35746.115 | 1.8694 | 0.048788 | 2.4603 | 97.4244 | 239.6906 | 0 | 57.5 | 4 | 51.5 | 292.8032 | 1584.4992 | 76.7548 | 5.4115 | 0.91485 | 110 | 161.7989 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82.0777 | 102.54
CID=1194050649 | 0 | 60 | 99.208 | 4 | 54 | 10.8 | 1.7401 | 148.5582 | 14.1363 | 277.8855 | 439.3549 | 402.1796 | 35914.8119 | 1.3827 | 0.048861 | 1.8249 | 94.1757 | 171.8647 | 0 | 60 | 4 | 54 | 292.8032 | 1681.7842 | 90.2399 | 5.7437 | 0.91407 | 95.3496 | 156.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.1756 | 100.8854
CID=1194050746 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194050711 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194050552 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194050773 | 0 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194050870 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187592 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187495 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187530 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187689 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187468 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187371 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187406 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019187565 | 3 | 15 | 10.4803 | 4 | 9 | 1.8 | 1.7385 | 148.4988 | 15.6766 | 212.2062 | 412.4664 | 403.9734 | 19625.4314 | 0.66932 | 0.0074564 | 12.247 | 10.4803 | 128.3533 | 3 | 15 | 4 | 9 | 325.9849 | 488.3739 | 25.7178 | 1.4981 | 0.70335 | 88.4824 | 22.6392 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.4251 | 11.1654
CID=-2019187344 | 3 | 17.5 | 18.9601 | 4 | 11.5 | 2.3 | 1.7385 | 148.4988 | 15.6766 | 215.6398 | 414.1547 | 403.9734 | 22313.9267 | 0.94718 | 0.0099382 | 9.4085 | 18.9601 | 178.3855 | 3 | 17.5 | 4 | 11.5 | 325.9849 | 528.7968 | 31.3447 | 1.6222 | 0.76955 | 110 | 37.4337 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.626 | 22.4048
CID=-2019187247 | 3 | 20 | 23.4933 | 4 | 14 | 2.8 | 1.7385 | 148.4988 | 15.6766 | 219.0933 | 415.8156 | 403.9734 | 23701.5343 | 1.0523 | 0.011462 | 8.2812 | 23.4933 | 194.5518 | 3 | 20 | 4 | 14 | 325.9849 | 571.7069 | 34.6056 | 1.7538 | 0.79619 | 110 | 44.8313 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0707 | 27.9674
CID=1356190995 | 3 | 22.5 | 28.5927 | 4 | 16.5 | 3.3 | 1.7385 | 148.4988 | 15.6766 | 222.5675 | 417.4491 | 403.9734 | 25046.6859 | 1.1675 | 0.013233 | 7.4071 | 28.5927 | 211.7902 | 3 | 22.5 | 4 | 16.5 | 325.9849 | 617.2019 | 37.7145 | 1.8933 | 0.82057 | 110 | 52.9414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1238 | 34.0823
CID=1356191092 | 3 | 25 | 34.1636 | 4 | 19 | 3.8 | 1.7385 | 148.4988 | 15.6766 | 226.0633 | 419.0555 | 403.9734 | 26291.4508 | 1.2792 | 0.015232 | 6.6618 | 34.1636 | 227.5896 | 3 | 25 | 4 | 19 | 325.9849 | 665.3809 | 40.8519 | 2.0411 | 0.84175 | 110 | 61.6647 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0916 | 40.8543
CID=1356191057 | 3 | 27.5 | 38.8353 | 4 | 21.5 | 4.3 | 1.7385 | 148.4988 | 15.6766 | 229.5813 | 420.635 | 403.9734 | 27239.1604 | 1.3591 | 0.017032 | 6.1031 | 38.8353 | 237.0144 | 3 | 27.5 | 4 | 21.5 | 325.9849 | 716.3449 | 43.6408 | 2.1975 | 0.85599 | 110 | 68.9308 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.1927 | 46.3828
CID=1356190898 | 3 | 30 | 45.55 | 4 | 24 | 4.8 | 1.7385 | 148.4988 | 15.6766 | 233.1226 | 422.1878 | 403.9734 | 28398.2131 | 1.4753 | 0.019581 | 5.5337 | 45.55 | 252.0589 | 3 | 30 | 4 | 24 | 325.9849 | 770.1963 | 46.8421 | 2.3627 | 0.87204 | 110 | 79.3609 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.1571 | 54.3477
CID=1356191119 | 3 | 32.5 | 52.9515 | 4 | 26.5 | 5.3 | 1.7385 | 148.4988 | 15.6766 | 236.688 | 423.7141 | 403.9734 | 29494.069 | 1.5941 | 0.022475 | 5.0362 | 52.9515 | 266.6742 | 3 | 32.5 | 4 | 26.5 | 325.9849 | 827.0396 | 50.0717 | 2.537 | 0.88512 | 110 | 90.8937 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.4325 | 63.1245
CID=1356191216 | 3 | 35 | 60.5899 | 4 | 29 | 5.8 | 1.7385 | 148.4988 | 15.6766 | 240.2788 | 425.2142 | 403.9734 | 30520.2257 | 1.6997 | 0.025583 | 4.592 | 60.5898 | 278.2276 | 3 | 35 | 4 | 29 | 325.9849 | 886.981 | 53.3672 | 2.7209 | 0.89488 | 110 | 102.8702 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6165 | 72.2476
CID=1356191181 | 3 | 37.5 | 67.5237 | 4 | 31.5 | 6.3 | 1.7385 | 148.4988 | 15.6766 | 243.8959 | 426.6882 | 403.9734 | 31356.6527 | 1.788 | 0.02859 | 4.2387 | 67.5237 | 286.2117 | 3 | 37.5 | 4 | 31.5 | 325.9849 | 950.1287 | 56.374 | 2.9146 | 0.90136 | 110 | 113.819 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.0856 | 80.3364
CID=1356191022 | 3 | 40 | 74.5489 | 4 | 34 | 6.8 | 1.7385 | 148.4988 | 15.6766 | 247.5407 | 428.1364 | 403.9734 | 32113.9135 | 1.8683 | 0.031777 | 3.9204 | 74.5489 | 292.2625 | 3 | 40 | 4 | 34 | 325.9849 | 1016.593 | 59.3947 | 3.1185 | 0.90622 | 110 | 124.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.953 | 88.4142
CID=1356191243 | 3 | 42.5 | 83.1283 | 4 | 36.5 | 7.3 | 1.7385 | 148.4988 | 15.6766 | 251.2145 | 429.559 | 403.9734 | 32907.3808 | 1.9725 | 0.035694 | 3.6247 | 83.1283 | 301.3187 | 3 | 42.5 | 4 | 36.5 | 325.9849 | 1086.4865 | 62.5107 | 3.3329 | 0.91047 | 110 | 138.72 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.6354 | 98.2926
CID=1356191340 | 3 | 45 | 90.9928 | 4 | 39 | 7.8 | 1.7385 | 148.4988 | 15.6766 | 254.9187 | 430.9562 | 403.9734 | 33682.6127 | 2.0585 | 0.039545 | 3.372 | 90.9928 | 306.8294 | 3 | 45 | 4 | 39 | 325.9849 | 1159.9242 | 65.4676 | 3.5582 | 0.9132 | 110 | 151.3892 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9298 | 107.3472
CID=-1857047122 | 3 | 47.5 | 96.4013 | 4 | 41.5 | 8.3 | 1.7385 | 148.4988 | 15.6766 | 258.655 | 432.3283 | 403.9734 | 34235.5857 | 2.1171 | 0.042652 | 3.1914 | 96.4013 | 307.6583 | 3 | 47.5 | 4 | 41.5 | 325.9849 | 1237.0237 | 67.8173 | 3.7947 | 0.91461 | 110 | 160.1402 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.1667 | 112.8128
CID=-1857047025 | 3 | 50 | 98.4011 | 4 | 44 | 8.8 | 1.7385 | 148.4988 | 15.6766 | 262.425 | 433.6755 | 403.9734 | 34486.5472 | 2.1224 | 0.044582 | 3.0531 | 98.4011 | 300.4258 | 3 | 50 | 4 | 44 | 325.9849 | 1317.9055 | 69.7696 | 4.0428 | 0.91506 | 110 | 163.383 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1496 | 113.4849
CID=-1857047060 | 3 | 52.5 | 99.0583 | 4 | 46.5 | 9.3 | 1.7385 | 148.4988 | 15.6766 | 266.2308 | 434.9982 | 403.9734 | 34641.255 | 2.1047 | 0.046082 | 2.9266 | 99.0583 | 289.9018 | 3 | 52.5 | 4 | 46.5 | 325.9849 | 1402.6932 | 71.6531 | 4.3029 | 0.9152 | 110 | 164.4495 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.3888 | 112.6148
CID=-1857047219 | 3 | 55 | 100.7036 | 4 | 49 | 9.8 | 1.7385 | 148.4988 | 15.6766 | 270.0745 | 436.2964 | 403.9734 | 34865.6267 | 2.0926 | 0.048095 | 2.7824 | 100.7036 | 280.2023 | 3 | 55 | 4 | 49 | 325.9849 | 1491.5141 | 73.855 | 4.5754 | 0.91552 | 110 | 167.121 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.8924 | 112.3073
CID=-1857046998 | 3 | 57.5 | 103.2834 | 4 | 51.5 | 10.3 | 1.7385 | 148.4988 | 15.6766 | 273.9586 | 437.5705 | 403.9734 | 35186.3356 | 2.0851 | 0.050647 | 2.6248 | 103.2834 | 271.1001 | 3 | 57.5 | 4 | 51.5 | 325.9849 | 1584.4992 | 76.3605 | 4.8607 | 0.91599 | 110 | 171.3143 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73.9935 | 113.0467
CID=-1857046901 | 3 | 60 | 105.556 | 4 | 54 | 10.8 | 1.7385 | 148.4988 | 15.6766 | 277.8855 | 438.8208 | 403.9734 | 35467.0388 | 2.0767 | 0.053237 | 2.4807 | 105.556 | 261.8479 | 3 | 60 | 4 | 54 | 325.9849 | 1681.7842 | 78.799 | 5.1591 | 0.91637 | 110 | 175.0126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82.0539 | 113.39
CID=-1857046936 | 3 | 62.5 | 108.5988 | 4 | 56.5 | 11.3 | 1.7385 | 148.4988 | 15.6766 | 281.8586 | 440.0476 | 403.9734 | 35802.7008 | 2.0746 | 0.056369 | 2.3328 | 108.5988 | 253.3371 | 3 | 62.5 | 4 | 56.5 | 325.9849 | 1783.5096 | 81.4278 | 5.4711 | 0.91681 | 110 | 179.97 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 92.802 | 113.8644
CID=-1857047095 | 3 | 65 | 110.2438 | 4 | 59 | 11.8 | 1.7385 | 148.4988 | 15.6766 | 285.881 | 441.2512 | 403.9734 | 36076.347 | 2.0431 | 0.059072 | 2.1885 | 110.2438 | 241.2717 | 3 | 65 | 4 | 59 | 325.9849 | 1889.8218 | 84.135 | 5.7973 | 0.91703 | 109.1733 | 182.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 105.0584 | 111.9723
CID=-1857046874 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857046777 | 3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101105 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101202 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101167 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101008 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101229 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101326 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101291 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101132 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101353 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162101450 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2051137012 | 6 | 20 | 19.5293 | 4 | 14 | 2.8 | 1.7371 | 148.3861 | 17.3476 | 219.0933 | 415.3827 | 405.7474 | 21878.6225 | 1.0163 | 0.010193 | 9.7138 | 19.5293 | 189.7029 | 6 | 20 | 4 | 14 | 361.9781 | 571.7069 | 33.4207 | 1.5794 | 0.77318 | 110 | 38.3761 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5417 | 22.8585
CID=-2051136915 | 6 | 22.5 | 24.0466 | 4 | 16.5 | 3.3 | 1.7371 | 148.3861 | 17.3476 | 222.5675 | 417.0123 | 405.7474 | 23212.154 | 1.1213 | 0.011735 | 8.5415 | 24.0465 | 205.3927 | 6 | 22.5 | 4 | 16.5 | 361.9781 | 617.2019 | 36.6089 | 1.7051 | 0.7991 | 110 | 45.72 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1644 | 28.6739
CID=-2051136950 | 6 | 25 | 29.3274 | 4 | 19 | 3.8 | 1.7371 | 148.3861 | 17.3476 | 226.0633 | 418.6147 | 405.7474 | 24544.339 | 1.2436 | 0.013586 | 7.6192 | 29.3274 | 223.451 | 6 | 25 | 4 | 19 | 361.9781 | 665.3809 | 39.7022 | 1.8382 | 0.82366 | 110 | 54.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3537 | 34.9853
CID=-2051137109 | 6 | 27.5 | 35.2037 | 4 | 21.5 | 4.3 | 1.7371 | 148.3861 | 17.3476 | 229.5813 | 420.1903 | 405.7474 | 25799.6334 | 1.3689 | 0.015712 | 6.8504 | 35.2037 | 241.1579 | 6 | 27.5 | 4 | 21.5 | 361.9781 | 716.3449 | 42.7791 | 1.979 | 0.84517 | 110 | 63.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.739 | 42.0253
CID=-2051136888 | 6 | 30 | 41.1344 | 4 | 24 | 4.8 | 1.7371 | 148.3861 | 17.3476 | 233.1226 | 421.7392 | 405.7474 | 26913.2158 | 1.478 | 0.01795 | 6.2027 | 41.1344 | 255.1442 | 6 | 30 | 4 | 24 | 361.9781 | 770.1963 | 45.822 | 2.1277 | 0.86202 | 110 | 72.5013 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.1012 | 49.1455
CID=-2051136791 | 6 | 32.5 | 46.9105 | 4 | 26.5 | 5.3 | 1.7371 | 148.3861 | 17.3476 | 236.688 | 423.2616 | 405.7474 | 27878.9232 | 1.5756 | 0.020239 | 5.6782 | 46.9105 | 266.3672 | 6 | 32.5 | 4 | 26.5 | 361.9781 | 827.0396 | 48.7016 | 2.2848 | 0.87477 | 110 | 81.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7427 | 55.9665
CID=-2051136826 | 6 | 35 | 54.5727 | 4 | 29 | 5.8 | 1.7371 | 148.3861 | 17.3476 | 240.2788 | 424.7577 | 405.7474 | 28979.899 | 1.7028 | 0.02327 | 5.1631 | 54.5728 | 281.7674 | 6 | 35 | 4 | 29 | 361.9781 | 886.981 | 51.8874 | 2.4504 | 0.88746 | 110 | 93.4287 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.991 | 65.1
CID=-2051136985 | 6 | 37.5 | 62.5311 | 4 | 31.5 | 6.3 | 1.7371 | 148.3861 | 17.3476 | 243.8959 | 426.2278 | 405.7474 | 29991.659 | 1.8209 | 0.026547 | 4.7131 | 62.5311 | 294.718 | 6 | 37.5 | 4 | 31.5 | 361.9781 | 950.1287 | 55.0793 | 2.6248 | 0.89689 | 110 | 105.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.3835 | 74.5803
CID=-2051136764 | 6 | 40 | 71.2417 | 4 | 34 | 6.8 | 1.7371 | 148.3861 | 17.3476 | 247.5407 | 427.6721 | 405.7474 | 30992.2928 | 1.9365 | 0.030247 | 4.3003 | 71.2417 | 306.363 | 6 | 40 | 4 | 34 | 361.9781 | 1016.593 | 58.4002 | 2.8084 | 0.90411 | 110 | 119.7202 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2032 | 84.9212
CID=-2051136667 | 6 | 42.5 | 77.3268 | 4 | 36.5 | 7.3 | 1.7371 | 148.3861 | 17.3476 | 251.2145 | 429.0909 | 405.7474 | 31627.6635 | 2.0072 | 0.033177 | 4.0112 | 77.3268 | 310.1747 | 6 | 42.5 | 4 | 36.5 | 361.9781 | 1086.4865 | 61.0948 | 3.0015 | 0.90777 | 110 | 129.4226 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7881 | 91.8398
CID=1324241575 | 6 | 45 | 86.2318 | 4 | 39 | 7.8 | 1.7371 | 148.3861 | 17.3476 | 254.9187 | 430.4842 | 405.7474 | 32436.4765 | 2.1142 | 0.037307 | 3.6981 | 86.2317 | 318.8895 | 6 | 45 | 4 | 39 | 361.9781 | 1159.9242 | 64.2487 | 3.2044 | 0.91166 | 110 | 143.7109 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.4962 | 102.1436
CID=1324241672 | 6 | 47.5 | 94.9278 | 4 | 41.5 | 8.3 | 1.7371 | 148.3861 | 17.3476 | 258.655 | 431.8524 | 405.7474 | 33148.1531 | 2.2169 | 0.041575 | 3.4351 | 94.9278 | 326.0904 | 6 | 47.5 | 4 | 41.5 | 361.9781 | 1237.0237 | 67.211 | 3.4174 | 0.91426 | 110 | 157.7533 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.1636 | 112.1825
CID=1324241637 | 6 | 50 | 103.7337 | 4 | 44 | 8.8 | 1.7371 | 148.3861 | 17.3476 | 262.425 | 433.1958 | 405.7474 | 33957.7744 | 2.3139 | 0.046121 | 3.1969 | 103.7337 | 331.6297 | 6 | 50 | 4 | 44 | 361.9781 | 1317.9055 | 70.1566 | 3.6408 | 0.91607 | 110 | 172.0468 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3056 | 122.2097
CID=1324241478 | 6 | 52.5 | 106.736 | 4 | 46.5 | 9.3 | 1.7371 | 148.3861 | 17.3476 | 266.2308 | 434.5145 | 405.7474 | 34267.8662 | 2.3376 | 0.048588 | 3.0555 | 106.736 | 326.1328 | 6 | 52.5 | 4 | 46.5 | 361.9781 | 1402.6932 | 72.1455 | 3.8751 | 0.91655 | 110 | 176.9343 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.1646 | 124.2598
CID=1324241699 | 6 | 55 | 108.5626 | 4 | 49 | 9.8 | 1.7371 | 148.3861 | 17.3476 | 270.0745 | 435.8088 | 405.7474 | 34490.355 | 2.3381 | 0.050721 | 2.9219 | 108.5626 | 317.2132 | 6 | 55 | 4 | 49 | 361.9781 | 1491.5141 | 74.1213 | 4.1205 | 0.91681 | 110 | 179.9111 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.3101 | 124.6468
CID=1324241796 | 6 | 57.5 | 110.1781 | 4 | 51.5 | 10.3 | 1.7371 | 148.3861 | 17.3476 | 273.9586 | 437.0791 | 405.7474 | 34707.69 | 2.3277 | 0.052905 | 2.7843 | 110.1781 | 306.7635 | 6 | 57.5 | 4 | 51.5 | 361.9781 | 1584.4992 | 76.2338 | 4.3773 | 0.91702 | 110 | 182.5456 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66.4309 | 124.7604
CID=1324241761 | 6 | 60 | 111.8566 | 4 | 54 | 10.8 | 1.7371 | 148.3861 | 17.3476 | 277.8855 | 438.3255 | 405.7474 | 34918.313 | 2.3127 | 0.055267 | 2.6436 | 111.8567 | 295.7001 | 6 | 60 | 4 | 54 | 361.9781 | 1681.7842 | 78.4807 | 4.6461 | 0.91723 | 110 | 185.2848 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 75.0155 | 124.137
CID=1324241602 | 6 | 62.5 | 114.7691 | 4 | 56.5 | 11.3 | 1.7371 | 148.3861 | 17.3476 | 281.8586 | 439.5483 | 405.7474 | 35237.2244 | 2.3067 | 0.058361 | 2.49 | 114.7691 | 285.778 | 6 | 62.5 | 4 | 56.5 | 361.9781 | 1783.5096 | 81.023 | 4.9271 | 0.91756 | 110 | 190.0414 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 83.3904 | 125.2286
CID=1324241823 | 6 | 65 | 117.1592 | 4 | 59 | 11.8 | 1.7371 | 148.3861 | 17.3476 | 285.881 | 440.748 | 405.7474 | 35502.9857 | 2.2976 | 0.06144 | 2.3507 | 117.1592 | 275.4005 | 6 | 65 | 4 | 59 | 361.9781 | 1889.8218 | 83.4772 | 5.2208 | 0.91779 | 110 | 193.9487 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 92.0266 | 125.5368
CID=1324241920 | 6 | 67.5 | 119.6923 | 4 | 61.5 | 12.3 | 1.7371 | 148.3861 | 17.3476 | 289.9569 | 441.9247 | 405.7474 | 35793.3292 | 2.2792 | 0.064832 | 2.2049 | 119.6923 | 263.9102 | 6 | 67.5 | 4 | 61.5 | 361.9781 | 2000.8736 | 86.1569 | 5.5276 | 0.91802 | 109.9732 | 198.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 5.223 | 104.302 | 124.8224
CID=-1888996542 | 6 | 69.99 | 122.0248 | 4 | 63.99 | 12.798 | 1.7371 | 148.3861 | 17.3476 | 294.074 | 443.0743 | 405.7474 | 35978.5349 | 1.7308 | 0.065687 | 1.6571 | 116.6407 | 193.2819 | 6 | 69.99 | 4 | 63.99 | 361.9781 | 2116.3519 | 98.2332 | 5.8466 | 0.91774 | 95.3496 | 193.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 116.6406 | 123.8195
CID=-1888996445 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996480 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996639 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996418 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996321 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996356 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996515 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996294 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888996197 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130151685 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130151782 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1130151747 | 9 | 22.5 | 19.4659 | 4 | 16.5 | 3.3 | 1.7357 | 148.2186 | 19.1581 | 222.5675 | 416.6065 | 407.5003 | 21269.1736 | 1.0686 | 0.010269 | 10.1522 | 19.4659 | 197.6226 | 9 | 22.5 | 4 | 16.5 | 400.9358 | 617.2019 | 35.2918 | 1.5394 | 0.77278 | 110 | 38.2713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.8546 | 22.6697
CID=1130151588 | 9 | 25 | 24.5307 | 4 | 19 | 3.8 | 1.7357 | 148.2186 | 19.1581 | 226.0633 | 418.2053 | 407.5003 | 22723.0437 | 1.1949 | 0.011994 | 8.8378 | 24.5307 | 216.798 | 9 | 25 | 4 | 19 | 400.9358 | 665.3809 | 38.5816 | 1.6596 | 0.80159 | 110 | 46.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.2198 | 29.301
CID=1130151809 | 9 | 27.5 | 30.0249 | 4 | 21.5 | 4.3 | 1.7357 | 148.2186 | 19.1581 | 229.5813 | 419.7772 | 407.5003 | 24046.4273 | 1.3228 | 0.013939 | 7.8385 | 30.0249 | 235.3511 | 9 | 27.5 | 4 | 21.5 | 400.9358 | 716.3449 | 41.7154 | 1.7867 | 0.82651 | 110 | 55.1938 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4687 | 35.877
CID=1130151906 | 9 | 30 | 36.1318 | 4 | 24 | 4.8 | 1.7357 | 148.2186 | 19.1581 | 233.1226 | 421.3224 | 407.5003 | 25302.2069 | 1.4585 | 0.016169 | 7.0388 | 36.1318 | 254.3248 | 9 | 30 | 4 | 24 | 400.9358 | 770.1963 | 44.7548 | 1.921 | 0.8481 | 110 | 64.729 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.9305 | 43.1989
CID=1130151871 | 9 | 32.5 | 42.733 | 4 | 26.5 | 5.3 | 1.7357 | 148.2186 | 19.1581 | 236.688 | 422.8412 | 407.5003 | 26478.9243 | 1.5873 | 0.018663 | 6.3447 | 42.733 | 271.1286 | 9 | 32.5 | 4 | 26.5 | 400.9358 | 827.0396 | 47.849 | 2.0628 | 0.86587 | 110 | 74.9838 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2579 | 51.2247
CID=1130151712 | 9 | 35 | 48.2005 | 4 | 29 | 5.8 | 1.7357 | 148.2186 | 19.1581 | 240.2788 | 424.3337 | 407.5003 | 27366.982 | 1.6795 | 0.020893 | 5.8267 | 48.2005 | 280.8477 | 9 | 35 | 4 | 29 | 400.9358 | 886.981 | 50.5967 | 2.2123 | 0.87721 | 110 | 83.4841 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0505 | 57.5838
CID=1130151933 | 9 | 37.5 | 56.1047 | 4 | 31.5 | 6.3 | 1.7357 | 148.2186 | 19.1581 | 243.8959 | 425.8002 | 407.5003 | 28467.8949 | 1.8149 | 0.02406 | 5.2923 | 56.1047 | 296.9256 | 9 | 37.5 | 4 | 31.5 | 400.9358 | 950.1287 | 53.7464 | 2.3698 | 0.88954 | 110 | 95.8275 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6818 | 66.9124
CID=1130152030 | 9 | 40 | 64.596 | 4 | 34 | 6.8 | 1.7357 | 148.2186 | 19.1581 | 247.5407 | 427.2409 | 407.5003 | 29487.6056 | 1.9509 | 0.027585 | 4.831 | 64.596 | 312.0635 | 9 | 40 | 4 | 34 | 400.9358 | 1016.593 | 56.877 | 2.5356 | 0.89886 | 110 | 109.187 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2008 | 77.061
CID=-2083086432 | 9 | 42.5 | 73.4111 | 4 | 36.5 | 7.3 | 1.7357 | 148.2186 | 19.1581 | 251.2145 | 428.656 | 407.5003 | 30458.7378 | 2.0726 | 0.031398 | 4.4123 | 73.4111 | 323.9107 | 9 | 42.5 | 4 | 36.5 | 400.9358 | 1086.4865 | 60.0967 | 2.7099 | 0.90553 | 110 | 123.1731 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9216 | 87.5743
CID=-2083086335 | 9 | 45 | 81.7449 | 4 | 39 | 7.8 | 1.7357 | 148.2186 | 19.1581 | 254.9187 | 430.0457 | 407.5003 | 31282.8264 | 2.1795 | 0.035227 | 4.0681 | 81.7449 | 332.5472 | 9 | 45 | 4 | 39 | 400.9358 | 1159.9242 | 63.1212 | 2.893 | 0.90989 | 110 | 136.4989 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.7915 | 97.396
CID=-2083086370 | 9 | 47.5 | 89.3256 | 4 | 41.5 | 8.3 | 1.7357 | 148.2186 | 19.1581 | 258.655 | 431.4103 | 407.5003 | 31961.5175 | 2.2653 | 0.038971 | 3.7747 | 89.3256 | 337.1749 | 9 | 47.5 | 4 | 41.5 | 400.9358 | 1237.0237 | 66.011 | 3.0853 | 0.9127 | 110 | 148.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.4856 | 105.939
CID=-2083086529 | 9 | 50 | 98.9755 | 4 | 44 | 8.8 | 1.7357 | 148.2186 | 19.1581 | 262.425 | 432.7501 | 407.5003 | 32709.3098 | 2.3823 | 0.043721 | 3.492 | 98.9754 | 345.6193 | 9 | 50 | 4 | 44 | 400.9358 | 1317.9055 | 69.0645 | 3.2871 | 0.91518 | 110 | 164.315 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3087 | 117.1977
CID=-2083086308 | 9 | 52.5 | 107.6322 | 4 | 46.5 | 9.3 | 1.7357 | 148.2186 | 19.1581 | 266.2308 | 434.0651 | 407.5003 | 33382.1668 | 2.4793 | 0.048342 | 3.2541 | 107.6322 | 350.2492 | 9 | 52.5 | 4 | 46.5 | 400.9358 | 1402.6932 | 71.9187 | 3.4985 | 0.91668 | 110 | 178.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.6486 | 126.9601
CID=-2083086211 | 9 | 55 | 108.9541 | 4 | 49 | 9.8 | 1.7357 | 148.2186 | 19.1581 | 270.0745 | 435.3559 | 407.5003 | 33582.9043 | 2.4766 | 0.050234 | 3.1237 | 108.9541 | 340.3443 | 9 | 55 | 4 | 49 | 400.9358 | 1491.5141 | 73.7516 | 3.7201 | 0.91686 | 110 | 180.5493 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.9361 | 126.9601
CID=-2083086246 | 9 | 57.5 | 110.6106 | 4 | 51.5 | 10.3 | 1.7357 | 148.2186 | 19.1581 | 273.9586 | 436.6225 | 407.5003 | 33804.9681 | 2.4737 | 0.052392 | 2.9866 | 110.6107 | 330.3478 | 9 | 57.5 | 4 | 51.5 | 400.9358 | 1584.4992 | 75.7357 | 3.952 | 0.91708 | 110 | 183.2513 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5619 | 126.9602
CID=-2083086405 | 9 | 60 | 112.0987 | 4 | 54 | 10.8 | 1.7357 | 148.2186 | 19.1581 | 277.8855 | 437.8652 | 407.5003 | 34020.4791 | 2.4611 | 0.054625 | 2.8457 | 112.0987 | 318.9966 | 9 | 60 | 4 | 54 | 400.9358 | 1681.7842 | 77.8457 | 4.1946 | 0.91726 | 110 | 185.6799 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.5145 | 126.9601
CID=-2083086184 | 9 | 62.5 | 113.9411 | 4 | 56.5 | 11.3 | 1.7357 | 148.2186 | 19.1581 | 281.8586 | 439.0844 | 407.5003 | 34267.7612 | 2.4424 | 0.057176 | 2.6932 | 113.9411 | 306.8621 | 9 | 62.5 | 4 | 56.5 | 400.9358 | 1783.5096 | 80.1932 | 4.4484 | 0.91747 | 110 | 188.6887 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.8839 | 126.9602
CID=-2083086087 | 9 | 65 | 116.3564 | 4 | 59 | 11.8 | 1.7357 | 148.2186 | 19.1581 | 285.881 | 440.2804 | 407.5003 | 34556.0818 | 2.4235 | 0.060183 | 2.5331 | 116.3564 | 294.7398 | 9 | 65 | 4 | 59 | 400.9358 | 1889.8218 | 82.7568 | 4.7135 | 0.91772 | 110 | 192.636 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 84.545 | 126.9602
CID=1194047326 | 9 | 67.5 | 118.5889 | 4 | 61.5 | 12.3 | 1.7357 | 148.2186 | 19.1581 | 289.9569 | 441.4534 | 407.5003 | 34838.7068 | 2.3985 | 0.063338 | 2.3774 | 118.589 | 281.9329 | 9 | 67.5 | 4 | 61.5 | 400.9358 | 2000.8736 | 85.3904 | 4.9905 | 0.91793 | 110 | 196.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 93.4753 | 126.9601
CID=1194047357 | 9 | 69.99 | 120.8842 | 4 | 63.99 | 12.798 | 1.7357 | 148.2186 | 19.1581 | 294.074 | 442.5993 | 407.5003 | 35133.156 | 2.3671 | 0.066774 | 2.2211 | 120.8842 | 268.4908 | 9 | 69.99 | 4 | 63.99 | 400.9358 | 2116.3519 | 88.1731 | 5.2785 | 0.91812 | 109.5446 | 200.0439 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7948 | 102.6563 | 126.9602
CID=1194047388 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047419 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047450 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047481 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047512 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047543 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047574 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1194047605 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019190791 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019190760 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019190729 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019190698 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2019190667 | 12 | 25 | 15.23 | 4 | 19 | 3.8 | 1.7345 | 147.9949 | 21.1172 | 226.0633 | 417.8241 | 409.2305 | 19884.8168 | 0.96426 | 0.0091276 | 11.5969 | 15.23 | 176.6207 | 12 | 25 | 4 | 19 | 443.0145 | 665.3809 | 35.7022 | 1.5019 | 0.74337 | 88.7522 | 31.1279 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.795 | 16.7083
CID=-2019190636 | 12 | 27.5 | 25.1305 | 4 | 21.5 | 4.3 | 1.7345 | 147.9949 | 21.1172 | 229.5813 | 419.3925 | 409.2305 | 22274.5295 | 1.2759 | 0.012298 | 9.1208 | 25.1305 | 229.2101 | 12 | 27.5 | 4 | 21.5 | 443.0145 | 716.3449 | 40.6378 | 1.617 | 0.80461 | 110 | 47.454 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.1128 | 29.8031
CID=-2019190605 | 12 | 30 | 30.8098 | 4 | 24 | 4.8 | 1.7345 | 147.9949 | 21.1172 | 233.1226 | 420.9344 | 409.2305 | 23572.5545 | 1.4082 | 0.014329 | 8.049 | 30.8098 | 247.9884 | 12 | 30 | 4 | 24 | 443.0145 | 770.1963 | 43.7952 | 1.7385 | 0.82961 | 110 | 56.4248 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0293 | 36.7366
CID=-2019190574 | 12 | 32.5 | 37.1253 | 4 | 26.5 | 5.3 | 1.7345 | 147.9949 | 21.1172 | 236.688 | 422.4497 | 409.2305 | 24834.4198 | 1.5524 | 0.016662 | 7.215 | 37.1253 | 267.8578 | 12 | 32.5 | 4 | 26.5 | 443.0145 | 827.0396 | 46.8124 | 1.8668 | 0.85111 | 110 | 66.2738 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.6766 | 44.2749
CID=-2019190543 | 12 | 35 | 43.9671 | 4 | 29 | 5.8 | 1.7345 | 147.9949 | 21.1172 | 240.2788 | 423.9389 | 409.2305 | 25995.6339 | 1.6936 | 0.019277 | 6.508 | 43.9671 | 286.1387 | 12 | 35 | 4 | 29 | 443.0145 | 886.981 | 49.8325 | 2.0021 | 0.86867 | 110 | 76.9008 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.1723 | 52.5653
CID=-2019190512 | 12 | 37.5 | 49.7168 | 4 | 31.5 | 6.3 | 1.7345 | 147.9949 | 21.1172 | 243.8959 | 425.402 | 409.2305 | 26892.0124 | 1.7934 | 0.021644 | 5.9642 | 49.7168 | 296.5189 | 12 | 37.5 | 4 | 31.5 | 443.0145 | 950.1287 | 52.5887 | 2.1447 | 0.87991 | 110 | 85.8461 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8063 | 59.3536
CID=1356187796 | 12 | 40 | 57.5384 | 4 | 34 | 6.8 | 1.7345 | 147.9949 | 21.1172 | 247.5407 | 426.8393 | 409.2305 | 27940.2419 | 1.9312 | 0.024842 | 5.427 | 57.5384 | 312.262 | 12 | 40 | 4 | 34 | 443.0145 | 1016.593 | 55.6315 | 2.2947 | 0.89136 | 110 | 98.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0173 | 68.7122
CID=1356187827 | 12 | 42.5 | 66.4787 | 4 | 36.5 | 7.3 | 1.7345 | 147.9949 | 21.1172 | 251.2145 | 428.251 | 409.2305 | 28982.797 | 2.08 | 0.028592 | 4.9441 | 66.4787 | 328.6775 | 12 | 42.5 | 4 | 36.5 | 443.0145 | 1086.4865 | 58.7567 | 2.4525 | 0.9005 | 110 | 112.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0083 | 79.3022
CID=1356187858 | 12 | 45 | 75.5888 | 4 | 39 | 7.8 | 1.7345 | 147.9949 | 21.1172 | 254.9187 | 429.6374 | 409.2305 | 29936.4589 | 2.2139 | 0.032592 | 4.5197 | 75.5888 | 341.6375 | 12 | 45 | 4 | 39 | 443.0145 | 1159.9242 | 61.8892 | 2.6183 | 0.90682 | 110 | 126.646 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.8335 | 90.1739
CID=1356187889 | 12 | 47.5 | 85.5663 | 4 | 41.5 | 8.3 | 1.7345 | 147.9949 | 21.1172 | 258.655 | 430.9986 | 409.2305 | 30884.6852 | 2.3465 | 0.037121 | 4.1293 | 85.5663 | 353.3264 | 12 | 47.5 | 4 | 41.5 | 443.0145 | 1237.0237 | 65.1374 | 2.7923 | 0.91142 | 110 | 142.6398 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2059 | 102.0198
CID=1356187920 | 12 | 50 | 92.3955 | 4 | 44 | 8.8 | 1.7345 | 147.9949 | 21.1172 | 262.425 | 432.335 | 409.2305 | 31476.9039 | 2.4271 | 0.040687 | 3.8564 | 92.3955 | 356.3161 | 12 | 50 | 4 | 44 | 443.0145 | 1317.9055 | 67.7856 | 2.9749 | 0.9136 | 110 | 153.6559 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.3372 | 109.7483
CID=1356187951 | 12 | 52.5 | 102.4471 | 4 | 46.5 | 9.3 | 1.7345 | 147.9949 | 21.1172 | 266.2308 | 433.6467 | 409.2305 | 32247.4545 | 2.5464 | 0.045719 | 3.5544 | 102.4471 | 364.1382 | 12 | 52.5 | 4 | 46.5 | 443.0145 | 1402.6932 | 70.9049 | 3.1662 | 0.91585 | 110 | 169.9544 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5194 | 121.423
CID=1356187982 | 12 | 55 | 107.9237 | 4 | 49 | 9.8 | 1.7345 | 147.9949 | 21.1172 | 270.0745 | 434.934 | 409.2305 | 32657.1052 | 2.6024 | 0.049193 | 3.3555 | 107.9237 | 362.1364 | 12 | 55 | 4 | 49 | 443.0145 | 1491.5141 | 73.2859 | 3.3667 | 0.91672 | 110 | 178.8696 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8145 | 126.9602
CID=1356188013 | 12 | 57.5 | 109.3651 | 4 | 51.5 | 10.3 | 1.7345 | 147.9949 | 21.1172 | 273.9586 | 436.1972 | 409.2305 | 32833.9975 | 2.5955 | 0.051205 | 3.2103 | 109.3651 | 351.0999 | 12 | 57.5 | 4 | 51.5 | 443.0145 | 1584.4992 | 75.2391 | 3.5766 | 0.91692 | 110 | 181.2196 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5802 | 126.9601
CID=1356188044 | 12 | 60 | 110.9415 | 4 | 54 | 10.8 | 1.7345 | 147.9949 | 21.1172 | 277.8855 | 437.4365 | 409.2305 | 33033.299 | 2.5888 | 0.05341 | 3.0649 | 110.9415 | 340.0212 | 12 | 60 | 4 | 54 | 443.0145 | 1681.7842 | 77.2758 | 3.7962 | 0.91712 | 110 | 183.7911 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.8856 | 126.9602
CID=1356188075 | 12 | 62.5 | 112.7501 | 4 | 56.5 | 11.3 | 1.7345 | 147.9949 | 21.1172 | 281.8586 | 438.6523 | 409.2305 | 33273.7468 | 2.5801 | 0.055874 | 2.9146 | 112.7501 | 328.6268 | 12 | 62.5 | 4 | 56.5 | 443.0145 | 1783.5096 | 79.448 | 4.0258 | 0.91733 | 110 | 186.7434 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70.1201 | 126.9601
CID=-1857050321 | 12 | 65 | 114.2642 | 4 | 59 | 11.8 | 1.7345 | 147.9949 | 21.1172 | 285.881 | 439.8448 | 409.2305 | 33516.8185 | 2.5447 | 0.058386 | 2.747 | 114.2642 | 313.8827 | 12 | 65 | 4 | 59 | 443.0145 | 1889.8218 | 81.9148 | 4.2658 | 0.9175 | 110 | 189.2165 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 76.1762 | 126.9602
CID=-1857050290 | 12 | 67.5 | 116.3776 | 4 | 61.5 | 12.3 | 1.7345 | 147.9949 | 21.1172 | 289.9569 | 441.0144 | 409.2305 | 33790.8531 | 2.5182 | 0.061377 | 2.5809 | 116.3776 | 300.3563 | 12 | 67.5 | 4 | 61.5 | 443.0145 | 2000.8736 | 84.4863 | 4.5165 | 0.91772 | 110 | 192.6706 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 84.6298 | 126.9602
CID=-1857050259 | 12 | 69.99 | 118.8978 | 4 | 63.99 | 12.798 | 1.7345 | 147.9949 | 21.1172 | 294.074 | 442.1569 | 409.2305 | 34125.0959 | 2.493 | 0.064801 | 2.4146 | 118.8978 | 287.0898 | 12 | 69.99 | 4 | 63.99 | 443.0145 | 2116.3519 | 87.1906 | 4.7772 | 0.91795 | 110 | 196.7927 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 94.7107 | 126.9601
CID=-1857050228 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857050197 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857050166 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857050135 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857050104 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857050073 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1857050042 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162097906 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162097937 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162097968 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162097999 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162098030 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162098061 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162098092 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1162098123 | 15 | 30 | 25.6697 | 4 | 24 | 4.8 | 1.7333 | 147.7132 | 23.2347 | 233.1226 | 420.5719 | 410.9364 | 21819.9113 | 1.359 | 0.012592 | 9.4135 | 25.6697 | 241.6421 | 15 | 30 | 4 | 24 | 488.3739 | 770.1963 | 42.7186 | 1.5771 | 0.80725 | 110 | 48.3134 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3198 | 30.1197
CID=1162098154 | 15 | 32.5 | 31.4175 | 4 | 26.5 | 5.3 | 1.7333 | 147.7132 | 23.2347 | 236.688 | 422.0841 | 410.9364 | 23092.265 | 1.4941 | 0.014676 | 8.2868 | 31.4175 | 260.3492 | 15 | 32.5 | 4 | 26.5 | 488.3739 | 827.0396 | 45.8467 | 1.6935 | 0.83194 | 110 | 57.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0742 | 37.5319
CID=1162098185 | 15 | 35 | 37.8939 | 4 | 29 | 5.8 | 1.7333 | 147.7132 | 23.2347 | 240.2788 | 423.5701 | 410.9364 | 24331.2083 | 1.6457 | 0.017097 | 7.4115 | 37.8939 | 280.8517 | 15 | 35 | 4 | 29 | 488.3739 | 886.981 | 48.8475 | 1.8162 | 0.85335 | 110 | 67.4682 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.7101 | 45.2884
CID=-2051140211 | 15 | 37.5 | 45.0493 | 4 | 31.5 | 6.3 | 1.7333 | 147.7132 | 23.2347 | 243.8959 | 425.03 | 410.9364 | 25502.138 | 1.8016 | 0.01986 | 6.6803 | 45.0493 | 300.9444 | 15 | 37.5 | 4 | 31.5 | 488.3739 | 950.1287 | 51.8284 | 1.9455 | 0.871 | 110 | 78.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.4587 | 53.9129
CID=-2051140180 | 15 | 40 | 52.8485 | 4 | 34 | 6.8 | 1.7333 | 147.7132 | 23.2347 | 247.5407 | 426.4641 | 410.9364 | 26620.3176 | 1.9513 | 0.022974 | 6.033 | 52.8485 | 318.8356 | 15 | 40 | 4 | 34 | 488.3739 | 1016.593 | 54.8931 | 2.0816 | 0.88496 | 110 | 90.7328 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4735 | 63.3068
CID=-2051140149 | 15 | 42.5 | 59.1097 | 4 | 36.5 | 7.3 | 1.7333 | 147.7132 | 23.2347 | 251.2145 | 427.8727 | 410.9364 | 27444.816 | 2.0556 | 0.0257 | 5.5544 | 59.1097 | 328.3201 | 15 | 42.5 | 4 | 36.5 | 488.3739 | 1086.4865 | 57.6012 | 2.2247 | 0.89323 | 110 | 100.5428 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7682 | 70.5569
CID=-2051140118 | 15 | 45 | 68.2475 | 4 | 39 | 7.8 | 1.7333 | 147.7132 | 23.2347 | 254.9187 | 429.2559 | 410.9364 | 28485.8981 | 2.2107 | 0.029595 | 5.0538 | 68.2475 | 344.9099 | 15 | 45 | 4 | 39 | 488.3739 | 1159.9242 | 60.7024 | 2.3751 | 0.90193 | 110 | 114.9662 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.93 | 81.3534
CID=-2051140087 | 15 | 47.5 | 77.8707 | 4 | 41.5 | 8.3 | 1.7333 | 147.7132 | 23.2347 | 258.655 | 430.614 | 410.9364 | 29434.5476 | 2.3648 | 0.033868 | 4.6245 | 77.8707 | 360.1102 | 15 | 47.5 | 4 | 41.5 | 488.3739 | 1237.0237 | 63.7555 | 2.5329 | 0.90805 | 110 | 130.2923 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.6346 | 92.9494
CID=-2051140056 | 15 | 50 | 87.9493 | 4 | 44 | 8.8 | 1.7333 | 147.7132 | 23.2347 | 262.425 | 431.9472 | 410.9364 | 30354.1666 | 2.5043 | 0.038538 | 4.2288 | 87.9493 | 371.9157 | 15 | 50 | 4 | 44 | 488.3739 | 1317.9055 | 66.9155 | 2.6986 | 0.91225 | 110 | 146.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.943 | 104.9514
CID=-2051140025 | 15 | 52.5 | 97.8265 | 4 | 46.5 | 9.3 | 1.7333 | 147.7132 | 23.2347 | 266.2308 | 433.2557 | 410.9364 | 31163.3737 | 2.6322 | 0.043386 | 3.8936 | 97.8265 | 380.8976 | 15 | 52.5 | 4 | 46.5 | 488.3739 | 1402.6932 | 69.9575 | 2.8722 | 0.91493 | 110 | 162.4509 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2093 | 116.6989
CID=-2051139994 | 15 | 55 | 105.9032 | 4 | 49 | 9.8 | 1.7333 | 147.7132 | 23.2347 | 270.0745 | 434.5399 | 410.9364 | 31770.4677 | 2.7229 | 0.047792 | 3.6217 | 105.9033 | 383.5493 | 15 | 55 | 4 | 49 | 488.3739 | 1491.5141 | 72.7483 | 3.054 | 0.91642 | 110 | 175.578 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8297 | 125.5944
CID=-2051139963 | 15 | 57.5 | 108.1461 | 4 | 51.5 | 10.3 | 1.7333 | 147.7132 | 23.2347 | 273.9586 | 435.7999 | 410.9364 | 31983.0446 | 2.7285 | 0.050067 | 3.456 | 108.1461 | 373.749 | 15 | 57.5 | 4 | 51.5 | 488.3739 | 1584.4992 | 74.7753 | 3.2444 | 0.91675 | 110 | 179.232 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.704 | 126.9601
CID=-2051139932 | 15 | 60 | 109.7674 | 4 | 54 | 10.8 | 1.7333 | 147.7132 | 23.2347 | 277.8855 | 437.0361 | 410.9364 | 32169.2934 | 2.7206 | 0.052229 | 3.2976 | 109.7675 | 361.974 | 15 | 60 | 4 | 54 | 488.3739 | 1681.7842 | 76.8192 | 3.4436 | 0.91697 | 110 | 181.8758 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.1896 | 126.9601
CID=1324238376 | 15 | 62.5 | 111.2107 | 4 | 56.5 | 11.3 | 1.7333 | 147.7132 | 23.2347 | 281.8586 | 438.2486 | 410.9364 | 32363.5957 | 2.7063 | 0.054465 | 3.1411 | 111.2107 | 349.3229 | 15 | 62.5 | 4 | 56.5 | 488.3739 | 1783.5096 | 78.9297 | 3.6519 | 0.91715 | 110 | 184.2305 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.9624 | 126.9602
CID=1324238407 | 15 | 65 | 113.0371 | 4 | 59 | 11.8 | 1.7333 | 147.7132 | 23.2347 | 285.881 | 439.4379 | 410.9364 | 32590.2083 | 2.6879 | 0.057038 | 2.9736 | 113.0371 | 336.1313 | 15 | 65 | 4 | 59 | 488.3739 | 1889.8218 | 81.2377 | 3.8696 | 0.91737 | 110 | 187.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71.2677 | 126.9602
CID=1324238438 | 15 | 67.5 | 114.9625 | 4 | 61.5 | 12.3 | 1.7333 | 147.7132 | 23.2347 | 289.9569 | 440.6043 | 410.9364 | 32829.9432 | 2.6591 | 0.059854 | 2.7983 | 114.9625 | 321.7025 | 15 | 67.5 | 4 | 61.5 | 488.3739 | 2000.8736 | 83.7335 | 4.097 | 0.91758 | 110 | 190.3576 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 78.9695 | 126.9602
CID=1324238469 | 15 | 69.99 | 116.635 | 4 | 63.99 | 12.798 | 1.7333 | 147.7132 | 23.2347 | 294.074 | 441.7436 | 410.9364 | 33068.6057 | 2.6179 | 0.062767 | 2.623 | 116.635 | 305.9377 | 15 | 69.99 | 4 | 63.99 | 488.3739 | 2116.3519 | 86.3472 | 4.3335 | 0.91774 | 110 | 193.0914 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 85.6595 | 126.9602
CID=1324238500 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324238531 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324238562 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324238593 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324238624 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=1324238655 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999741 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999710 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999679 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999648 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999617 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999586 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999555 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999524 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999493 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1888999462 | 18 | 32.5 | 27.4591 | 4 | 26.5 | 5.3 | 1.7322 | 147.3721 | 25.5211 | 236.688 | 421.7412 | 412.6163 | 21637.6359 | 1.4852 | 0.013288 | 9.5155 | 27.4592 | 261.288 | 18 | 32.5 | 4 | 26.5 | 537.1767 | 827.0396 | 45.184 | 1.5396 | 0.8156 | 110 | 51.1522 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.839 | 32.3325
CID=1130148486 | 18 | 35 | 31.9527 | 4 | 29 | 5.8 | 1.7322 | 147.3721 | 25.5211 | 240.2788 | 423.2242 | 412.6163 | 22613.2064 | 1.5858 | 0.015011 | 8.5531 | 31.9527 | 273.2957 | 18 | 35 | 4 | 29 | 537.1767 | 886.981 | 47.8801 | 1.6512 | 0.83395 | 110 | 58.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.112 | 38.233
CID=1130148517 | 18 | 37.5 | 38.7117 | 4 | 31.5 | 6.3 | 1.7322 | 147.3721 | 25.5211 | 243.8959 | 424.6812 | 412.6163 | 23849.8822 | 1.745 | 0.017564 | 7.6053 | 38.7117 | 294.4157 | 18 | 37.5 | 4 | 31.5 | 537.1767 | 950.1287 | 50.9308 | 1.7687 | 0.85565 | 110 | 68.7388 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9579 | 46.2963
CID=1130148548 | 18 | 40 | 46.1535 | 4 | 34 | 6.8 | 1.7322 | 147.3721 | 25.5211 | 247.5407 | 426.1123 | 412.6163 | 25027.0761 | 1.9133 | 0.02047 | 6.8431 | 46.1534 | 315.8323 | 18 | 40 | 4 | 34 | 537.1767 | 1016.593 | 53.8963 | 1.8925 | 0.87327 | 110 | 80.2991 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0416 | 55.1907
CID=1130148579 | 18 | 42.5 | 54.1321 | 4 | 36.5 | 7.3 | 1.7322 | 147.3721 | 25.5211 | 251.2145 | 427.5179 | 412.6163 | 26127.7079 | 2.073 | 0.023704 | 6.1808 | 54.1321 | 334.5788 | 18 | 42.5 | 4 | 36.5 | 537.1767 | 1086.4865 | 56.9049 | 2.0226 | 0.88684 | 110 | 92.7394 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9546 | 64.858
CID=1130148610 | 18 | 45 | 60.4966 | 4 | 39 | 7.8 | 1.7322 | 147.3721 | 25.5211 | 254.9187 | 428.8982 | 412.6163 | 26938.7353 | 2.1818 | 0.026523 | 5.6874 | 60.4966 | 344.0708 | 18 | 45 | 4 | 39 | 537.1767 | 1159.9242 | 59.59 | 2.1593 | 0.89478 | 110 | 102.7235 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0409 | 72.3151
CID=1130148641 | 18 | 47.5 | 69.7298 | 4 | 41.5 | 8.3 | 1.7322 | 147.3721 | 25.5211 | 258.655 | 430.2533 | 412.6163 | 27951.2946 | 2.3455 | 0.03053 | 5.1787 | 69.7298 | 361.1093 | 18 | 47.5 | 4 | 41.5 | 537.1767 | 1237.0237 | 62.6187 | 2.3028 | 0.90304 | 110 | 117.318 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.9027 | 83.3388
CID=1130148672 | 18 | 50 | 80.0426 | 4 | 44 | 8.8 | 1.7322 | 147.3721 | 25.5211 | 262.425 | 431.5835 | 412.6163 | 28938.5057 | 2.5174 | 0.035151 | 4.7237 | 80.0426 | 378.0963 | 18 | 50 | 4 | 44 | 537.1767 | 1317.9055 | 65.7027 | 2.4534 | 0.90912 | 110 | 133.7694 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7506 | 95.4733
CID=1130148703 | 18 | 52.5 | 90.3639 | 4 | 46.5 | 9.3 | 1.7322 | 147.3721 | 25.5211 | 266.2308 | 432.8891 | 412.6163 | 29836.6127 | 2.6683 | 0.040024 | 4.3225 | 90.3639 | 390.6007 | 18 | 52.5 | 4 | 46.5 | 537.1767 | 1402.6932 | 68.7894 | 2.6112 | 0.91302 | 110 | 150.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.0197 | 107.8119
CID=1130148734 | 18 | 55 | 101.6775 | 4 | 49 | 9.8 | 1.7322 | 147.3721 | 25.5211 | 270.0745 | 434.1702 | 412.6163 | 30734.8842 | 2.8192 | 0.045563 | 3.9523 | 101.6775 | 401.859 | 18 | 55 | 4 | 49 | 537.1767 | 1491.5141 | 71.9809 | 2.7766 | 0.91571 | 110 | 168.7034 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9579 | 121.2507
CID=1130148765 | 18 | 57.5 | 107.141 | 4 | 51.5 | 10.3 | 1.7322 | 147.3721 | 25.5211 | 273.9586 | 435.4273 | 412.6163 | 31151.9633 | 2.8804 | 0.049053 | 3.7278 | 107.141 | 399.3964 | 18 | 57.5 | 4 | 51.5 | 537.1767 | 1584.4992 | 74.3324 | 2.9497 | 0.91661 | 110 | 177.5942 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.6837 | 126.9601
CID=-2083089631 | 18 | 60 | 108.5065 | 4 | 54 | 10.8 | 1.7322 | 147.3721 | 25.5211 | 277.8855 | 436.6604 | 412.6163 | 31306.5212 | 2.8697 | 0.051052 | 3.5632 | 108.5065 | 386.635 | 18 | 60 | 4 | 54 | 537.1767 | 1681.7842 | 76.3143 | 3.1308 | 0.9168 | 110 | 179.8195 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1459 | 126.9601
CID=-2083089600 | 18 | 62.5 | 110.1181 | 4 | 56.5 | 11.3 | 1.7322 | 147.3721 | 25.5211 | 281.8586 | 437.87 | 412.6163 | 31510.8876 | 2.8498 | 0.053296 | 3.3839 | 110.1182 | 372.6311 | 18 | 62.5 | 4 | 56.5 | 537.1767 | 1783.5096 | 78.5002 | 3.3202 | 0.91701 | 110 | 182.4478 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59.592 | 126.9601
CID=-2083089569 | 18 | 65 | 111.5844 | 4 | 59 | 11.8 | 1.7322 | 147.3721 | 25.5211 | 285.881 | 439.0563 | 412.6163 | 31714.9346 | 2.8294 | 0.055638 | 3.2136 | 111.5844 | 358.5871 | 18 | 65 | 4 | 59 | 537.1767 | 1889.8218 | 80.7007 | 3.5181 | 0.9172 | 110 | 184.8404 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.4574 | 126.9601
CID=-2083089538 | 18 | 67.5 | 113.2579 | 4 | 61.5 | 12.3 | 1.7322 | 147.3721 | 25.5211 | 289.9569 | 440.2196 | 412.6163 | 31942.2463 | 2.8012 | 0.058253 | 3.0337 | 113.2579 | 343.5941 | 18 | 67.5 | 4 | 61.5 | 537.1767 | 2000.8736 | 83.0817 | 3.7248 | 0.91739 | 110 | 187.5727 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.1509 | 126.9602
CID=-2083089507 | 18 | 69.99 | 115.201 | 4 | 63.99 | 12.798 | 1.7322 | 147.3721 | 25.5211 | 294.074 | 441.3558 | 412.6163 | 32187.5359 | 2.7661 | 0.061198 | 2.8463 | 115.201 | 327.8958 | 18 | 69.99 | 4 | 63.99 | 537.1767 | 2116.3519 | 85.6431 | 3.9398 | 0.9176 | 110 | 190.7473 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79.9236 | 126.9602
CID=-2083089476 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083089445 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083089414 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083089383 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-2083089352 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489715066 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489714969 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489715004 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489715163 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489714942 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489714845 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489714880 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489715039 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489715314 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489715217 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682513301 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682513204 | 21 | 35 | 21.7574 | 4 | 29 | 5.8 | 1.7312 | 146.9698 | 27.9878 | 240.2788 | 422.8982 | 414.2684 | 20077.336 | 1.3566 | 0.011633 | 10.8482 | 21.7574 | 236.0282 | 21 | 35 | 4 | 29 | 589.5892 | 886.981 | 45.7159 | 1.5044 | 0.7866 | 88.9969 | 42.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.5732 | 24.4855
CID=-1682513239 | 21 | 37.5 | 32.6057 | 4 | 31.5 | 6.3 | 1.7312 | 146.9698 | 27.9878 | 243.8959 | 424.3523 | 414.2684 | 22167.0459 | 1.6858 | 0.015397 | 8.8085 | 32.6057 | 287.2069 | 21 | 37.5 | 4 | 31.5 | 589.5892 | 950.1287 | 49.9822 | 1.6115 | 0.83633 | 110 | 59.2342 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0444 | 38.7928
CID=-1682513398 | 21 | 40 | 39.5835 | 4 | 34 | 6.8 | 1.7312 | 146.9698 | 27.9878 | 247.5407 | 425.7807 | 414.2684 | 23384.0199 | 1.8503 | 0.018066 | 7.7937 | 39.5835 | 308.5005 | 21 | 40 | 4 | 34 | 589.5892 | 1016.593 | 53.063 | 1.7242 | 0.85802 | 110 | 70.0929 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5838 | 47.2501
CID=-1682513177 | 21 | 42.5 | 47.2316 | 4 | 36.5 | 7.3 | 1.7312 | 146.9698 | 27.9878 | 251.2145 | 427.1835 | 414.2684 | 24563.722 | 2.028 | 0.021094 | 7.0011 | 47.2316 | 330.6709 | 21 | 42.5 | 4 | 36.5 | 589.5892 | 1086.4865 | 56.0126 | 1.8428 | 0.87539 | 110 | 81.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8198 | 56.3689
CID=-1682513080 | 21 | 45 | 55.4974 | 4 | 39 | 7.8 | 1.7312 | 146.9698 | 27.9878 | 254.9187 | 428.5609 | 414.2684 | 25653.1358 | 2.2042 | 0.024489 | 6.3291 | 55.4974 | 351.2464 | 21 | 45 | 4 | 39 | 589.5892 | 1159.9242 | 58.9561 | 1.9673 | 0.88873 | 110 | 94.8762 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9995 | 66.3301
CID=-1682513115 | 21 | 47.5 | 63.9527 | 4 | 41.5 | 8.3 | 1.7312 | 146.9698 | 27.9878 | 258.655 | 429.9132 | 414.2684 | 26647.7484 | 2.3625 | 0.028123 | 5.7486 | 63.9527 | 367.6413 | 21 | 47.5 | 4 | 41.5 | 589.5892 | 1237.0237 | 61.9049 | 2.0981 | 0.89826 | 110 | 108.171 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2319 | 76.5263
CID=-1682513274 | 21 | 50 | 71.5235 | 4 | 44 | 8.8 | 1.7312 | 146.9698 | 27.9878 | 262.425 | 431.2407 | 414.2684 | 27460.8235 | 2.491 | 0.031619 | 5.2883 | 71.5235 | 378.2348 | 21 | 50 | 4 | 44 | 589.5892 | 1317.9055 | 64.6537 | 2.2353 | 0.9043 | 110 | 120.1684 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9299 | 85.388
CID=-1682513549 | 21 | 52.5 | 81.9552 | 4 | 46.5 | 9.3 | 1.7312 | 146.9698 | 27.9878 | 266.2308 | 432.5434 | 414.2684 | 28441.0988 | 2.6681 | 0.036388 | 4.8194 | 81.9552 | 394.9769 | 21 | 52.5 | 4 | 46.5 | 589.5892 | 1402.6932 | 67.7099 | 2.3791 | 0.90998 | 110 | 136.8365 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.5049 | 97.772
CID=-1682513452 | 21 | 55 | 92.8424 | 4 | 49 | 9.8 | 1.7312 | 146.9698 | 27.9878 | 270.0745 | 433.8218 | 414.2684 | 29335.8423 | 2.8419 | 0.041598 | 4.4138 | 92.8424 | 409.7884 | 21 | 55 | 4 | 49 | 589.5892 | 1491.5141 | 70.7286 | 2.5298 | 0.91372 | 110 | 154.3786 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.7568 | 110.8709
CID=126006352 | 21 | 57.5 | 104.274 | 4 | 51.5 | 10.3 | 1.7312 | 146.9698 | 27.9878 | 273.9586 | 435.076 | 414.2684 | 30207.2297 | 3.0013 | 0.047327 | 4.0385 | 104.274 | 421.1157 | 21 | 57.5 | 4 | 51.5 | 589.5892 | 1584.4992 | 73.8458 | 2.6875 | 0.91616 | 110 | 172.9259 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.7196 | 124.4588
CID=126006449 | 21 | 60 | 107.3133 | 4 | 54 | 10.8 | 1.7312 | 146.9698 | 27.9878 | 277.8855 | 436.3063 | 414.2684 | 30474.1022 | 3.0216 | 0.049942 | 3.8401 | 107.3133 | 412.0987 | 21 | 60 | 4 | 54 | 589.5892 | 1681.7842 | 75.9623 | 2.8525 | 0.91663 | 110 | 177.8749 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.373 | 126.9601
CID=126006414 | 21 | 62.5 | 108.9027 | 4 | 56.5 | 11.3 | 1.7312 | 146.9698 | 27.9878 | 281.8586 | 437.513 | 414.2684 | 30655.9509 | 3.0097 | 0.052115 | 3.6594 | 108.9028 | 398.5183 | 21 | 62.5 | 4 | 56.5 | 589.5892 | 1783.5096 | 78.0393 | 3.025 | 0.91685 | 110 | 180.4656 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7306 | 126.9601
CID=126006255 | 21 | 65 | 110.3398 | 4 | 59 | 11.8 | 1.7312 | 146.9698 | 27.9878 | 285.881 | 438.6964 | 414.2684 | 30849.241 | 2.9858 | 0.054377 | 3.4741 | 110.3398 | 383.3368 | 21 | 65 | 4 | 59 | 589.5892 | 1889.8218 | 80.2347 | 3.2053 | 0.91704 | 110 | 182.8094 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.4786 | 126.9602
CID=126006476 | 21 | 67.5 | 111.9784 | 4 | 61.5 | 12.3 | 1.7312 | 146.9698 | 27.9878 | 289.9569 | 439.8569 | 414.2684 | 31082.5173 | 2.9563 | 0.056901 | 3.2819 | 111.9784 | 367.5051 | 21 | 67.5 | 4 | 61.5 | 589.5892 | 2000.8736 | 82.5783 | 3.3937 | 0.91724 | 110 | 185.4835 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.0331 | 126.9602
CID=126006573 | 21 | 69.99 | 113.7588 | 4 | 63.99 | 12.798 | 1.7312 | 146.9698 | 27.9878 | 294.074 | 440.9902 | 414.2684 | 31313.9222 | 2.925 | 0.059682 | 3.0905 | 113.7588 | 351.5661 | 21 | 69.99 | 4 | 63.99 | 589.5892 | 2116.3519 | 85.0152 | 3.5895 | 0.91745 | 110 | 188.3908 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.1546 | 126.9602
CID=126006538 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126006379 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126006104 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126006201 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653771 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653674 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653709 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653868 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653647 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653550 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653585 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653744 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844654019 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844653922 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521664486 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521664389 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521664424 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521664583 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521664362 | 24 | 40 | 33.2159 | 4 | 34 | 6.8 | 1.7302 | 146.5045 | 30.6472 | 247.5407 | 425.4661 | 415.8906 | 21721.6929 | 1.7892 | 0.015784 | 9.0682 | 33.2159 | 301.2073 | 24 | 40 | 4 | 34 | 645.7808 | 1016.593 | 52.1138 | 1.5742 | 0.8385 | 110 | 60.1868 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.4516 | 39.1373
CID=-1521664265 | 24 | 42.5 | 40.2405 | 4 | 36.5 | 7.3 | 1.7302 | 146.5045 | 30.6472 | 251.2145 | 426.8662 | 415.8906 | 22911.5912 | 1.9567 | 0.018513 | 8.0072 | 40.2405 | 322.2154 | 24 | 42.5 | 4 | 36.5 | 645.7808 | 1086.4865 | 55.1686 | 1.6824 | 0.85974 | 110 | 71.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.6006 | 48.1204
CID=-1521664300 | 24 | 45 | 48.0481 | 4 | 39 | 7.8 | 1.7302 | 146.5045 | 30.6472 | 254.9187 | 428.241 | 415.8906 | 24067.2555 | 2.1423 | 0.021651 | 7.1771 | 48.0481 | 344.846 | 24 | 45 | 4 | 39 | 645.7808 | 1159.9242 | 58.1102 | 1.7962 | 0.87693 | 110 | 83.2469 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7334 | 57.4863
CID=-1521664459 | 24 | 47.5 | 56.5994 | 4 | 41.5 | 8.3 | 1.7302 | 146.5045 | 30.6472 | 258.655 | 429.5907 | 415.8906 | 25159.3706 | 2.3337 | 0.025211 | 6.483 | 56.5994 | 366.9331 | 24 | 47.5 | 4 | 41.5 | 645.7808 | 1237.0237 | 61.0255 | 1.9155 | 0.89018 | 110 | 96.6028 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.8929 | 67.8348
CID=-1521664734 | 24 | 50 | 65.8131 | 4 | 44 | 8.8 | 1.7302 | 146.5045 | 30.6472 | 262.425 | 430.9154 | 415.8906 | 26199.7813 | 2.5152 | 0.029197 | 5.865 | 65.8131 | 385.9927 | 24 | 50 | 4 | 44 | 645.7808 | 1317.9055 | 64.017 | 2.0408 | 0.89993 | 110 | 111.111 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2397 | 79.0043
CID=-1521664637 | 24 | 52.5 | 72.9738 | 4 | 46.5 | 9.3 | 1.7302 | 146.5045 | 30.6472 | 266.2308 | 432.2155 | 415.8906 | 26952.7677 | 2.6367 | 0.032624 | 5.4075 | 72.9738 | 394.6077 | 24 | 52.5 | 4 | 46.5 | 645.7808 | 1402.6932 | 66.6846 | 2.1721 | 0.90525 | 110 | 122.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.8629 | 87.3441
CID=-1714462721 | 24 | 55 | 83.5488 | 4 | 49 | 9.8 | 1.7302 | 146.5045 | 30.6472 | 270.0745 | 433.4912 | 415.8906 | 27911.8929 | 2.8245 | 0.037556 | 4.9296 | 83.5488 | 411.8614 | 24 | 55 | 4 | 49 | 645.7808 | 1491.5141 | 69.6865 | 2.3096 | 0.91064 | 110 | 139.3956 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4237 | 99.9239
CID=-1714462624 | 24 | 57.5 | 95.3388 | 4 | 51.5 | 10.3 | 1.7302 | 146.5045 | 30.6472 | 273.9586 | 434.7427 | 415.8906 | 28847.6367 | 3.022 | 0.043249 | 4.4989 | 95.3389 | 428.9234 | 24 | 57.5 | 4 | 51.5 | 645.7808 | 1584.4992 | 72.7457 | 2.4536 | 0.91436 | 110 | 158.419 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.2609 | 113.6981
CID=-1714462659 | 24 | 60 | 106.4663 | 4 | 54 | 10.8 | 1.7302 | 146.5045 | 30.6472 | 277.8855 | 435.9703 | 415.8906 | 29664.4902 | 3.1833 | 0.04901 | 4.1263 | 106.4664 | 439.3147 | 24 | 60 | 4 | 54 | 645.7808 | 1681.7842 | 75.7527 | 2.6043 | 0.91651 | 110 | 176.4951 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.9849 | 126.9601
CID=-1714462818 | 24 | 62.5 | 107.8384 | 4 | 56.5 | 11.3 | 1.7302 | 146.5045 | 30.6472 | 281.8586 | 437.1743 | 415.8906 | 29839.3898 | 3.1702 | 0.051038 | 3.9402 | 107.8384 | 424.9097 | 24 | 62.5 | 4 | 56.5 | 645.7808 | 1783.5096 | 77.7641 | 2.7618 | 0.91671 | 110 | 178.7306 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4735 | 126.9601
CID=-1714462597 | 24 | 65 | 109.1781 | 4 | 59 | 11.8 | 1.7302 | 146.5045 | 30.6472 | 285.881 | 438.355 | 415.8906 | 30015.3089 | 3.1474 | 0.053196 | 3.748 | 109.1781 | 409.1979 | 24 | 65 | 4 | 59 | 645.7808 | 1889.8218 | 79.8957 | 2.9264 | 0.91689 | 110 | 180.9145 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.832 | 126.9601
CID=-1714462500 | 24 | 67.5 | 110.6056 | 4 | 61.5 | 12.3 | 1.7302 | 146.5045 | 30.6472 | 289.9569 | 439.5127 | 415.8906 | 30222.9929 | 3.1179 | 0.055555 | 3.55 | 110.6057 | 392.6494 | 24 | 67.5 | 4 | 61.5 | 645.7808 | 2000.8736 | 82.1535 | 3.0984 | 0.91708 | 110 | 183.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.542 | 126.9602
CID=-1714462535 | 24 | 69.99 | 112.3909 | 4 | 63.99 | 12.798 | 1.7302 | 146.5045 | 30.6472 | 294.074 | 440.6434 | 415.8906 | 30454.627 | 3.0853 | 0.058257 | 3.3441 | 112.3909 | 375.8435 | 24 | 69.99 | 4 | 63.99 | 645.7808 | 2116.3519 | 84.561 | 3.2772 | 0.91729 | 110 | 186.157 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68.6833 | 126.9601
CID=-1714462694 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714462969 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714462872 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94056932 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057029 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94056994 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94056835 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057056 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057153 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057118 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94056959 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94056684 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94056781 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876603191 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876603094 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876603129 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876603288 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876603067 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876602970 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876603005 | 27 | 42.5 | 34.9323 | 4 | 36.5 | 7.3 | 1.7292 | 145.9744 | 33.5123 | 251.2145 | 426.563 | 417.481 | 21463.0211 | 1.9329 | 0.016556 | 9.2 | 34.9323 | 321.3784 | 27 | 42.5 | 4 | 36.5 | 705.9244 | 1086.4865 | 54.4982 | 1.5391 | 0.84429 | 110 | 62.8622 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.346 | 41.1277
CID=-1876603164 | 27 | 45 | 40.7919 | 4 | 39 | 7.8 | 1.7292 | 145.9744 | 33.5123 | 254.9187 | 427.9352 | 417.481 | 22437.766 | 2.0691 | 0.018944 | 8.2458 | 40.7919 | 336.3625 | 27 | 45 | 4 | 39 | 705.9244 | 1159.9242 | 57.2594 | 1.6431 | 0.86116 | 110 | 71.9694 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5416 | 48.8753
CID=-1876603439 | 27 | 47.5 | 48.9487 | 4 | 41.5 | 8.3 | 1.7292 | 145.9744 | 33.5123 | 258.655 | 429.2823 | 417.481 | 23593.9565 | 2.265 | 0.022261 | 7.3493 | 48.9488 | 359.7411 | 27 | 47.5 | 4 | 41.5 | 705.9244 | 1237.0237 | 60.2517 | 1.7523 | 0.87856 | 110 | 84.6494 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0626 | 58.5775
CID=-1876603342 | 27 | 50 | 57.8612 | 4 | 44 | 8.8 | 1.7292 | 145.9744 | 33.5123 | 262.425 | 430.6045 | 417.481 | 24698.5224 | 2.4708 | 0.026022 | 6.6212 | 57.8613 | 383.113 | 27 | 50 | 4 | 44 | 705.9244 | 1317.9055 | 63.1765 | 1.8669 | 0.89176 | 110 | 98.5821 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.8529 | 69.1973
CID=-1553613906 | 27 | 52.5 | 67.341 | 4 | 46.5 | 9.3 | 1.7292 | 145.9744 | 33.5123 | 266.2308 | 431.902 | 417.481 | 25725.8232 | 2.6672 | 0.030191 | 5.9907 | 67.3409 | 403.4207 | 27 | 52.5 | 4 | 46.5 | 705.9244 | 1402.6932 | 66.1249 | 1.987 | 0.90121 | 110 | 113.5295 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.4146 | 80.6498
CID=-1553613809 | 27 | 55 | 75.2209 | 4 | 49 | 9.8 | 1.7292 | 145.9744 | 33.5123 | 270.0745 | 433.1751 | 417.481 | 26517.1706 | 2.8074 | 0.033979 | 5.5015 | 75.2209 | 413.8257 | 27 | 55 | 4 | 49 | 705.9244 | 1491.5141 | 68.8532 | 2.1129 | 0.90661 | 110 | 126.0588 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.1505 | 89.9111
CID=-1553613844 | 27 | 57.5 | 85.5115 | 4 | 51.5 | 10.3 | 1.7292 | 145.9744 | 33.5123 | 273.9586 | 434.4241 | 417.481 | 27420.8162 | 2.9927 | 0.038924 | 5.0229 | 85.5115 | 429.5168 | 27 | 57.5 | 4 | 51.5 | 705.9244 | 1584.4992 | 71.7825 | 2.2446 | 0.9114 | 110 | 142.5516 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.5589 | 102.1624
CID=-1553614003 | 27 | 60 | 97.3645 | 4 | 54 | 10.8 | 1.7292 | 145.9744 | 33.5123 | 277.8855 | 435.6491 | 417.481 | 28346.4087 | 3.1952 | 0.044788 | 4.5811 | 97.3645 | 446.0391 | 27 | 60 | 4 | 54 | 705.9244 | 1681.7842 | 74.8133 | 2.3824 | 0.91483 | 110 | 161.7017 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7067 | 116.2504
CID=-1553613782 | 27 | 62.5 | 106.6147 | 4 | 56.5 | 11.3 | 1.7292 | 145.9744 | 33.5123 | 281.8586 | 436.8505 | 417.481 | 29014.4542 | 3.3382 | 0.049933 | 4.2464 | 106.6147 | 452.7289 | 27 | 62.5 | 4 | 56.5 | 705.9244 | 1783.5096 | 77.5246 | 2.5265 | 0.91653 | 110 | 176.7368 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5787 | 126.9601
CID=-1553613685 | 27 | 65 | 108.0437 | 4 | 59 | 11.8 | 1.7292 | 145.9744 | 33.5123 | 285.881 | 438.0286 | 417.481 | 29213.1713 | 3.3158 | 0.052069 | 4.0388 | 108.0437 | 436.3617 | 27 | 65 | 4 | 59 | 705.9244 | 1889.8218 | 79.6456 | 2.6771 | 0.91674 | 110 | 179.0652 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.2946 | 126.9601
CID=-1553613720 | 27 | 67.5 | 109.3345 | 4 | 61.5 | 12.3 | 1.7292 | 145.9744 | 33.5123 | 289.9569 | 439.1838 | 417.481 | 29401.764 | 3.286 | 0.054302 | 3.8327 | 109.3345 | 419.0417 | 27 | 67.5 | 4 | 61.5 | 705.9244 | 2000.8736 | 81.8423 | 2.8344 | 0.91691 | 110 | 181.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.4575 | 126.9602
CID=-1553613879 | 27 | 69.99 | 111.0421 | 4 | 63.99 | 12.798 | 1.7292 | 145.9744 | 33.5123 | 294.074 | 440.3118 | 417.481 | 29616.0463 | 3.2555 | 0.056892 | 3.618 | 111.0422 | 401.7459 | 27 | 69.99 | 4 | 63.99 | 705.9244 | 2116.3519 | 84.1793 | 2.998 | 0.91713 | 110 | 183.9554 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.2881 | 126.9602
CID=-1553614154 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553614057 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412141 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412044 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412079 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412238 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412017 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411920 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411955 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412114 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412389 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746412292 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718265 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718234 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718203 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718172 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718141 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718110 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718079 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718048 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489718513 | 30 | 45 | 30.7347 | 4 | 39 | 7.8 | 1.7283 | 145.3777 | 36.5977 | 254.9187 | 427.6403 | 419.0371 | 20243.0992 | 1.882 | 0.015351 | 10.0494 | 30.7347 | 308.8648 | 30 | 45 | 4 | 39 | 770.1963 | 1159.9242 | 55.7908 | 1.506 | 0.82932 | 110 | 56.3071 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2285 | 35.2368
CID=-1489718482 | 30 | 47.5 | 41.4557 | 4 | 41.5 | 8.3 | 1.7283 | 145.3777 | 36.5977 | 258.655 | 428.9849 | 419.0371 | 21988.976 | 2.191 | 0.019432 | 8.4765 | 41.4557 | 351.3979 | 30 | 47.5 | 4 | 41.5 | 770.1963 | 1237.0237 | 59.4046 | 1.6061 | 0.86281 | 110 | 73.0001 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.3626 | 49.4867
CID=-1682516500 | 30 | 50 | 49.8909 | 4 | 44 | 8.8 | 1.7283 | 145.3777 | 36.5977 | 262.425 | 430.3047 | 419.0371 | 23133.2147 | 2.3943 | 0.022912 | 7.5158 | 49.8909 | 374.9713 | 30 | 50 | 4 | 44 | 770.1963 | 1317.9055 | 62.4355 | 1.7111 | 0.88021 | 110 | 86.1175 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.758 | 59.6018
CID=-1682516469 | 30 | 52.5 | 58.9735 | 4 | 46.5 | 9.3 | 1.7283 | 145.3777 | 36.5977 | 266.2308 | 431.5997 | 419.0371 | 24232.5716 | 2.6099 | 0.026813 | 6.7626 | 58.9735 | 398.8146 | 30 | 52.5 | 4 | 46.5 | 770.1963 | 1402.6932 | 65.345 | 1.8212 | 0.89307 | 110 | 100.3287 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.5286 | 70.4551
CID=-1682516438 | 30 | 55 | 68.7499 | 4 | 49 | 9.8 | 1.7283 | 145.3777 | 36.5977 | 270.0745 | 432.8703 | 419.0371 | 25250.8311 | 2.8251 | 0.031186 | 6.1213 | 68.7499 | 420.8398 | 30 | 55 | 4 | 49 | 770.1963 | 1491.5141 | 68.2483 | 1.9365 | 0.90232 | 110 | 115.7629 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2091 | 82.2635
CID=-1682516407 | 30 | 57.5 | 79.2998 | 4 | 51.5 | 10.3 | 1.7283 | 145.3777 | 36.5977 | 273.9586 | 434.1168 | 419.0371 | 26230.8908 | 3.0316 | 0.036102 | 5.5463 | 79.2998 | 439.8228 | 30 | 57.5 | 4 | 51.5 | 770.1963 | 1584.4992 | 71.2253 | 2.0573 | 0.90876 | 110 | 132.5795 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0207 | 95.0594
CID=-1682516376 | 30 | 60 | 87.2964 | 4 | 54 | 10.8 | 1.7283 | 145.3777 | 36.5977 | 277.8855 | 435.3393 | 419.0371 | 26928.8517 | 3.1663 | 0.040288 | 5.1197 | 87.2964 | 446.9315 | 30 | 60 | 4 | 54 | 770.1963 | 1681.7842 | 73.8949 | 2.1836 | 0.91203 | 110 | 145.4257 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.1156 | 104.3567
CID=-1682516345 | 30 | 62.5 | 99.274 | 4 | 56.5 | 11.3 | 1.7283 | 145.3777 | 36.5977 | 281.8586 | 436.5383 | 419.0371 | 27837.3288 | 3.3788 | 0.04636 | 4.6689 | 99.274 | 463.5035 | 30 | 62.5 | 4 | 56.5 | 770.1963 | 1783.5096 | 76.8874 | 2.3157 | 0.91524 | 110 | 164.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2449 | 118.617
CID=-1682516314 | 30 | 65 | 107.0505 | 4 | 59 | 11.8 | 1.7283 | 145.3777 | 36.5977 | 285.881 | 437.7139 | 419.0371 | 28402.038 | 3.4963 | 0.051042 | 4.3489 | 107.0505 | 465.5488 | 30 | 65 | 4 | 59 | 770.1963 | 1889.8218 | 79.4645 | 2.4537 | 0.91659 | 110 | 177.4467 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.3217 | 126.9601
CID=-1682516283 | 30 | 67.5 | 108.4145 | 4 | 61.5 | 12.3 | 1.7283 | 145.3777 | 36.5977 | 289.9569 | 438.8665 | 419.0371 | 28592.099 | 3.4736 | 0.053247 | 4.1358 | 108.4145 | 448.3783 | 30 | 67.5 | 4 | 61.5 | 770.1963 | 2000.8736 | 81.5995 | 2.5979 | 0.91679 | 110 | 179.6696 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.7777 | 126.9602
CID=-1682516748 | 30 | 69.99 | 109.9059 | 4 | 63.99 | 12.798 | 1.7283 | 145.3777 | 36.5977 | 294.074 | 439.9919 | 419.0371 | 28820.0678 | 3.4372 | 0.055672 | 3.9081 | 109.9059 | 429.525 | 30 | 69.99 | 4 | 63.99 | 770.1963 | 2116.3519 | 83.8948 | 2.7478 | 0.91699 | 110 | 182.1015 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.743 | 126.9602
CID=-1682516717 | -18 | -5 | 11.4819 | 4 | -11 | 0 | 1.7524 | 147.8757 | 7.2169 | 185.3801 | 401.7246 | 391.078 | 23679.9387 | 0.4936 | 0.0071895 | 8.8429 | 11.4819 | 101.5332 | -18 | -5 | 4 | -11 | 144.6004 | 243.3424 | 12.6883 | 1.6829 | 0.71248 | 110 | 24.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.5498 | 11.5167
CID=126003153 | -18 | -2.5 | 14.5752 | 4 | -8.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 188.676 | 403.6805 | 391.078 | 25372.7045 | 0.56416 | 0.0080899 | 7.8343 | 14.5752 | 114.1872 | -18 | -2.5 | 4 | -8.5 | 144.6004 | 267.1911 | 16.3107 | 1.8478 | 0.73833 | 110 | 29.9932 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.577 | 14.6204
CID=126003184 | -18 | 0 | 18.1232 | 4 | -6 | 0 | 1.7524 | 147.8757 | 7.2169 | 191.9873 | 405.6071 | 391.078 | 26944.0283 | 0.6335 | 0.0091741 | 6.9592 | 18.1232 | 126.1239 | -18 | 0 | 4 | -6 | 144.6004 | 292.8032 | 20.0499 | 2.0249 | 0.76403 | 110 | 36.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.7893 | 18.1802
CID=126003215 | -18 | 2.5 | 21.2784 | 4 | -3.5 | 0 | 1.7524 | 147.8757 | 7.2169 | 195.3144 | 407.5045 | 391.078 | 28159.3883 | 0.68582 | 0.010205 | 6.3096 | 21.2784 | 134.2586 | -18 | 2.5 | 4 | -3.5 | 144.6004 | 320.2635 | 23.3227 | 2.2148 | 0.78382 | 110 | 41.2456 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8511 | 21.3458
CID=126003246 | -18 | 5 | 25.6898 | 4 | -1 | 0 | 1.7524 | 147.8757 | 7.2169 | 198.6579 | 409.3731 | 391.078 | 29597.8594 | 0.7528 | 0.011642 | 5.6386 | 25.6898 | 144.8546 | -18 | 5 | 4 | -1 | 144.6004 | 349.6586 | 27.2869 | 2.4181 | 0.80735 | 110 | 48.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5588 | 25.7708
CID=126003277 | -18 | 7.5 | 30.5463 | 4 | 1.5 | 0.3 | 1.7524 | 147.8757 | 7.2169 | 202.0183 | 411.2128 | 391.078 | 30950.429 | 0.81841 | 0.01327 | 5.0654 | 30.5463 | 154.728 | -18 | 7.5 | 4 | 1.5 | 144.6004 | 381.0767 | 31.3006 | 2.6354 | 0.82858 | 110 | 56.0118 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.097 | 30.644
CID=126003308 | -18 | 10 | 35.8428 | 4 | 4 | 0.8 | 1.7524 | 147.8757 | 7.2169 | 205.396 | 413.024 | 391.078 | 32182.1904 | 0.88262 | 0.015098 | 4.5724 | 35.8428 | 163.8865 | -18 | 10 | 4 | 4 | 144.6004 | 414.6075 | 35.3553 | 2.8673 | 0.8472 | 110 | 64.2793 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0916 | 35.9571
CID=126003339 | -18 | 12.5 | 39.8166 | 4 | 6.5 | 1.3 | 1.7524 | 147.8757 | 7.2169 | 208.7918 | 414.8068 | 391.078 | 32983.5554 | 0.9304 | 0.016595 | 4.2595 | 39.8166 | 169.5992 | -18 | 12.5 | 4 | 6.5 | 144.6004 | 450.3422 | 38.2738 | 3.1144 | 0.85864 | 110 | 70.4549 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.2624 | 39.94
CID=126003370 | -18 | 15 | 45.3097 | 4 | 9 | 1.8 | 1.7524 | 147.8757 | 7.2169 | 212.2062 | 416.5615 | 391.078 | 34130.998 | 0.99225 | 0.018628 | 3.9172 | 45.3097 | 177.4864 | -18 | 15 | 4 | 9 | 144.6004 | 488.3739 | 41.8607 | 3.3774 | 0.87155 | 110 | 78.9872 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.7059 | 45.4484
CID=126002905 | -18 | 17.5 | 50.5036 | 4 | 11.5 | 2.3 | 1.7524 | 147.8757 | 7.2169 | 215.6398 | 418.2881 | 391.078 | 35112.7209 | 1.0535 | 0.020649 | 3.6596 | 50.5036 | 184.8215 | -18 | 17.5 | 4 | 11.5 | 144.6004 | 528.7968 | 44.8561 | 3.657 | 0.88124 | 110 | 87.0727 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3419 | 50.6552
CID=126002936 | -18 | 20 | 51.5031 | 4 | 14 | 2.8 | 1.7524 | 147.8757 | 7.2169 | 219.0933 | 419.9871 | 391.078 | 35352.5986 | 1.0652 | 0.021389 | 3.557 | 51.5031 | 183.1954 | -18 | 20 | 4 | 14 | 144.6004 | 571.7069 | 46.0365 | 3.9537 | 0.88287 | 110 | 88.6319 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3788 | 51.6444
CID=-1844656970 | -18 | 22.5 | 51.3821 | 4 | 16.5 | 3.3 | 1.7524 | 147.8757 | 7.2169 | 222.5675 | 421.6585 | 391.078 | 35417.0429 | 1.049 | 0.02179 | 3.4404 | 51.3821 | 176.7746 | -18 | 22.5 | 4 | 16.5 | 144.6004 | 617.2019 | 47.4326 | 4.2683 | 0.88268 | 110 | 88.4432 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.5651 | 51.5068
CID=-1844656939 | -18 | 25 | 51.4593 | 4 | 19 | 3.8 | 1.7524 | 147.8757 | 7.2169 | 226.0633 | 423.3026 | 391.078 | 35483.8434 | 1.0473 | 0.022278 | 3.3584 | 51.4593 | 172.8189 | -18 | 25 | 4 | 19 | 144.6004 | 665.3809 | 48.4388 | 4.6015 | 0.8828 | 110 | 88.5636 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8699 | 30.9668 | 51.5623
CID=-1844656908 | -18 | 27.5 | 51.7906 | 4 | 21.5 | 4.3 | 1.7524 | 147.8757 | 7.2169 | 229.5813 | 424.9196 | 391.078 | 35673.6215 | 1.0311 | 0.022878 | 3.2151 | 51.7906 | 166.5131 | -18 | 27.5 | 4 | 21.5 | 144.6004 | 716.3449 | 50.3352 | 4.954 | 0.88333 | 110 | 89.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8426 | 35.6287 | 51.8719
CID=-1844656877 | -18 | 30 | 51.8387 | 4 | 24 | 4.8 | 1.7524 | 147.8757 | 7.2169 | 233.1226 | 426.5097 | 391.078 | 35851.4543 | 1.0001 | 0.023408 | 3.0474 | 51.8387 | 157.9728 | -18 | 30 | 4 | 24 | 144.6004 | 770.1963 | 52.6994 | 5.3264 | 0.88341 | 110 | 89.1558 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.9637 | 51.8934
CID=-1844656846 | -18 | 32.5 | 51.3736 | 4 | 26.5 | 5.3 | 1.7524 | 147.8757 | 7.2169 | 236.688 | 428.0733 | 391.078 | 36005.3158 | 0.96712 | 0.02378 | 2.9064 | 51.3736 | 149.3142 | -18 | 32.5 | 4 | 26.5 | 144.6004 | 827.0396 | 54.7922 | 5.7195 | 0.88267 | 110 | 88.4298 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 48.2998 | 51.389
CID=-1844656815 | -18 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844656784 | -18 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844656753 | -18 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844657218 | -18 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844657187 | -18 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667685 | -18 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667654 | -18 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667623 | -18 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667592 | -18 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667561 | -18 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667530 | -18 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667499 | -18 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667468 | -18 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667933 | -18 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521667902 | -18 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714465920 | -15 | -5 | 0 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714465889 | -15 | -2.5 | 11.7782 | 4 | -8.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 188.676 | 402.9994 | 392.9623 | 23114.8318 | 0.53133 | 0.0073114 | 9.2157 | 11.7782 | 108.5444 | -15 | -2.5 | 4 | -8.5 | 163.9401 | 267.1911 | 14.4562 | 1.6298 | 0.71511 | 110 | 25.0243 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4.9292 | 11.8126
CID=-1714465858 | -15 | 0 | 15.092 | 4 | -6 | 0 | 1.7499 | 148.1062 | 8.1279 | 191.9873 | 404.9188 | 392.9623 | 24835.5575 | 0.60906 | 0.0082826 | 8.1106 | 15.092 | 122.4058 | -15 | 0 | 4 | -6 | 163.9401 | 292.8032 | 18.1109 | 1.786 | 0.74232 | 110 | 30.8896 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.7776 | 15.1388
CID=-1714465827 | -15 | 2.5 | 18.8249 | 4 | -3.5 | 0 | 1.7499 | 148.1062 | 8.1279 | 195.3144 | 406.8092 | 392.9623 | 26408.9107 | 0.68556 | 0.0094328 | 7.1979 | 18.8249 | 135.5 | -15 | 2.5 | 4 | -3.5 | 163.9401 | 320.2635 | 21.7489 | 1.9535 | 0.76867 | 110 | 37.2091 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.9172 | 18.8847
CID=-1714465796 | -15 | 5 | 23.0397 | 4 | -1 | 0 | 1.7499 | 148.1062 | 8.1279 | 198.6579 | 408.6707 | 392.9623 | 27882.348 | 0.76075 | 0.010778 | 6.4157 | 23.0397 | 147.8168 | -15 | 5 | 4 | -1 | 163.9401 | 349.6586 | 25.4753 | 2.1328 | 0.79375 | 110 | 44.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.3095 | 23.1137
CID=-1714465765 | -15 | 7.5 | 26.6901 | 4 | 1.5 | 0.3 | 1.7499 | 148.1062 | 8.1279 | 202.0183 | 410.5034 | 392.9623 | 29022.2279 | 0.81683 | 0.012021 | 5.8437 | 26.6901 | 155.9693 | -15 | 7.5 | 4 | 1.5 | 163.9401 | 381.0767 | 28.686 | 2.3245 | 0.81209 | 110 | 49.9345 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.7669 | 26.7752
CID=-1714465734 | -15 | 10 | 31.9019 | 4 | 4 | 0.8 | 1.7499 | 148.1062 | 8.1279 | 205.396 | 412.3077 | 392.9623 | 30407.6825 | 0.88934 | 0.013777 | 5.2288 | 31.9019 | 166.8099 | -15 | 10 | 4 | 4 | 163.9401 | 414.6075 | 32.7014 | 2.529 | 0.83376 | 110 | 58.1343 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.7699 | 32.0031
CID=-1714465703 | -15 | 12.5 | 37.4272 | 4 | 6.5 | 1.3 | 1.7499 | 148.1062 | 8.1279 | 208.7918 | 414.0836 | 392.9623 | 31651.026 | 0.96041 | 0.015702 | 4.726 | 37.4272 | 176.8798 | -15 | 12.5 | 4 | 6.5 | 163.9401 | 450.3422 | 36.5774 | 2.747 | 0.852 | 110 | 66.743 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.601 | 37.5469
CID=-1714466168 | -15 | 15 | 41.8367 | 4 | 9 | 1.8 | 1.7499 | 148.1062 | 8.1279 | 212.2062 | 415.8315 | 392.9623 | 32499.4469 | 1.0124 | 0.01736 | 4.3742 | 41.8368 | 183.0018 | -15 | 15 | 4 | 9 | 163.9401 | 488.3739 | 39.6772 | 2.979 | 0.86374 | 110 | 73.5919 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.8508 | 41.9673
CID=-1714466137 | -15 | 17.5 | 47.6911 | 4 | 11.5 | 2.3 | 1.7499 | 148.1062 | 8.1279 | 215.6398 | 417.5513 | 392.9623 | 33546.6973 | 1.081 | 0.019542 | 4.0194 | 47.6912 | 191.6886 | -15 | 17.5 | 4 | 11.5 | 163.9401 | 528.7968 | 43.2036 | 3.2255 | 0.87626 | 110 | 82.6913 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.3412 | 47.8386
CID=94053733 | -15 | 20 | 53.4327 | 4 | 14 | 2.8 | 1.7499 | 148.1062 | 8.1279 | 219.0933 | 419.2435 | 392.9623 | 34593.7282 | 1.148 | 0.021779 | 3.7357 | 53.4327 | 199.61 | -15 | 20 | 4 | 14 | 163.9401 | 571.7069 | 46.3574 | 3.4873 | 0.88583 | 110 | 91.6457 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.1691 | 53.5948
CID=94053764 | -15 | 22.5 | 58.2751 | 4 | 16.5 | 3.3 | 1.7499 | 148.1062 | 8.1279 | 222.5675 | 420.9082 | 392.9623 | 35393.3138 | 1.202 | 0.023815 | 3.5145 | 58.2751 | 204.8076 | -15 | 22.5 | 4 | 16.5 | 163.9401 | 617.2019 | 49.0368 | 3.7648 | 0.89225 | 110 | 99.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0585 | 58.447
CID=94053795 | -15 | 25 | 58.6482 | 4 | 19 | 3.8 | 1.7499 | 148.1062 | 8.1279 | 226.0633 | 422.5457 | 392.9623 | 35516.3133 | 1.2013 | 0.024439 | 3.4186 | 58.6482 | 200.4921 | -15 | 25 | 4 | 19 | 163.9401 | 665.3809 | 50.1975 | 4.0587 | 0.89269 | 110 | 99.8176 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.8402 | 58.803
CID=94053826 | -15 | 27.5 | 58.4398 | 4 | 21.5 | 4.3 | 1.7499 | 148.1062 | 8.1279 | 229.5813 | 424.156 | 392.9623 | 35536.6684 | 1.1833 | 0.024894 | 3.3082 | 58.4398 | 193.3303 | -15 | 27.5 | 4 | 21.5 | 163.9401 | 716.3449 | 51.595 | 4.3696 | 0.89245 | 110 | 99.4903 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.3546 | 58.5759
CID=94053857 | -15 | 30 | 57.8316 | 4 | 24 | 4.8 | 1.7499 | 148.1062 | 8.1279 | 233.1226 | 425.7396 | 392.9623 | 35549.4647 | 1.1647 | 0.025232 | 3.219 | 57.8316 | 186.1625 | -15 | 30 | 4 | 24 | 163.9401 | 770.1963 | 52.7602 | 4.698 | 0.89172 | 110 | 98.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.422 | 57.9392
CID=94053888 | -15 | 32.5 | 58.3097 | 4 | 26.5 | 5.3 | 1.7499 | 148.1062 | 8.1279 | 236.688 | 427.2966 | 392.9623 | 35752.3732 | 1.1462 | 0.02598 | 3.072 | 58.3097 | 179.1256 | -15 | 32.5 | 4 | 26.5 | 163.9401 | 827.0396 | 54.816 | 5.0448 | 0.89229 | 110 | 99.286 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.4958 | 58.3942
CID=94053919 | -15 | 35 | 58.8985 | 4 | 29 | 5.8 | 1.7499 | 148.1062 | 8.1279 | 240.2788 | 428.8272 | 392.9623 | 35981.2944 | 1.1278 | 0.026807 | 2.9236 | 58.8985 | 172.1977 | -15 | 35 | 4 | 29 | 163.9401 | 886.981 | 57.0141 | 5.4104 | 0.89299 | 110 | 100.2109 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.0343 | 58.9531
CID=94053950 | -15 | 37.5 | 56.5788 | 4 | 31.5 | 6.3 | 1.7499 | 148.1062 | 8.1279 | 243.8959 | 430.3317 | 392.9623 | 35987.7189 | 1.0733 | 0.026585 | 2.8278 | 56.5788 | 159.9951 | -15 | 37.5 | 4 | 31.5 | 163.9401 | 950.1287 | 58.4545 | 5.7956 | 0.89015 | 110 | 96.5704 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 55.3815 | 56.5848
CID=94053485 | -15 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94053516 | -15 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606390 | -15 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606359 | -15 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606328 | -15 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606297 | -15 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606266 | -15 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606235 | -15 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606204 | -15 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606173 | -15 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606638 | -15 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876606607 | -15 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553617105 | -15 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553617074 | -12 | -5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553617043 | -12 | -2.5 | 0 | 4 | -7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553617012 | -12 | 0 | 12.3643 | 4 | -6 | 0 | 1.7476 | 148.2918 | 9.1273 | 191.9873 | 404.2823 | 394.8346 | 22715.23 | 0.58034 | 0.0075089 | 9.5209 | 12.3643 | 117.7201 | -12 | 0 | 4 | -6 | 185.2442 | 292.8032 | 16.4939 | 1.5806 | 0.72021 | 110 | 26.0837 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.4538 | 12.3991
CID=-1553616981 | -12 | 2.5 | 15.5918 | 4 | -3.5 | 0 | 1.7476 | 148.2918 | 9.1273 | 195.3144 | 406.166 | 394.8346 | 24305.892 | 0.6555 | 0.0084755 | 8.3881 | 15.5918 | 130.7849 | -12 | 2.5 | 4 | -3.5 | 185.2442 | 320.2635 | 19.9703 | 1.7289 | 0.7461 | 110 | 31.7509 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9439 | 15.6403
CID=-1553616950 | -12 | 5 | 19.4834 | 4 | -1 | 0 | 1.7476 | 148.2918 | 9.1273 | 198.6579 | 408.021 | 394.8346 | 25870.6549 | 0.73975 | 0.0096855 | 7.4485 | 19.4834 | 145.1217 | -12 | 5 | 4 | -1 | 185.2442 | 349.6586 | 23.4744 | 1.8876 | 0.77289 | 110 | 38.3002 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3298 | 19.5445
CID=-1553616919 | -12 | 7.5 | 23.8998 | 4 | 1.5 | 0.3 | 1.7476 | 148.2918 | 9.1273 | 202.0183 | 409.8472 | 394.8346 | 27338.9395 | 0.82247 | 0.011106 | 6.6354 | 23.8998 | 158.5858 | -12 | 7.5 | 4 | 1.5 | 185.2442 | 381.0767 | 27.0944 | 2.0572 | 0.79834 | 110 | 45.4845 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.5649 | 23.9769
CID=-1553616888 | -12 | 10 | 27.7174 | 4 | 4 | 0.8 | 1.7476 | 148.2918 | 9.1273 | 205.396 | 411.6451 | 394.8346 | 28465.8809 | 0.88378 | 0.012416 | 6.0403 | 27.7174 | 167.4224 | -12 | 10 | 4 | 4 | 185.2442 | 414.6075 | 30.2288 | 2.2382 | 0.81676 | 110 | 51.5604 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.993 | 27.8065
CID=-1553617353 | -12 | 12.5 | 33.1245 | 4 | 6.5 | 1.3 | 1.7476 | 148.2918 | 9.1273 | 208.7918 | 413.4146 | 394.8346 | 29822.7338 | 0.96365 | 0.014255 | 5.4123 | 33.1245 | 179.2802 | -12 | 12.5 | 4 | 6.5 | 185.2442 | 450.3422 | 34.0656 | 2.4311 | 0.83817 | 110 | 60.0441 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1391 | 33.2299
CID=-1553617322 | -12 | 15 | 38.9766 | 4 | 9 | 1.8 | 1.7476 | 148.2918 | 9.1273 | 212.2062 | 415.1561 | 394.8346 | 31087.0725 | 1.0419 | 0.016307 | 4.8817 | 38.9766 | 190.2718 | -12 | 15 | 4 | 9 | 185.2442 | 488.3739 | 37.8896 | 2.6364 | 0.85638 | 110 | 69.1503 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0304 | 39.1019
CID=-1746415340 | -12 | 17.5 | 45.3624 | 4 | 11.5 | 2.3 | 1.7476 | 148.2918 | 9.1273 | 215.6398 | 416.8697 | 394.8346 | 32252.8517 | 1.1183 | 0.018611 | 4.4178 | 45.3624 | 200.4018 | -12 | 17.5 | 4 | 11.5 | 185.2442 | 528.7968 | 41.7901 | 2.8546 | 0.87166 | 110 | 79.0692 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.4121 | 45.5079
CID=-1746415309 | -12 | 20 | 50.0067 | 4 | 14 | 2.8 | 1.7476 | 148.2918 | 9.1273 | 219.0933 | 418.5557 | 394.8346 | 32994.7418 | 1.1741 | 0.020455 | 4.1261 | 50.0067 | 206.3307 | -12 | 20 | 4 | 14 | 185.2442 | 571.7069 | 44.5797 | 3.0862 | 0.88041 | 110 | 86.298 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.032 | 50.1624
CID=-1746415278 | -12 | 22.5 | 56.6109 | 4 | 16.5 | 3.3 | 1.7476 | 148.2918 | 9.1273 | 222.5675 | 420.2141 | 394.8346 | 34073.1524 | 1.248 | 0.023015 | 3.7978 | 56.6109 | 214.9956 | -12 | 22.5 | 4 | 16.5 | 185.2442 | 617.2019 | 48.0715 | 3.3318 | 0.89019 | 110 | 96.6208 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.8538 | 56.7855
CID=-1746415247 | -12 | 25 | 62.8016 | 4 | 19 | 3.8 | 1.7476 | 148.2918 | 9.1273 | 226.0633 | 421.8454 | 394.8346 | 35009.5687 | 1.3205 | 0.025548 | 3.5486 | 62.8016 | 222.8573 | -12 | 25 | 4 | 19 | 185.2442 | 665.3809 | 51.0174 | 3.5919 | 0.89716 | 110 | 106.3546 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9272 | 62.9919
CID=-1746415216 | -12 | 27.5 | 65.485 | 4 | 21.5 | 4.3 | 1.7476 | 148.2918 | 9.1273 | 229.5813 | 423.4496 | 394.8346 | 35446.7065 | 1.3513 | 0.027003 | 3.41 | 65.485 | 223.3039 | -12 | 27.5 | 4 | 21.5 | 185.2442 | 716.3449 | 52.7461 | 3.867 | 0.89965 | 110 | 110.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.6206 | 65.6702
CID=-1746415185 | -12 | 30 | 65.7723 | 4 | 24 | 4.8 | 1.7476 | 148.2918 | 9.1273 | 233.1226 | 425.027 | 394.8346 | 35540.2975 | 1.3489 | 0.027694 | 3.3165 | 65.7723 | 218.1339 | -12 | 30 | 4 | 24 | 185.2442 | 770.1963 | 53.9399 | 4.1577 | 0.8999 | 110 | 111.0465 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8883 | 32.3085 | 65.9405
CID=-1746415154 | -12 | 32.5 | 65.6557 | 4 | 26.5 | 5.3 | 1.7476 | 148.2918 | 9.1273 | 236.688 | 426.5779 | 394.8346 | 35587.0026 | 1.3298 | 0.028277 | 3.2031 | 65.6557 | 210.2988 | -12 | 32.5 | 4 | 26.5 | 185.2442 | 827.0396 | 55.4501 | 4.4646 | 0.8998 | 110 | 110.8621 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.6126 | 65.8016
CID=-1746415123 | -12 | 35 | 65.5228 | 4 | 29 | 5.8 | 1.7476 | 148.2918 | 9.1273 | 240.2788 | 428.1024 | 394.8346 | 35680.6578 | 1.3091 | 0.028886 | 3.0879 | 65.5228 | 202.3303 | -12 | 35 | 4 | 29 | 185.2442 | 886.981 | 57.053 | 4.7882 | 0.89968 | 110 | 110.6519 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.4028 | 65.639
CID=-1746415588 | -12 | 37.5 | 66.0192 | 4 | 31.5 | 6.3 | 1.7476 | 148.2918 | 9.1273 | 243.8959 | 429.6009 | 394.8346 | 35871.6643 | 1.2883 | 0.029762 | 2.9455 | 66.0192 | 194.4567 | -12 | 37.5 | 4 | 31.5 | 185.2442 | 950.1287 | 59.1398 | 5.1291 | 0.90011 | 110 | 111.437 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.9875 | 66.1098
CID=-1746415557 | -12 | 40 | 66.0482 | 4 | 34 | 6.8 | 1.7476 | 148.2918 | 9.1273 | 247.5407 | 431.0734 | 394.8346 | 36027.8415 | 1.2663 | 0.03051 | 2.8239 | 66.0482 | 186.5123 | -12 | 40 | 4 | 34 | 185.2442 | 1016.593 | 61.0119 | 5.4879 | 0.90014 | 110 | 111.4829 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7776 | 55.8685 | 66.0993
CID=-1489717244 | -12 | 42.5 | 63.9561 | 4 | 36.5 | 7.3 | 1.7476 | 148.2918 | 9.1273 | 251.2145 | 432.5204 | 394.8346 | 36100.6105 | 1.2063 | 0.030473 | 2.7088 | 63.9561 | 173.2466 | -12 | 42.5 | 4 | 36.5 | 185.2442 | 1086.4865 | 62.8433 | 5.8652 | 0.89827 | 110 | 108.1764 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 63.1387 | 63.9602
CID=-1489717147 | -12 | 45 | 0 | 4 | 39 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717050 | -12 | 47.5 | 0 | 4 | 41.5 | 8.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717209 | -12 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717120 | -12 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717023 | -12 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489716926 | -12 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717085 | -12 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717492 | -12 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489717395 | -12 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682515479 | -12 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682515382 | -12 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682515285 | -9 | -5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682515444 | -9 | -2.5 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682515355 | -9 | 0 | 0 | 4 | -4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682515258 | -9 | 2.5 | 10.3484 | 4 | -3.5 | 0 | 1.7455 | 148.4312 | 10.2212 | 195.3144 | 405.5712 | 396.6938 | 20990.5919 | 0.55504 | 0.0070691 | 10.801 | 10.3484 | 111.7732 | -9 | 2.5 | 4 | -3.5 | 208.6448 | 320.2635 | 16.4025 | 1.535 | 0.70212 | 110 | 22.3934 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.8776 | 10.3709
CID=-1682515161 | -9 | 5 | 16.0408 | 4 | -1 | 0 | 1.7455 | 148.4312 | 10.2212 | 198.6579 | 407.4201 | 396.6938 | 23768.227 | 0.70323 | 0.0086594 | 8.6819 | 16.0408 | 139.2647 | -9 | 5 | 4 | -1 | 208.6448 | 349.6586 | 21.8419 | 1.6759 | 0.74942 | 110 | 32.5203 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5.9672 | 16.0914
CID=-1682515320 | -9 | 7.5 | 20.1231 | 4 | 1.5 | 0.3 | 1.7455 | 148.4312 | 10.2212 | 202.0183 | 409.2404 | 396.6938 | 25342.1158 | 0.79579 | 0.0099388 | 7.6986 | 20.1231 | 154.9204 | -9 | 7.5 | 4 | 1.5 | 208.6448 | 381.0767 | 25.2707 | 1.8264 | 0.77688 | 110 | 39.3545 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.3549 | 20.1873
CID=-1682515727 | -9 | 10 | 24.7498 | 4 | 4 | 0.8 | 1.7455 | 148.4312 | 10.2212 | 205.396 | 411.0322 | 396.6938 | 26808.0056 | 0.88668 | 0.011439 | 6.8534 | 24.7498 | 169.6199 | -9 | 10 | 4 | 4 | 208.6448 | 414.6075 | 28.798 | 1.9871 | 0.8027 | 110 | 46.846 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.9222 | 24.8293
CID=-1682515630 | -9 | 12.5 | 29.2714 | 4 | 6.5 | 1.3 | 1.7455 | 148.4312 | 10.2212 | 208.7918 | 412.7959 | 396.6938 | 28044.0844 | 0.96378 | 0.012976 | 6.1868 | 29.2714 | 181.0962 | -9 | 12.5 | 4 | 6.5 | 208.6448 | 450.3422 | 32.1071 | 2.1584 | 0.82343 | 110 | 54.0099 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.5321 | 29.3656
CID=126004174 | -9 | 15 | 34.3044 | 4 | 9 | 1.8 | 1.7455 | 148.4312 | 10.2212 | 212.2062 | 414.5315 | 396.6938 | 29251.2587 | 1.0412 | 0.014731 | 5.5997 | 34.3044 | 192.0952 | -9 | 15 | 4 | 9 | 208.6448 | 488.3739 | 35.5078 | 2.3407 | 0.84222 | 110 | 61.8841 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3102 | 34.4149
CID=126004271 | -9 | 17.5 | 40.5893 | 4 | 11.5 | 2.3 | 1.7455 | 148.4312 | 10.2212 | 215.6398 | 416.2392 | 396.6938 | 30560.0435 | 1.1272 | 0.016946 | 5.0279 | 40.5893 | 204.0803 | -9 | 17.5 | 4 | 11.5 | 208.6448 | 528.7968 | 39.3664 | 2.5344 | 0.86064 | 110 | 71.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.7558 | 40.7191
CID=126004368 | -9 | 20 | 47.2 | 4 | 14 | 2.8 | 1.7455 | 148.4312 | 10.2212 | 219.0933 | 417.9194 | 396.6938 | 31728.0856 | 1.2114 | 0.019356 | 4.5583 | 47.2 | 215.1501 | -9 | 20 | 4 | 14 | 208.6448 | 571.7069 | 43.0863 | 2.7401 | 0.87533 | 110 | 81.927 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.9978 | 47.3518
CID=126004209 | -9 | 22.5 | 52.4917 | 4 | 16.5 | 3.3 | 1.7455 | 148.4312 | 10.2212 | 222.5675 | 419.5721 | 396.6938 | 32535.7583 | 1.2735 | 0.021444 | 4.2244 | 52.4917 | 221.7436 | -9 | 22.5 | 4 | 16.5 | 208.6448 | 617.2019 | 46.1121 | 2.9581 | 0.88442 | 110 | 90.1755 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.6774 | 52.6566
CID=126004298 | -9 | 25 | 59.281 | 4 | 19 | 3.8 | 1.7455 | 148.4312 | 10.2212 | 226.0633 | 421.1976 | 396.6938 | 33486.4941 | 1.3529 | 0.024113 | 3.8942 | 59.2809 | 230.8514 | -9 | 25 | 4 | 19 | 208.6448 | 665.3809 | 49.4579 | 3.1891 | 0.89343 | 110 | 100.8118 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.5308 | 59.4656
CID=126004395 | -9 | 27.5 | 66.2203 | 4 | 21.5 | 4.3 | 1.7455 | 148.4312 | 10.2212 | 229.5813 | 422.7961 | 396.6938 | 34507.8705 | 1.4322 | 0.026949 | 3.6142 | 66.2203 | 239.3337 | -9 | 27.5 | 4 | 21.5 | 208.6448 | 716.3449 | 52.6273 | 3.4333 | 0.90028 | 110 | 111.7552 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.7566 | 66.4236
CID=126004492 | -9 | 30 | 73.1125 | 4 | 24 | 4.8 | 1.7455 | 148.4312 | 10.2212 | 233.1226 | 424.3678 | 396.6938 | 35392.9323 | 1.5105 | 0.029897 | 3.3793 | 73.1125 | 247.0677 | -9 | 30 | 4 | 24 | 208.6448 | 770.1963 | 55.556 | 3.6914 | 0.90534 | 110 | 122.6974 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.1758 | 73.3333
CID=126004333 | -9 | 32.5 | 73.5122 | 4 | 26.5 | 5.3 | 1.7455 | 148.4312 | 10.2212 | 236.688 | 425.913 | 396.6938 | 35504.5062 | 1.514 | 0.030704 | 3.2953 | 73.5122 | 242.2479 | -9 | 32.5 | 4 | 26.5 | 208.6448 | 827.0396 | 56.6465 | 3.9639 | 0.90559 | 110 | 123.3343 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.425 | 73.7137
CID=126003926 | -9 | 35 | 73.1741 | 4 | 29 | 5.8 | 1.7455 | 148.4312 | 10.2212 | 240.2788 | 427.4319 | 396.6938 | 35541.4281 | 1.491 | 0.031287 | 3.1871 | 73.1741 | 233.2127 | -9 | 35 | 4 | 29 | 208.6448 | 886.981 | 58.1017 | 4.2512 | 0.90538 | 110 | 122.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.4523 | 73.3536
CID=126004023 | -9 | 37.5 | 73.2342 | 4 | 31.5 | 6.3 | 1.7455 | 148.4312 | 10.2212 | 243.8959 | 428.9247 | 396.6938 | 35591.1345 | 1.4884 | 0.03205 | 3.1055 | 73.2342 | 227.4284 | -9 | 37.5 | 4 | 31.5 | 208.6448 | 950.1287 | 59.2591 | 4.5538 | 0.90542 | 110 | 122.8913 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8724 | 42.9142 | 73.3866
CID=-1844655949 | -9 | 40 | 73.9234 | 4 | 34 | 6.8 | 1.7455 | 148.4312 | 10.2212 | 247.5407 | 430.3916 | 396.6938 | 35789.5075 | 1.4667 | 0.033092 | 2.9594 | 73.9234 | 218.7681 | -9 | 40 | 4 | 34 | 208.6448 | 1016.593 | 61.3801 | 4.8724 | 0.90584 | 110 | 123.9895 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.0108 | 74.0486
CID=-1844655852 | -9 | 42.5 | 74.4209 | 4 | 36.5 | 7.3 | 1.7455 | 148.4312 | 10.2212 | 251.2145 | 431.833 | 396.6938 | 35970.2058 | 1.4434 | 0.03412 | 2.8216 | 74.4209 | 209.9829 | -9 | 42.5 | 4 | 36.5 | 208.6448 | 1086.4865 | 63.4927 | 5.2074 | 0.90614 | 110 | 124.7826 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.1264 | 74.5178
CID=-1844655755 | -9 | 45 | 74.4773 | 4 | 39 | 7.8 | 1.7455 | 148.4312 | 10.2212 | 254.9187 | 433.2489 | 396.6938 | 35552.8119 | 1.0155 | 0.031284 | 2.2149 | 65.0043 | 143.9788 | -9 | 45 | 4 | 39 | 208.6448 | 1159.9242 | 74.7802 | 5.5593 | 0.89922 | 98.353 | 109.8322 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 64.4822 | 74.5276
CID=-1844655914 | -9 | 47.5 | 70.7824 | 4 | 41.5 | 8.3 | 1.7455 | 148.4312 | 10.2212 | 258.655 | 434.6398 | 396.6938 | 36119.6991 | 1.3082 | 0.034478 | 2.5514 | 70.7774 | 180.5813 | -9 | 47.5 | 4 | 41.5 | 208.6448 | 1237.0237 | 67.9309 | 5.9289 | 0.90379 | 109.5196 | 118.9822 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 71.7723 | 70.7774
CID=-1844655825 | -9 | 50 | 0 | 4 | 44 | 8.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844655728 | -9 | 52.5 | 0 | 4 | 46.5 | 9.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844655631 | -9 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844655790 | -9 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844656197 | -9 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844656100 | -9 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666664 | -9 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666567 | -9 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666470 | -9 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666629 | -6 | -5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666540 | -6 | -2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666443 | -6 | 0 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666346 | -6 | 2.5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666505 | -6 | 5 | 0 | 4 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521666912 | -6 | 7.5 | 16.4101 | 4 | 1.5 | 0.3 | 1.7436 | 148.523 | 11.416 | 202.0183 | 408.6791 | 398.5385 | 23226.739 | 0.75253 | 0.0088263 | 9.012 | 16.4101 | 147.8874 | -6 | 7.5 | 4 | 1.5 | 234.2779 | 381.0767 | 23.6827 | 1.6266 | 0.75211 | 110 | 33.1501 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6.453 | 16.4601
CID=-1521666815 | -6 | 10 | 20.752 | 4 | 4 | 0.8 | 1.7436 | 148.523 | 11.416 | 205.396 | 410.4654 | 398.5385 | 24823.3556 | 0.85373 | 0.010195 | 7.9458 | 20.752 | 164.8921 | -6 | 10 | 4 | 4 | 234.2779 | 414.6075 | 27.1384 | 1.7697 | 0.7807 | 110 | 40.386 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.6696 | 20.8178
CID=-1714464899 | -6 | 12.5 | 25.5851 | 4 | 6.5 | 1.3 | 1.7436 | 148.523 | 11.416 | 208.7918 | 412.2236 | 398.5385 | 26291.4178 | 0.95337 | 0.011775 | 7.0704 | 25.5851 | 180.8983 | -6 | 12.5 | 4 | 6.5 | 234.2779 | 450.3422 | 30.5736 | 1.9223 | 0.80684 | 110 | 48.1787 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.2176 | 25.6674
CID=-1714464802 | -6 | 15 | 30.9892 | 4 | 9 | 1.8 | 1.7436 | 148.523 | 11.416 | 212.2062 | 413.9537 | 398.5385 | 27668.9026 | 1.0511 | 0.013596 | 6.32 | 30.9892 | 195.8522 | -6 | 15 | 4 | 9 | 234.2779 | 488.3739 | 34.0875 | 2.0846 | 0.83031 | 110 | 56.706 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.7286 | 31.091
CID=-1714464705 | -6 | 17.5 | 35.5308 | 4 | 11.5 | 2.3 | 1.7436 | 148.523 | 11.416 | 215.6398 | 415.6561 | 398.5385 | 28711.9126 | 1.1221 | 0.015233 | 5.7762 | 35.5308 | 205.2334 | -6 | 17.5 | 4 | 11.5 | 234.2779 | 528.7968 | 37.1025 | 2.2571 | 0.84622 | 110 | 63.7938 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.814 | 35.6449
CID=-1714464864 | -6 | 20 | 42.0469 | 4 | 14 | 2.8 | 1.7436 | 148.523 | 11.416 | 219.0933 | 417.3308 | 398.5385 | 29988.6705 | 1.2164 | 0.017552 | 5.1911 | 42.0469 | 218.2686 | -6 | 20 | 4 | 14 | 234.2779 | 571.7069 | 40.8157 | 2.4403 | 0.86425 | 110 | 73.9183 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.1569 | 42.1821
CID=-1714464775 | -6 | 22.5 | 48.9989 | 4 | 16.5 | 3.3 | 1.7436 | 148.523 | 11.416 | 222.5675 | 418.9782 | 398.5385 | 31172.4138 | 1.3086 | 0.020108 | 4.6996 | 48.9989 | 230.2765 | -6 | 22.5 | 4 | 16.5 | 234.2779 | 617.2019 | 44.4741 | 2.6345 | 0.87865 | 110 | 84.7275 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.5255 | 49.1571
CID=-1714464678 | -6 | 25 | 56.5987 | 4 | 19 | 3.8 | 1.7436 | 148.523 | 11.416 | 226.0633 | 420.5983 | 398.5385 | 32277.5378 | 1.399 | 0.022983 | 4.2632 | 56.5987 | 241.2937 | -6 | 25 | 4 | 19 | 234.2779 | 665.3809 | 48.2358 | 2.8401 | 0.89018 | 110 | 96.6018 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.3432 | 56.7809
CID=-1714464581 | -6 | 27.5 | 61.9506 | 4 | 21.5 | 4.3 | 1.7436 | 148.523 | 11.416 | 229.5813 | 422.1916 | 398.5385 | 32966.0328 | 1.4629 | 0.025238 | 3.9899 | 61.9507 | 247.1751 | -6 | 27.5 | 4 | 21.5 | 234.2779 | 716.3449 | 50.9277 | 3.0577 | 0.89631 | 110 | 105.0131 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.3062 | 62.1448
CID=-1714464740 | -6 | 30 | 69.6936 | 4 | 24 | 4.8 | 1.7436 | 148.523 | 11.416 | 233.1226 | 423.758 | 398.5385 | 33968.2424 | 1.5501 | 0.028404 | 3.679 | 69.6936 | 256.4031 | -6 | 30 | 4 | 24 | 234.2779 | 770.1963 | 54.2928 | 3.2875 | 0.90302 | 110 | 117.2605 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.4924 | 69.9107
CID=-1714465147 | -6 | 32.5 | 77.0155 | 4 | 26.5 | 5.3 | 1.7436 | 148.523 | 11.416 | 236.688 | 425.298 | 398.5385 | 34874.9016 | 1.6352 | 0.031569 | 3.4365 | 77.0155 | 264.6632 | -6 | 32.5 | 4 | 26.5 | 234.2779 | 827.0396 | 57.2128 | 3.5302 | 0.90761 | 110 | 128.9249 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2611 | 77.2504
CID=-1714465050 | -6 | 35 | 82.2076 | 4 | 29 | 5.8 | 1.7436 | 148.523 | 11.416 | 240.2788 | 426.8116 | 398.5385 | 35504.9846 | 1.6924 | 0.034127 | 3.2581 | 82.2076 | 267.8374 | -6 | 35 | 4 | 29 | 234.2779 | 886.981 | 59.5388 | 3.786 | 0.91009 | 110 | 137.2416 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.2819 | 82.4485
CID=94054754 | -6 | 37.5 | 82.7332 | 4 | 31.5 | 6.3 | 1.7436 | 148.523 | 11.416 | 243.8959 | 428.2991 | 398.5385 | 35617.7725 | 1.6913 | 0.035116 | 3.1613 | 82.7332 | 261.5464 | -6 | 37.5 | 4 | 31.5 | 234.2779 | 950.1287 | 60.8697 | 4.0556 | 0.91031 | 110 | 138.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.1102 | 82.9524
CID=94054851 | -6 | 40 | 82.3197 | 4 | 34 | 6.8 | 1.7436 | 148.523 | 11.416 | 247.5407 | 429.7609 | 398.5385 | 35623.0689 | 1.6659 | 0.03581 | 3.0557 | 82.3198 | 251.5452 | -6 | 40 | 4 | 34 | 234.2779 | 1016.593 | 62.3712 | 4.3393 | 0.91013 | 110 | 137.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.5036 | 82.5148
CID=94054948 | -6 | 42.5 | 81.1792 | 4 | 36.5 | 7.3 | 1.7436 | 148.523 | 11.416 | 251.2145 | 431.197 | 398.5385 | 35584.9186 | 1.6397 | 0.036268 | 2.9756 | 81.1792 | 241.5606 | -6 | 42.5 | 4 | 36.5 | 234.2779 | 1086.4865 | 63.5724 | 4.6376 | 0.90964 | 110 | 135.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.8837 | 81.3364
CID=94054789 | -6 | 45 | 82.4081 | 4 | 39 | 7.8 | 1.7436 | 148.523 | 11.416 | 254.9187 | 432.6077 | 398.5385 | 35816.1862 | 1.6368 | 0.037684 | 2.8525 | 82.4081 | 235.0717 | -6 | 45 | 4 | 39 | 234.2779 | 1159.9242 | 65.4557 | 4.9511 | 0.91017 | 110 | 137.5634 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8436 | 56.269 | 82.5395
CID=94054878 | -6 | 47.5 | 82.8415 | 4 | 41.5 | 8.3 | 1.7436 | 148.523 | 11.416 | 258.655 | 433.9933 | 398.5385 | 35983.0692 | 1.6107 | 0.038865 | 2.7198 | 82.8415 | 225.3105 | -6 | 47.5 | 4 | 41.5 | 234.2779 | 1237.0237 | 67.5669 | 5.2802 | 0.91035 | 110 | 138.2593 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8103 | 63.1967 | 82.9402
CID=94054975 | -6 | 50 | 82.2842 | 4 | 44 | 8.8 | 1.7436 | 148.523 | 11.416 | 262.425 | 435.3541 | 398.5385 | 35722.2242 | 1.1082 | 0.036298 | 2.0381 | 74.0091 | 150.8396 | -6 | 50 | 4 | 44 | 234.2779 | 1317.9055 | 81.0313 | 5.6254 | 0.90589 | 95.8314 | 124.1262 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 73.7545 | 82.3271
CID=94055072 | -6 | 52.5 | 79.3293 | 4 | 46.5 | 9.3 | 1.7436 | 148.523 | 11.416 | 266.2308 | 436.6902 | 398.5385 | 36189.9086 | 1.461 | 0.039595 | 2.437 | 79.3179 | 193.2958 | -6 | 52.5 | 4 | 46.5 | 234.2779 | 1402.6932 | 72.3832 | 5.9873 | 0.90877 | 109.5619 | 132.6085 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 81.6054 | 79.3179
CID=94054913 | -6 | 55 | 0 | 4 | 49 | 9.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94054506 | -6 | 57.5 | 0 | 4 | 51.5 | 10.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94054603 | -6 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605369 | -6 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605272 | -6 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605175 | -6 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605334 | -6 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605245 | -3 | -5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605148 | -3 | -2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605051 | -3 | 0 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605210 | -3 | 2.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605617 | -3 | 5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876605520 | -3 | 7.5 | 0 | 4 | 2 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553616084 | -3 | 10 | 16.9813 | 4 | 4 | 0.8 | 1.7418 | 148.5658 | 12.7186 | 205.396 | 409.9411 | 400.3675 | 22773.0055 | 0.8116 | 0.0090531 | 9.3185 | 16.9813 | 158.2398 | -3 | 10 | 4 | 4 | 262.283 | 414.6075 | 25.6566 | 1.5808 | 0.75618 | 110 | 34.1193 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.2395 | 17.0303
CID=-1553615987 | -3 | 12.5 | 21.3573 | 4 | 6.5 | 1.3 | 1.7418 | 148.5658 | 12.7186 | 208.7918 | 411.6941 | 400.3675 | 24308.9759 | 0.91348 | 0.010451 | 8.1939 | 21.3573 | 174.9997 | -3 | 12.5 | 4 | 6.5 | 262.283 | 450.3422 | 29.0583 | 1.717 | 0.78428 | 110 | 41.3742 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8059 | 21.4254
CID=-1553615890 | -3 | 15 | 26.3679 | 4 | 9 | 1.8 | 1.7418 | 148.5658 | 12.7186 | 212.2062 | 413.4192 | 400.3675 | 25766.3612 | 1.0224 | 0.012104 | 7.2956 | 26.3679 | 192.3693 | -3 | 15 | 4 | 9 | 262.283 | 488.3739 | 32.3827 | 1.862 | 0.81059 | 110 | 49.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5793 | 26.4523
CID=-1553616049 | -3 | 17.5 | 31.9947 | 4 | 11.5 | 2.3 | 1.7418 | 148.5658 | 12.7186 | 215.6398 | 415.1165 | 400.3675 | 27136.2615 | 1.1293 | 0.014017 | 6.52 | 31.9947 | 208.6045 | -3 | 17.5 | 4 | 11.5 | 262.283 | 528.7968 | 35.8022 | 2.0161 | 0.8341 | 110 | 58.2795 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.3834 | 32.0983
CID=-1553615960 | -3 | 20 | 36.7199 | 4 | 14 | 2.8 | 1.7418 | 148.5658 | 12.7186 | 219.0933 | 416.7863 | 400.3675 | 28165.6923 | 1.2063 | 0.015735 | 5.955 | 36.7199 | 218.6659 | -3 | 20 | 4 | 14 | 262.283 | 571.7069 | 38.7626 | 2.1797 | 0.8499 | 110 | 65.6435 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.1276 | 36.8384
CID=-1553615863 | -3 | 22.5 | 43.4124 | 4 | 16.5 | 3.3 | 1.7418 | 148.5658 | 12.7186 | 222.5675 | 418.4287 | 400.3675 | 29421.7314 | 1.3093 | 0.018143 | 5.3623 | 43.4124 | 232.7907 | -3 | 22.5 | 4 | 16.5 | 262.283 | 617.2019 | 42.3076 | 2.3532 | 0.86743 | 110 | 76.0391 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.3536 | 43.5534
CID=-1553615766 | -3 | 25 | 50.8858 | 4 | 19 | 3.8 | 1.7418 | 148.5658 | 12.7186 | 226.0633 | 420.0439 | 400.3675 | 30658.7615 | 1.4102 | 0.020906 | 4.8305 | 50.8858 | 245.8018 | -3 | 25 | 4 | 19 | 262.283 | 665.3809 | 46.0264 | 2.5369 | 0.88188 | 110 | 87.6688 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.2962 | 51.0495
CID=-1553615925 | -3 | 27.5 | 58.6876 | 4 | 21.5 | 4.3 | 1.7418 | 148.5658 | 12.7186 | 229.5813 | 421.6322 | 400.3675 | 31757.2543 | 1.509 | 0.023896 | 4.3915 | 58.6876 | 257.7241 | -3 | 27.5 | 4 | 21.5 | 262.283 | 716.3449 | 49.6087 | 2.7312 | 0.89274 | 110 | 99.8796 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.9887 | 58.877
CID=-1553616332 | -3 | 30 | 65.2507 | 4 | 24 | 4.8 | 1.7418 | 148.5658 | 12.7186 | 233.1226 | 423.1938 | 400.3675 | 32559.3982 | 1.5861 | 0.026603 | 4.0655 | 65.2507 | 265.2741 | -3 | 30 | 4 | 24 | 262.283 | 770.1963 | 52.6547 | 2.9365 | 0.89944 | 110 | 110.2217 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0589 | 65.4577
CID=-1553616235 | -3 | 32.5 | 72.7252 | 4 | 26.5 | 5.3 | 1.7418 | 148.5658 | 12.7186 | 236.688 | 424.7289 | 400.3675 | 33387.3469 | 1.6733 | 0.029745 | 3.7661 | 72.7253 | 273.8878 | -3 | 32.5 | 4 | 26.5 | 262.283 | 827.0396 | 55.7688 | 3.1532 | 0.90509 | 110 | 122.0808 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.3282 | 72.9534
CID=-1746414319 | -3 | 35 | 81.0365 | 4 | 29 | 5.8 | 1.7418 | 148.5658 | 12.7186 | 240.2788 | 426.2376 | 400.3675 | 34377.2968 | 1.766 | 0.033326 | 3.4888 | 81.0365 | 282.7178 | -3 | 35 | 4 | 29 | 262.283 | 886.981 | 58.9688 | 3.3818 | 0.90957 | 110 | 135.3627 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.2318 | 81.2868
CID=-1746414222 | -3 | 37.5 | 88.9876 | 4 | 31.5 | 6.3 | 1.7418 | 148.5658 | 12.7186 | 243.8959 | 427.7203 | 400.3675 | 35212.5558 | 1.8577 | 0.03695 | 3.2665 | 88.9876 | 290.6762 | -3 | 37.5 | 4 | 31.5 | 262.283 | 950.1287 | 61.8017 | 3.6225 | 0.91259 | 110 | 148.1523 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.4207 | 89.2568
CID=-1746414125 | -3 | 40 | 91.4015 | 4 | 34 | 6.8 | 1.7418 | 148.5658 | 12.7186 | 247.5407 | 429.1772 | 400.3675 | 35511.3517 | 1.8854 | 0.038719 | 3.1524 | 91.4015 | 288.1342 | -3 | 40 | 4 | 34 | 262.283 | 1016.593 | 63.3777 | 3.8759 | 0.91332 | 110 | 152.0494 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.004 | 91.6597
CID=-1746414284 | -3 | 42.5 | 91.7797 | 4 | 36.5 | 7.3 | 1.7418 | 148.5658 | 12.7186 | 251.2145 | 430.6085 | 400.3675 | 35600.015 | 1.882 | 0.039815 | 3.0584 | 91.7797 | 280.7036 | -3 | 42.5 | 4 | 36.5 | 262.283 | 1086.4865 | 64.7389 | 4.1424 | 0.91343 | 110 | 152.6606 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8883 | 44.8066 | 92.0158
CID=-1746414195 | -3 | 45 | 91.674 | 4 | 39 | 7.8 | 1.7418 | 148.5658 | 12.7186 | 254.9187 | 432.0144 | 400.3675 | 35644.784 | 1.8553 | 0.040788 | 2.9436 | 91.674 | 269.8536 | -3 | 45 | 4 | 39 | 262.283 | 1159.9242 | 66.4398 | 4.4224 | 0.9134 | 110 | 152.4898 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.0122 | 91.8833
CID=-1746414098 | -3 | 47.5 | 90.9227 | 4 | 41.5 | 8.3 | 1.7418 | 148.5658 | 12.7186 | 258.655 | 433.3951 | 400.3675 | 35669.6908 | 1.8262 | 0.041566 | 2.8463 | 90.9227 | 258.7961 | -3 | 47.5 | 4 | 41.5 | 262.283 | 1237.0237 | 67.9587 | 4.7164 | 0.91318 | 110 | 151.276 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57.2677 | 91.0918
CID=-1746414001 | -3 | 50 | 92.2354 | 4 | 44 | 8.8 | 1.7418 | 148.5658 | 12.7186 | 262.425 | 434.7511 | 400.3675 | 35884.268 | 1.8229 | 0.043236 | 2.7263 | 92.2354 | 251.4571 | -3 | 50 | 4 | 44 | 262.283 | 1317.9055 | 69.8835 | 5.0247 | 0.91356 | 110 | 153.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 4.839 | 64.1843 | 92.3763
CID=-1746414160 | -3 | 52.5 | 92.6448 | 4 | 46.5 | 9.3 | 1.7418 | 148.5658 | 12.7186 | 266.2308 | 436.0824 | 400.3675 | 36047.8704 | 1.7937 | 0.044634 | 2.5971 | 92.6448 | 240.6067 | -3 | 52.5 | 4 | 46.5 | 262.283 | 1402.6932 | 72.0291 | 5.348 | 0.91367 | 110 | 154.059 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8051 | 72.1709 | 92.7477
CID=-1746414567 | -3 | 55 | 91.987 | 4 | 49 | 9.8 | 1.7418 | 148.5658 | 12.7186 | 270.0745 | 437.3893 | 400.3675 | 35839.1471 | 1.2333 | 0.042163 | 1.9162 | 83.8581 | 160.6883 | -3 | 55 | 4 | 49 | 262.283 | 1491.5141 | 86.0361 | 5.6867 | 0.91076 | 95.4659 | 139.8926 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 83.791 | 92.0281
CID=-1746414470 | -3 | 57.5 | 88.5623 | 4 | 51.5 | 10.3 | 1.7418 | 148.5658 | 12.7186 | 273.9586 | 438.6721 | 400.3675 | 36239.4688 | 1.6267 | 0.045541 | 2.3224 | 88.544 | 205.6311 | -3 | 57.5 | 4 | 51.5 | 262.283 | 1584.4992 | 76.8958 | 6.0412 | 0.91245 | 109.5992 | 147.4368 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 92.1977 | 88.544
CID=-1489720443 | -3 | 60 | 0 | 4 | 54 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720412 | -3 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720249 | -3 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720218 | -3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720319 | -3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720288 | 0 | -5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720125 | 0 | -2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720094 | 0 | 0 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720691 | 0 | 2.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489720660 | 0 | 5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682518678 | 0 | 7.5 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682518647 | 0 | 10 | 0 | 4 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682518484 | 0 | 12.5 | 15.4873 | 4 | 6.5 | 1.3 | 1.7401 | 148.5582 | 14.1363 | 208.7918 | 411.2041 | 402.1796 | 21607.354 | 0.81628 | 0.0087156 | 10.1927 | 15.4873 | 157.858 | 0 | 12.5 | 4 | 6.5 | 292.8032 | 450.3422 | 26.4848 | 1.538 | 0.74531 | 110 | 31.5713 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.6527 | 15.5267
CID=-1682518453 | 0 | 15 | 21.8962 | 4 | 9 | 1.8 | 1.7401 | 148.5582 | 14.1363 | 212.2062 | 412.9246 | 402.1796 | 23788.7335 | 0.97473 | 0.010694 | 8.4568 | 21.8962 | 185.1726 | 0 | 15 | 4 | 9 | 292.8032 | 488.3739 | 30.9888 | 1.6679 | 0.78739 | 110 | 42.2508 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 7.8476 | 21.9668
CID=-1682518554 | 0 | 17.5 | 27.1318 | 4 | 11.5 | 2.3 | 1.7401 | 148.5582 | 14.1363 | 215.6398 | 414.6172 | 402.1796 | 25255.0179 | 1.0936 | 0.012436 | 7.5186 | 27.1318 | 203.993 | 0 | 17.5 | 4 | 11.5 | 292.8032 | 528.7968 | 34.2584 | 1.806 | 0.81412 | 110 | 50.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.6303 | 27.2198
CID=-1682518523 | 0 | 20 | 33.0145 | 4 | 14 | 2.8 | 1.7401 | 148.5582 | 14.1363 | 219.0933 | 416.2824 | 402.1796 | 26625.9516 | 1.2102 | 0.014452 | 6.7112 | 33.0145 | 221.5658 | 0 | 20 | 4 | 14 | 292.8032 | 571.7069 | 37.6182 | 1.9525 | 0.83779 | 110 | 59.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.4976 | 33.1226
CID=-1682518360 | 0 | 22.5 | 39.5186 | 4 | 16.5 | 3.3 | 1.7401 | 148.5582 | 14.1363 | 222.5675 | 417.9202 | 402.1796 | 27918.7985 | 1.3246 | 0.01675 | 6.0205 | 39.5186 | 237.9209 | 0 | 22.5 | 4 | 16.5 | 292.8032 | 617.2019 | 41.0323 | 2.1079 | 0.85784 | 110 | 69.9921 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.7099 | 39.6483
CID=-1682518329 | 0 | 25 | 44.8439 | 4 | 19 | 3.8 | 1.7401 | 148.5582 | 14.1363 | 226.0633 | 419.5308 | 402.1796 | 28890.5086 | 1.406 | 0.018771 | 5.5218 | 44.8439 | 247.6201 | 0 | 25 | 4 | 19 | 292.8032 | 665.3809 | 43.9517 | 2.2725 | 0.87056 | 110 | 78.2632 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.0491 | 44.9885
CID=-1682518926 | 0 | 27.5 | 52.5946 | 4 | 21.5 | 4.3 | 1.7401 | 148.5582 | 14.1363 | 229.5813 | 421.1145 | 402.1796 | 30099.2482 | 1.5161 | 0.021667 | 4.9755 | 52.5946 | 261.6847 | 0 | 27.5 | 4 | 21.5 | 292.8032 | 716.3449 | 47.5593 | 2.4465 | 0.88458 | 110 | 90.3361 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.7183 | 52.7648
CID=-1682518895 | 0 | 30 | 60.7465 | 4 | 24 | 4.8 | 1.7401 | 148.5582 | 14.1363 | 233.1226 | 422.6716 | 402.1796 | 31208.4706 | 1.6239 | 0.024823 | 4.5194 | 60.7464 | 274.5371 | 0 | 30 | 4 | 24 | 292.8032 | 770.1963 | 51.0749 | 2.6304 | 0.89505 | 110 | 103.1167 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.6284 | 60.943
CID=126000975 | 0 | 32.5 | 69.6495 | 4 | 26.5 | 5.3 | 1.7401 | 148.5582 | 14.1363 | 236.688 | 424.2021 | 402.1796 | 32254.1855 | 1.7295 | 0.028376 | 4.1093 | 69.6495 | 286.2115 | 0 | 32.5 | 4 | 26.5 | 292.8032 | 827.0396 | 54.706 | 2.8246 | 0.90299 | 110 | 117.1905 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.9262 | 69.8742
CID=126001006 | 0 | 35 | 75.764 | 4 | 29 | 5.8 | 1.7401 | 148.5582 | 14.1363 | 240.2788 | 425.7063 | 402.1796 | 32896.2156 | 1.8023 | 0.031125 | 3.8513 | 75.764 | 291.792 | 0 | 35 | 4 | 29 | 292.8032 | 886.981 | 57.331 | 3.0293 | 0.90692 | 110 | 126.9258 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2143 | 76.0029
CID=126001169 | 0 | 37.5 | 84.7338 | 4 | 31.5 | 6.3 | 1.7401 | 148.5582 | 14.1363 | 243.8959 | 427.1845 | 402.1796 | 33825.979 | 1.9039 | 0.035018 | 3.5564 | 84.7338 | 301.3505 | 0 | 37.5 | 4 | 31.5 | 292.8032 | 950.1287 | 60.5892 | 3.2449 | 0.91111 | 110 | 141.3004 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0433 | 84.9985
CID=126001200 | 0 | 40 | 93.2405 | 4 | 34 | 6.8 | 1.7401 | 148.5582 | 14.1363 | 247.5407 | 428.6369 | 402.1796 | 34707.7457 | 2.003 | 0.038933 | 3.3219 | 93.2405 | 309.7351 | 0 | 40 | 4 | 34 | 292.8032 | 1016.593 | 63.4716 | 3.4719 | 0.91383 | 110 | 155.0224 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.5584 | 93.5253
CID=126001099 | 0 | 42.5 | 101.6001 | 4 | 36.5 | 7.3 | 1.7401 | 148.5582 | 14.1363 | 251.2145 | 430.0637 | 402.1796 | 35479.6382 | 2.0954 | 0.042992 | 3.1134 | 101.6001 | 316.3261 | 0 | 42.5 | 4 | 36.5 | 292.8032 | 1086.4865 | 66.2617 | 3.7106 | 0.91569 | 110 | 168.5776 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.6283 | 101.9065
CID=126001130 | 0 | 45 | 101.6357 | 4 | 39 | 7.8 | 1.7401 | 148.5582 | 14.1363 | 254.9187 | 431.4651 | 402.1796 | 35538.216 | 2.0941 | 0.044087 | 3.0342 | 101.6357 | 308.3819 | 0 | 45 | 4 | 39 | 292.8032 | 1159.9242 | 67.4472 | 3.9614 | 0.9157 | 110 | 168.6354 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.0942 | 101.9148
CID=126001293 | 0 | 47.5 | 100.9957 | 4 | 41.5 | 8.3 | 1.7401 | 148.5582 | 14.1363 | 258.655 | 432.8414 | 402.1796 | 35556.4124 | 2.0621 | 0.044984 | 2.9304 | 100.9957 | 295.9624 | 0 | 47.5 | 4 | 41.5 | 292.8032 | 1237.0237 | 69.0097 | 4.2248 | 0.91558 | 110 | 167.5955 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.0502 | 101.2467
CID=126001324 | 0 | 50 | 101.9135 | 4 | 44 | 8.8 | 1.7401 | 148.5582 | 14.1363 | 262.425 | 434.1928 | 402.1796 | 35669.1823 | 2.0606 | 0.046566 | 2.8257 | 101.9135 | 287.9783 | 0 | 50 | 4 | 44 | 292.8032 | 1317.9055 | 70.6547 | 4.501 | 0.91575 | 110 | 169.087 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 57.491 | 102.1367
CID=126000727 | 0 | 52.5 | 101.4833 | 4 | 46.5 | 9.3 | 1.7401 | 148.5582 | 14.1363 | 266.2308 | 435.5196 | 402.1796 | 35734.7217 | 2.0283 | 0.047692 | 2.7171 | 101.4833 | 275.7417 | 0 | 52.5 | 4 | 46.5 | 292.8032 | 1402.6932 | 72.4139 | 4.7906 | 0.91567 | 110 | 168.3878 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.2952 | 101.6651
CID=126000758 | 0 | 55 | 101.8924 | 4 | 49 | 9.8 | 1.7401 | 148.5582 | 14.1363 | 270.0745 | 436.822 | 402.1796 | 35882.632 | 1.9957 | 0.049254 | 2.5875 | 101.8924 | 263.6461 | 0 | 55 | 4 | 49 | 292.8032 | 1491.5141 | 74.565 | 5.0939 | 0.91575 | 110 | 169.0527 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.7779 | 102.0387
CID=-1844659148 | 0 | 57.5 | 102.4377 | 4 | 51.5 | 10.3 | 1.7401 | 148.5582 | 14.1363 | 273.9586 | 438.1003 | 402.1796 | 36053.7595 | 1.9632 | 0.050985 | 2.4573 | 102.4377 | 251.7221 | 0 | 57.5 | 4 | 51.5 | 292.8032 | 1584.4992 | 76.8259 | 5.4115 | 0.91585 | 110 | 169.9391 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82.0777 | 102.54
CID=-1844659117 | 0 | 60 | 100.8519 | 4 | 54 | 10.8 | 1.7401 | 148.5582 | 14.1363 | 277.8855 | 439.3549 | 402.1796 | 35914.8119 | 1.3827 | 0.048861 | 1.8249 | 94.1757 | 171.8647 | 0 | 60 | 4 | 54 | 292.8032 | 1681.7842 | 90.2399 | 5.7437 | 0.91407 | 95.3496 | 156.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 94.1756 | 100.8854
CID=-1844658954 | 0 | 62.5 | 0 | 4 | 56.5 | 11.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844658923 | 0 | 65 | 0 | 4 | 59 | 11.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844659024 | 0 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844658993 | 0 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844658830 | 3 | -5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844658799 | 3 | -2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844659396 | 3 | 0 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844659365 | 3 | 2.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521669863 | 3 | 5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521669832 | 3 | 7.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521669669 | 3 | 10 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521669638 | 3 | 12.5 | 0 | 4 | 8 | 1.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521669739 | 3 | 15 | 11.1517 | 4 | 9 | 1.8 | 1.7385 | 148.4988 | 15.6766 | 212.2062 | 412.4664 | 403.9734 | 19834.9342 | 0.70008 | 0.0076266 | 12.0387 | 11.1517 | 134.2521 | 3 | 15 | 4 | 9 | 325.9849 | 488.3739 | 26.0529 | 1.4981 | 0.70951 | 87.9149 | 23.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8.4251 | 11.1654
CID=-1521669708 | 3 | 17.5 | 22.3359 | 4 | 11.5 | 2.3 | 1.7385 | 148.4988 | 15.6766 | 215.6398 | 414.1547 | 403.9734 | 23264.5624 | 1.0377 | 0.010915 | 8.75 | 22.3359 | 195.439 | 3 | 17.5 | 4 | 11.5 | 325.9849 | 528.7968 | 32.8974 | 1.6222 | 0.78987 | 110 | 42.9637 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 8.626 | 22.4048
CID=-1521669545 | 3 | 20 | 27.8779 | 4 | 14 | 2.8 | 1.7385 | 148.4988 | 15.6766 | 219.0933 | 415.8156 | 403.9734 | 24750.7948 | 1.167 | 0.01277 | 7.7392 | 27.8779 | 215.754 | 3 | 20 | 4 | 14 | 325.9849 | 571.7069 | 36.1941 | 1.7538 | 0.81747 | 110 | 51.814 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.0707 | 27.9674
CID=-1521669514 | 3 | 22.5 | 33.9725 | 4 | 16.5 | 3.3 | 1.7385 | 148.4988 | 15.6766 | 222.5675 | 417.4491 | 403.9734 | 26116.9269 | 1.2941 | 0.01488 | 6.9101 | 33.9725 | 234.7541 | 3 | 22.5 | 4 | 16.5 | 325.9849 | 617.2019 | 39.4622 | 1.8933 | 0.8411 | 110 | 61.3669 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.1238 | 34.0823
CID=-1521670111 | 3 | 25 | 40.7205 | 4 | 19 | 3.8 | 1.7385 | 148.4988 | 15.6766 | 226.0633 | 419.0555 | 403.9734 | 27399.3429 | 1.4186 | 0.017287 | 6.1979 | 40.7205 | 252.3816 | 3 | 25 | 4 | 19 | 325.9849 | 665.3809 | 42.7935 | 2.0411 | 0.86097 | 110 | 71.8585 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0916 | 40.8543
CID=-1521670080 | 3 | 27.5 | 46.2319 | 4 | 21.5 | 4.3 | 1.7385 | 148.4988 | 15.6766 | 229.5813 | 420.635 | 403.9734 | 28352.6446 | 1.5065 | 0.019402 | 5.6826 | 46.2318 | 262.719 | 3 | 27.5 | 4 | 21.5 | 325.9849 | 716.3449 | 45.6602 | 2.1975 | 0.87343 | 110 | 80.421 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.1927 | 46.3828
CID=-1714468098 | 3 | 30 | 54.1717 | 4 | 24 | 4.8 | 1.7385 | 148.4988 | 15.6766 | 233.1226 | 422.1878 | 403.9734 | 29539.4966 | 1.6265 | 0.022406 | 5.1298 | 54.1717 | 277.8878 | 3 | 30 | 4 | 24 | 325.9849 | 770.1963 | 49.1176 | 2.3627 | 0.8869 | 110 | 92.8013 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.1571 | 54.3477
CID=-1714468067 | 3 | 32.5 | 62.921 | 4 | 26.5 | 5.3 | 1.7385 | 148.4988 | 15.6766 | 236.688 | 423.7141 | 403.9734 | 30705.9925 | 1.7438 | 0.025815 | 4.6362 | 62.921 | 291.712 | 3 | 32.5 | 4 | 26.5 | 325.9849 | 827.0396 | 52.7022 | 2.537 | 0.89728 | 110 | 106.5429 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.4325 | 63.1245
CID=-1714467904 | 3 | 35 | 72.0145 | 4 | 29 | 5.8 | 1.7385 | 148.4988 | 15.6766 | 240.2788 | 425.2142 | 403.9734 | 31739.7808 | 1.8587 | 0.029498 | 4.225 | 72.0145 | 304.2638 | 3 | 35 | 4 | 29 | 325.9849 | 886.981 | 56.1656 | 2.7209 | 0.90463 | 110 | 120.9494 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.6165 | 72.2476
CID=-1714467873 | 3 | 37.5 | 80.0801 | 4 | 31.5 | 6.3 | 1.7385 | 148.4988 | 15.6766 | 243.8959 | 426.6882 | 403.9734 | 32539.017 | 1.9539 | 0.032993 | 3.9058 | 80.0802 | 312.7751 | 3 | 37.5 | 4 | 31.5 | 325.9849 | 950.1287 | 59.241 | 2.9146 | 0.90914 | 110 | 133.8296 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.0856 | 80.3364
CID=-1714467974 | 3 | 40 | 88.1369 | 4 | 34 | 6.8 | 1.7385 | 148.4988 | 15.6766 | 247.5407 | 428.1364 | 403.9734 | 33262.2349 | 2.0476 | 0.036654 | 3.6342 | 88.137 | 320.3057 | 3 | 40 | 4 | 34 | 325.9849 | 1016.593 | 62.1568 | 3.1185 | 0.91232 | 110 | 146.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.953 | 88.4142
CID=-1714467943 | 3 | 42.5 | 97.9893 | 4 | 36.5 | 7.3 | 1.7385 | 148.4988 | 15.6766 | 251.2145 | 429.559 | 403.9734 | 34209.5101 | 2.1556 | 0.041159 | 3.3605 | 97.9893 | 329.2888 | 3 | 42.5 | 4 | 36.5 | 325.9849 | 1086.4865 | 65.379 | 3.3329 | 0.91497 | 110 | 162.715 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 37.6354 | 98.2926
CID=-1714467780 | 3 | 45 | 107.0201 | 4 | 39 | 7.8 | 1.7385 | 148.4988 | 15.6766 | 254.9187 | 430.9562 | 403.9734 | 34999.359 | 2.2613 | 0.045586 | 3.1495 | 107.0201 | 337.0571 | 3 | 45 | 4 | 39 | 325.9849 | 1159.9242 | 68.1356 | 3.5582 | 0.91659 | 110 | 177.3972 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.9298 | 107.3472
CID=-1714467749 | 3 | 47.5 | 112.4846 | 4 | 41.5 | 8.3 | 1.7385 | 148.4988 | 15.6766 | 258.655 | 432.3283 | 403.9734 | 35498.5694 | 2.3216 | 0.048871 | 2.9993 | 112.4846 | 337.3768 | 3 | 47.5 | 4 | 41.5 | 325.9849 | 1237.0237 | 70.2722 | 3.7947 | 0.9173 | 110 | 186.31 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.1667 | 112.8128
CID=-1714468346 | 3 | 50 | 113.1833 | 4 | 44 | 8.8 | 1.7385 | 148.4988 | 15.6766 | 262.425 | 433.6755 | 403.9734 | 35605.0126 | 2.3199 | 0.05045 | 2.9013 | 113.1832 | 328.3758 | 3 | 50 | 4 | 44 | 325.9849 | 1317.9055 | 71.7829 | 4.0428 | 0.91738 | 110 | 187.4507 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1496 | 113.4849
CID=-1714468315 | 3 | 52.5 | 112.3437 | 4 | 46.5 | 9.3 | 1.7385 | 148.4988 | 15.6766 | 266.2308 | 434.9982 | 403.9734 | 35591.3726 | 2.2846 | 0.051502 | 2.8012 | 112.3436 | 314.6916 | 3 | 52.5 | 4 | 46.5 | 325.9849 | 1402.6932 | 73.3744 | 4.3029 | 0.91729 | 110 | 186.0798 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.3888 | 112.6148
CID=94051555 | 3 | 55 | 112.0753 | 4 | 49 | 9.8 | 1.7385 | 148.4988 | 15.6766 | 270.0745 | 436.2964 | 403.9734 | 35614.2418 | 2.2802 | 0.052867 | 2.7242 | 112.0753 | 305.318 | 3 | 55 | 4 | 49 | 325.9849 | 1491.5141 | 74.6984 | 4.5754 | 0.91726 | 110 | 185.6416 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8717 | 65.8924 | 112.3073
CID=94051586 | 3 | 57.5 | 112.8514 | 4 | 51.5 | 10.3 | 1.7385 | 148.4988 | 15.6766 | 273.9586 | 437.5705 | 403.9734 | 35779.5492 | 2.2466 | 0.054782 | 2.5883 | 112.8514 | 292.0881 | 3 | 57.5 | 4 | 51.5 | 325.9849 | 1584.4992 | 76.9313 | 4.8607 | 0.91735 | 110 | 186.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 73.9935 | 113.0467
CID=94051749 | 3 | 60 | 113.2334 | 4 | 54 | 10.8 | 1.7385 | 148.4988 | 15.6766 | 277.8855 | 438.8208 | 403.9734 | 35918.3906 | 2.2104 | 0.056659 | 2.4613 | 113.2334 | 278.6983 | 3 | 60 | 4 | 54 | 325.9849 | 1681.7842 | 79.1279 | 5.1591 | 0.91739 | 110 | 187.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 82.0539 | 113.39
CID=94051780 | 3 | 62.5 | 113.7591 | 4 | 56.5 | 11.3 | 1.7385 | 148.4988 | 15.6766 | 281.8586 | 440.0476 | 403.9734 | 36081.0168 | 2.1741 | 0.058744 | 2.3338 | 113.759 | 265.4904 | 3 | 62.5 | 4 | 56.5 | 325.9849 | 1783.5096 | 81.4301 | 5.4711 | 0.91745 | 110 | 188.3912 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 92.802 | 113.8644
CID=94051679 | 3 | 65 | 111.9377 | 4 | 59 | 11.8 | 1.7385 | 148.4988 | 15.6766 | 285.881 | 441.2512 | 403.9734 | 36148.2456 | 2.1016 | 0.059878 | 2.2172 | 111.9377 | 248.1833 | 3 | 65 | 4 | 59 | 325.9849 | 1889.8218 | 83.6391 | 5.7973 | 0.91724 | 110 | 185.4171 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 105.0584 | 111.9723
CID=94051710 | 3 | 67.5 | 0 | 4 | 61.5 | 12.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94051873 | 3 | 69.99 | 0 | 4 | 63.99 | 12.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94051904 | 6 | -5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94051307 | 6 | -2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94051338 | 6 | 0 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608568 | 6 | 2.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608537 | 6 | 5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608374 | 6 | 7.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608343 | 6 | 10 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608444 | 6 | 12.5 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608413 | 6 | 15 | 0 | 4 | 11 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608250 | 6 | 17.5 | 0 | 4 | 11.5 | 2.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876608219 | 6 | 20 | 22.7919 | 4 | 14 | 2.8 | 1.7371 | 148.3861 | 17.3476 | 219.0933 | 415.3827 | 405.7474 | 22760.2946 | 1.1068 | 0.011147 | 9.0645 | 22.7919 | 206.5969 | 6 | 20 | 4 | 14 | 361.9781 | 571.7069 | 34.8193 | 1.5794 | 0.7924 | 110 | 43.701 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.5417 | 22.8585
CID=-1876608816 | 6 | 22.5 | 28.5814 | 4 | 16.5 | 3.3 | 1.7371 | 148.3861 | 17.3476 | 222.5675 | 417.0123 | 405.7474 | 24248.8166 | 1.2426 | 0.013102 | 7.9636 | 28.5814 | 227.6108 | 6 | 22.5 | 4 | 16.5 | 361.9781 | 617.2019 | 38.1662 | 1.7051 | 0.82052 | 110 | 52.9236 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.1644 | 28.6739
CID=-1876608785 | 6 | 25 | 34.8721 | 4 | 19 | 3.8 | 1.7371 | 148.3861 | 17.3476 | 226.0633 | 418.6147 | 405.7474 | 25608.3396 | 1.3806 | 0.015301 | 7.1136 | 34.8721 | 248.0657 | 6 | 25 | 4 | 19 | 361.9781 | 665.3809 | 41.3456 | 1.8382 | 0.8441 | 110 | 62.7684 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3537 | 34.9853
CID=-1553619283 | 6 | 27.5 | 41.8888 | 4 | 21.5 | 4.3 | 1.7371 | 148.3861 | 17.3476 | 229.5813 | 420.1903 | 405.7474 | 26888.917 | 1.5159 | 0.017829 | 6.3753 | 41.8888 | 267.0559 | 6 | 27.5 | 4 | 21.5 | 361.9781 | 716.3449 | 44.6157 | 1.979 | 0.86387 | 110 | 73.6728 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.739 | 42.0253
CID=-1553619252 | 6 | 30 | 48.9853 | 4 | 24 | 4.8 | 1.7371 | 148.3861 | 17.3476 | 233.1226 | 421.7392 | 405.7474 | 28020.6392 | 1.6368 | 0.020493 | 5.768 | 48.9853 | 282.5494 | 6 | 30 | 4 | 24 | 361.9781 | 770.1963 | 47.7961 | 2.1277 | 0.87863 | 110 | 84.7064 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.1012 | 49.1455
CID=-1553619089 | 6 | 32.5 | 55.7854 | 4 | 26.5 | 5.3 | 1.7371 | 148.3861 | 17.3476 | 236.688 | 423.2616 | 405.7474 | 29007.7647 | 1.741 | 0.023178 | 5.2762 | 55.7854 | 294.3369 | 6 | 32.5 | 4 | 26.5 | 361.9781 | 827.0396 | 50.7997 | 2.2848 | 0.88912 | 110 | 95.3272 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7427 | 55.9665
CID=-1553619058 | 6 | 35 | 64.8895 | 4 | 29 | 5.8 | 1.7371 | 148.3861 | 17.3476 | 240.2788 | 424.7577 | 405.7474 | 30154.5055 | 1.8687 | 0.026766 | 4.7651 | 64.8894 | 309.206 | 6 | 35 | 4 | 29 | 361.9781 | 886.981 | 54.3152 | 2.4504 | 0.89912 | 110 | 109.6507 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.991 | 65.1
CID=-1553619159 | 6 | 37.5 | 74.3393 | 4 | 31.5 | 6.3 | 1.7371 | 148.3861 | 17.3476 | 243.8959 | 426.2278 | 405.7474 | 31196.5257 | 1.9935 | 0.03064 | 4.3402 | 74.3393 | 322.6468 | 6 | 37.5 | 4 | 31.5 | 361.9781 | 950.1287 | 57.712 | 2.6248 | 0.90609 | 110 | 124.6525 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.3835 | 74.5803
CID=-1553619128 | 6 | 40 | 84.6476 | 4 | 34 | 6.8 | 1.7371 | 148.3861 | 17.3476 | 247.5407 | 427.6721 | 405.7474 | 32186.4312 | 2.1156 | 0.035004 | 3.954 | 84.6476 | 334.6982 | 6 | 40 | 4 | 34 | 361.9781 | 1016.593 | 61.2303 | 2.8084 | 0.91107 | 110 | 141.1619 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.2032 | 84.9212
CID=-1553618965 | 6 | 42.5 | 91.5495 | 4 | 36.5 | 7.3 | 1.7371 | 148.3861 | 17.3476 | 251.2145 | 429.0909 | 405.7474 | 32784.7628 | 2.1976 | 0.038345 | 3.7096 | 91.5495 | 339.609 | 6 | 42.5 | 4 | 36.5 | 361.9781 | 1086.4865 | 63.8083 | 3.0015 | 0.91337 | 110 | 152.2885 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7881 | 91.8398
CID=-1553618934 | 6 | 45 | 101.8254 | 4 | 39 | 7.8 | 1.7371 | 148.3861 | 17.3476 | 254.9187 | 430.4842 | 405.7474 | 33646.8706 | 2.3151 | 0.043114 | 3.4292 | 101.8254 | 349.1779 | 6 | 45 | 4 | 39 | 361.9781 | 1159.9242 | 66.9781 | 3.2044 | 0.91573 | 110 | 168.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.4962 | 102.1436
CID=-1553619531 | 6 | 47.5 | 111.8374 | 4 | 41.5 | 8.3 | 1.7371 | 148.3861 | 17.3476 | 258.655 | 431.8524 | 405.7474 | 34507.5772 | 2.4293 | 0.048034 | 3.1951 | 111.8374 | 357.3313 | 6 | 47.5 | 4 | 41.5 | 361.9781 | 1237.0237 | 69.9161 | 3.4174 | 0.91723 | 110 | 185.2533 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.1636 | 112.1825
CID=-1553619500 | 6 | 50 | 121.8402 | 4 | 44 | 8.8 | 1.7371 | 148.3861 | 17.3476 | 262.425 | 433.1958 | 405.7474 | 35262.558 | 2.542 | 0.05322 | 2.9902 | 121.8402 | 364.3296 | 6 | 50 | 4 | 44 | 361.9781 | 1317.9055 | 72.7254 | 3.6408 | 0.9182 | 110 | 201.6094 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.3056 | 122.2097
CID=-1746417518 | 6 | 52.5 | 123.9093 | 4 | 46.5 | 9.3 | 1.7371 | 148.3861 | 17.3476 | 266.2308 | 434.5145 | 405.7474 | 35468.1341 | 2.5657 | 0.055506 | 2.8888 | 123.9093 | 357.9519 | 6 | 52.5 | 4 | 46.5 | 361.9781 | 1402.6932 | 74.297 | 3.8751 | 0.91835 | 110 | 204.999 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.1646 | 124.2598
CID=-1746417487 | 6 | 55 | 124.3251 | 4 | 49 | 9.8 | 1.7371 | 148.3861 | 17.3476 | 270.0745 | 435.8088 | 405.7474 | 35546.9212 | 2.5609 | 0.057251 | 2.7946 | 124.3251 | 347.4387 | 6 | 55 | 4 | 49 | 361.9781 | 1491.5141 | 75.8242 | 4.1205 | 0.91838 | 110 | 205.6803 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8882 | 60.3101 | 124.6468
CID=-1746417324 | 6 | 57.5 | 124.4688 | 4 | 51.5 | 10.3 | 1.7371 | 148.3861 | 17.3476 | 273.9586 | 437.0791 | 405.7474 | 35603.654 | 2.5245 | 0.058999 | 2.673 | 124.4688 | 332.7057 | 6 | 57.5 | 4 | 51.5 | 361.9781 | 1584.4992 | 77.7897 | 4.3773 | 0.91839 | 110 | 205.9157 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 66.4309 | 124.7604
CID=-1746417293 | 6 | 60 | 123.8914 | 4 | 54 | 10.8 | 1.7371 | 148.3861 | 17.3476 | 277.8855 | 438.3255 | 405.7474 | 35620.7294 | 2.5193 | 0.060557 | 2.6001 | 123.8914 | 322.1281 | 6 | 60 | 4 | 54 | 361.9781 | 1681.7842 | 79.1258 | 4.6461 | 0.91835 | 110 | 204.9696 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8685 | 75.0155 | 124.137
CID=-1746417394 | 6 | 62.5 | 125.0195 | 4 | 56.5 | 11.3 | 1.7371 | 148.3861 | 17.3476 | 281.8586 | 439.5483 | 405.7474 | 35803.3252 | 2.4818 | 0.063011 | 2.4593 | 125.0194 | 307.4662 | 6 | 62.5 | 4 | 56.5 | 361.9781 | 1783.5096 | 81.5119 | 4.9271 | 0.91843 | 110 | 206.8182 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 83.3904 | 125.2286
CID=-1746417363 | 6 | 65 | 125.3692 | 4 | 59 | 11.8 | 1.7371 | 148.3861 | 17.3476 | 285.881 | 440.748 | 405.7474 | 35934.5445 | 2.4416 | 0.06529 | 2.3344 | 125.3692 | 292.6609 | 6 | 65 | 4 | 59 | 361.9781 | 1889.8218 | 83.7586 | 5.2208 | 0.91845 | 110 | 207.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 92.0266 | 125.5368
CID=-1746417200 | 6 | 67.5 | 124.7198 | 4 | 61.5 | 12.3 | 1.7371 | 148.3861 | 17.3476 | 289.9569 | 441.9247 | 405.7474 | 36021.0579 | 2.3989 | 0.067273 | 2.2272 | 124.7198 | 277.7739 | 6 | 67.5 | 4 | 61.5 | 361.9781 | 2000.8736 | 85.8001 | 5.5276 | 0.91841 | 110 | 206.3271 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7805 | 104.302 | 124.8224
CID=-1746417169 | 6 | 69.99 | 123.7836 | 4 | 63.99 | 12.798 | 1.7371 | 148.3861 | 17.3476 | 294.074 | 443.0743 | 405.7474 | 35978.5349 | 1.7308 | 0.065687 | 1.6571 | 116.6407 | 193.2819 | 6 | 69.99 | 4 | 63.99 | 361.9781 | 2116.3519 | 98.2332 | 5.8466 | 0.91774 | 95.3496 | 193.1009 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 116.6406 | 123.8195
CID=-1746417766 | 9 | -5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746417735 | 9 | -2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710718 | 9 | 0 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710621 | 9 | 2.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710656 | 9 | 5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710815 | 9 | 7.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710842 | 9 | 10 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710745 | 9 | 12.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710780 | 9 | 15 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710939 | 9 | 17.5 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710966 | 9 | 20 | 0 | 4 | 14 | 2.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489710869 | 9 | 22.5 | 22.6056 | 4 | 16.5 | 3.3 | 1.7357 | 148.2186 | 19.1581 | 222.5675 | 416.6065 | 407.5003 | 22117.291 | 1.1637 | 0.011196 | 9.5201 | 22.6056 | 215.2074 | 9 | 22.5 | 4 | 16.5 | 400.9358 | 617.2019 | 36.5115 | 1.5394 | 0.79137 | 110 | 43.4 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 9.8546 | 22.6697
CID=-1682508953 | 9 | 25 | 29.2056 | 4 | 19 | 3.8 | 1.7357 | 148.2186 | 19.1581 | 226.0633 | 418.2053 | 407.5003 | 23742.4534 | 1.3199 | 0.013418 | 8.1997 | 29.2056 | 239.478 | 9 | 25 | 4 | 19 | 400.9358 | 665.3809 | 40.1517 | 1.6596 | 0.82316 | 110 | 53.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10.2198 | 29.301
CID=-1682508856 | 9 | 27.5 | 35.7599 | 4 | 21.5 | 4.3 | 1.7357 | 148.2186 | 19.1581 | 229.5813 | 419.7772 | 407.5003 | 25110.0326 | 1.4697 | 0.015731 | 7.3123 | 35.7599 | 261.4881 | 9 | 27.5 | 4 | 21.5 | 400.9358 | 716.3449 | 43.2952 | 1.7867 | 0.84694 | 110 | 64.1504 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.4687 | 35.877
CID=-1682508891 | 9 | 30 | 43.0576 | 4 | 24 | 4.8 | 1.7357 | 148.2186 | 19.1581 | 233.1226 | 421.3224 | 407.5003 | 26392.2472 | 1.6166 | 0.018386 | 6.5469 | 43.0576 | 281.8925 | 9 | 30 | 4 | 24 | 400.9358 | 770.1963 | 46.5154 | 1.921 | 0.86662 | 110 | 75.488 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.9305 | 43.1989
CID=-1682509050 | 9 | 32.5 | 51.0548 | 4 | 26.5 | 5.3 | 1.7357 | 148.2186 | 19.1581 | 236.688 | 422.8412 | 407.5003 | 27603.0759 | 1.7606 | 0.021389 | 5.8904 | 51.0548 | 300.7316 | 9 | 32.5 | 4 | 26.5 | 400.9358 | 827.0396 | 49.7767 | 2.0628 | 0.88215 | 110 | 87.9325 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2579 | 51.2247
CID=-1682509077 | 9 | 35 | 57.3961 | 4 | 29 | 5.8 | 1.7357 | 148.2186 | 19.1581 | 240.2788 | 424.3337 | 407.5003 | 28483.1584 | 1.86 | 0.023973 | 5.4191 | 57.3961 | 311.0375 | 9 | 35 | 4 | 29 | 400.9358 | 886.981 | 52.5675 | 2.2123 | 0.89118 | 110 | 97.8522 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0505 | 57.5838
CID=-1682508980 | 9 | 37.5 | 66.6962 | 4 | 31.5 | 6.3 | 1.7357 | 148.2186 | 19.1581 | 243.8959 | 425.8002 | 407.5003 | 29603.9357 | 1.9985 | 0.02769 | 4.9024 | 66.6962 | 326.9716 | 9 | 37.5 | 4 | 31.5 | 400.9358 | 950.1287 | 55.9494 | 2.3698 | 0.90068 | 110 | 112.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.6818 | 66.9124
CID=-1682509015 | 9 | 40 | 76.8117 | 4 | 34 | 6.8 | 1.7357 | 148.2186 | 19.1581 | 247.5407 | 427.2409 | 407.5003 | 30703.389 | 2.1339 | 0.03187 | 4.4437 | 76.8117 | 341.3309 | 9 | 40 | 4 | 34 | 400.9358 | 1016.593 | 59.4149 | 2.5356 | 0.9075 | 110 | 128.5993 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.2008 | 77.061
CID=-1682509174 | 9 | 42.5 | 87.291 | 4 | 36.5 | 7.3 | 1.7357 | 148.2186 | 19.1581 | 251.2145 | 428.656 | 407.5003 | 31676.5214 | 2.2663 | 0.036385 | 4.0577 | 87.291 | 354.1978 | 9 | 42.5 | 4 | 36.5 | 400.9358 | 1086.4865 | 62.7778 | 2.7099 | 0.91203 | 110 | 145.417 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 30.9216 | 87.5743
CID=-1682509201 | 9 | 45 | 97.083 | 4 | 39 | 7.8 | 1.7357 | 148.2186 | 19.1581 | 254.9187 | 430.0457 | 407.5003 | 32472.3633 | 2.3827 | 0.040873 | 3.7447 | 97.083 | 363.5513 | 9 | 45 | 4 | 39 | 400.9358 | 1159.9242 | 65.8839 | 2.893 | 0.91477 | 110 | 161.2453 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.7915 | 97.396
CID=-1682509104 | 9 | 47.5 | 105.6067 | 4 | 41.5 | 8.3 | 1.7357 | 148.2186 | 19.1581 | 258.655 | 431.4103 | 407.5003 | 33102.5283 | 2.4815 | 0.045116 | 3.4975 | 105.6068 | 369.3595 | 9 | 47.5 | 4 | 41.5 | 400.9358 | 1237.0237 | 68.6387 | 3.0853 | 0.91637 | 110 | 175.0952 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 39.4856 | 105.939
CID=126010700 | 9 | 50 | 116.8333 | 4 | 44 | 8.8 | 1.7357 | 148.2186 | 19.1581 | 262.425 | 432.7501 | 407.5003 | 33986.9942 | 2.6058 | 0.050638 | 3.2357 | 116.8333 | 378.0386 | 9 | 50 | 4 | 44 | 400.9358 | 1317.9055 | 71.7877 | 3.2871 | 0.91776 | 110 | 193.4157 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.3087 | 117.1977
CID=126010797 | 9 | 52.5 | 126.5736 | 4 | 46.5 | 9.3 | 1.7357 | 148.2186 | 19.1581 | 266.2308 | 434.0651 | 407.5003 | 34728.9229 | 2.7183 | 0.055877 | 3.034 | 126.5736 | 384.0197 | 9 | 52.5 | 4 | 46.5 | 400.9358 | 1402.6932 | 74.4873 | 3.4985 | 0.91853 | 110 | 209.366 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 49.6486 | 126.9601
CID=126010762 | 9 | 55 | 126.6 | 4 | 49 | 9.8 | 1.7357 | 148.2186 | 19.1581 | 270.0745 | 435.3559 | 407.5003 | 34789.2013 | 2.7095 | 0.057451 | 2.9412 | 126.5999 | 372.354 | 9 | 55 | 4 | 49 | 400.9358 | 1491.5141 | 75.9414 | 3.7201 | 0.91853 | 110 | 209.4092 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.9361 | 126.9601
CID=126010603 | 9 | 57.5 | 126.6332 | 4 | 51.5 | 10.3 | 1.7357 | 148.2186 | 19.1581 | 273.9586 | 436.6225 | 407.5003 | 34856.5749 | 2.6936 | 0.059136 | 2.8405 | 126.6333 | 359.7042 | 9 | 57.5 | 4 | 51.5 | 400.9358 | 1584.4992 | 77.5484 | 3.952 | 0.91853 | 110 | 209.4639 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.5619 | 126.9602
CID=126010576 | 9 | 60 | 126.6629 | 4 | 54 | 10.8 | 1.7357 | 148.2186 | 19.1581 | 277.8855 | 437.8652 | 407.5003 | 34930.2012 | 2.6679 | 0.06094 | 2.7301 | 126.663 | 345.8005 | 9 | 60 | 4 | 54 | 400.9358 | 1681.7842 | 79.34 | 4.1946 | 0.91853 | 110 | 209.5126 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.5145 | 126.9601
CID=126010673 | 9 | 62.5 | 126.6998 | 4 | 56.5 | 11.3 | 1.7357 | 148.2186 | 19.1581 | 281.8586 | 439.0844 | 407.5003 | 35004.729 | 2.6383 | 0.062884 | 2.6163 | 126.6999 | 331.4855 | 9 | 62.5 | 4 | 56.5 | 400.9358 | 1783.5096 | 81.2409 | 4.4484 | 0.91854 | 110 | 209.5731 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.8839 | 126.9602
CID=126010638 | 9 | 65 | 126.7481 | 4 | 59 | 11.8 | 1.7357 | 148.2186 | 19.1581 | 285.881 | 440.2804 | 407.5003 | 35110.7899 | 2.596 | 0.064986 | 2.4909 | 126.7482 | 315.7221 | 9 | 65 | 4 | 59 | 400.9358 | 1889.8218 | 83.3733 | 4.7135 | 0.91854 | 110 | 209.6523 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 84.545 | 126.9602
CID=126010479 | 9 | 67.5 | 126.7927 | 4 | 61.5 | 12.3 | 1.7357 | 148.2186 | 19.1581 | 289.9569 | 441.4534 | 407.5003 | 35252.1936 | 2.5411 | 0.067261 | 2.3557 | 126.7927 | 298.6844 | 9 | 67.5 | 4 | 61.5 | 400.9358 | 2000.8736 | 85.7361 | 4.9905 | 0.91854 | 110 | 209.7253 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 93.4753 | 126.9601
CID=126010452 | 9 | 69.99 | 126.8386 | 4 | 63.99 | 12.798 | 1.7357 | 148.2186 | 19.1581 | 294.074 | 442.5993 | 407.5003 | 35392.2116 | 2.4849 | 0.069725 | 2.2222 | 126.8386 | 281.8569 | 9 | 69.99 | 4 | 63.99 | 400.9358 | 2116.3519 | 88.172 | 5.2785 | 0.91855 | 110 | 209.8006 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 102.6563 | 126.9602
CID=126010549 | 12 | -5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649423 | 12 | -2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649326 | 12 | 0 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649361 | 12 | 2.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649520 | 12 | 5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649547 | 12 | 7.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649450 | 12 | 10 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649485 | 12 | 12.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649644 | 12 | 15 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649671 | 12 | 17.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844649574 | 12 | 20 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521660138 | 12 | 22.5 | 0 | 4 | 17 | 3.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1521660041 | 12 | 25 | 16.6787 | 4 | 19 | 3.8 | 1.7345 | 147.9949 | 21.1172 | 226.0633 | 417.8241 | 409.2305 | 20191.0005 | 1.0247 | 0.0095481 | 11.2537 | 16.6787 | 187.6972 | 12 | 25 | 4 | 19 | 443.0145 | 665.3809 | 36.2102 | 1.5019 | 0.75404 | 87.92 | 33.6067 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10.795 | 16.7083
CID=-1521660076 | 12 | 27.5 | 29.7097 | 4 | 21.5 | 4.3 | 1.7345 | 147.9949 | 21.1172 | 229.5813 | 419.3925 | 409.2305 | 23232.3545 | 1.3994 | 0.013707 | 8.4617 | 29.7097 | 251.3936 | 12 | 27.5 | 4 | 21.5 | 443.0145 | 716.3449 | 42.1206 | 1.617 | 0.82523 | 110 | 54.6988 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 11.1128 | 29.8031
CID=-1521660235 | 12 | 30 | 36.6181 | 4 | 24 | 4.8 | 1.7345 | 147.9949 | 21.1172 | 233.1226 | 420.9344 | 409.2305 | 24617.3459 | 1.5614 | 0.016164 | 7.5094 | 36.6181 | 274.9809 | 12 | 30 | 4 | 24 | 443.0145 | 770.1963 | 45.2939 | 1.7385 | 0.84959 | 110 | 65.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0293 | 36.7366
CID=-1521660262 | 12 | 32.5 | 44.1319 | 4 | 26.5 | 5.3 | 1.7345 | 147.9949 | 21.1172 | 236.688 | 422.4497 | 409.2305 | 25890.4539 | 1.7207 | 0.018929 | 6.7273 | 44.1319 | 296.8905 | 12 | 32.5 | 4 | 26.5 | 443.0145 | 827.0396 | 48.4312 | 1.8668 | 0.86903 | 110 | 77.1569 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.6766 | 44.2749
CID=-1521660165 | 12 | 35 | 52.3933 | 4 | 29 | 5.8 | 1.7345 | 147.9949 | 21.1172 | 240.2788 | 423.9389 | 409.2305 | 27089.6042 | 1.8766 | 0.022068 | 6.0514 | 52.3933 | 317.0525 | 12 | 35 | 4 | 29 | 443.0145 | 886.981 | 51.6264 | 2.0021 | 0.88427 | 110 | 90.0218 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.1723 | 52.5653
CID=-1521660200 | 12 | 37.5 | 59.1609 | 4 | 31.5 | 6.3 | 1.7345 | 147.9949 | 21.1172 | 243.8959 | 425.402 | 409.2305 | 27985.9479 | 1.9872 | 0.024844 | 5.5536 | 59.1608 | 328.5529 | 12 | 37.5 | 4 | 31.5 | 443.0145 | 950.1287 | 54.4349 | 2.1447 | 0.89329 | 110 | 100.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.8063 | 59.3536
CID=-1521660359 | 12 | 40 | 68.4887 | 4 | 34 | 6.8 | 1.7345 | 147.9949 | 21.1172 | 247.5407 | 426.8393 | 409.2305 | 29071.3063 | 2.1333 | 0.02864 | 5.0364 | 68.4887 | 344.936 | 12 | 40 | 4 | 34 | 443.0145 | 1016.593 | 57.6746 | 2.2947 | 0.90212 | 110 | 115.3486 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.0173 | 68.7122
CID=-1521660386 | 12 | 42.5 | 79.0457 | 4 | 36.5 | 7.3 | 1.7345 | 147.9949 | 21.1172 | 251.2145 | 428.251 | 409.2305 | 30159.1379 | 2.28 | 0.033056 | 4.5578 | 79.0457 | 360.2706 | 12 | 42.5 | 4 | 36.5 | 443.0145 | 1086.4865 | 61.1069 | 2.4525 | 0.90864 | 110 | 132.1726 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.0083 | 79.3022
CID=-1521660289 | 12 | 45 | 89.8822 | 4 | 39 | 7.8 | 1.7345 | 147.9949 | 21.1172 | 254.9187 | 429.6374 | 409.2305 | 31137.4425 | 2.4233 | 0.037793 | 4.1604 | 89.8822 | 373.9472 | 12 | 45 | 4 | 39 | 443.0145 | 1159.9242 | 64.406 | 2.6183 | 0.91287 | 110 | 149.5959 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.8335 | 90.1739
CID=-1714458373 | 12 | 47.5 | 101.6907 | 4 | 41.5 | 8.3 | 1.7345 | 147.9949 | 21.1172 | 258.655 | 430.9986 | 409.2305 | 32074.733 | 2.5634 | 0.043137 | 3.7957 | 101.6908 | 385.9925 | 12 | 47.5 | 4 | 41.5 | 443.0145 | 1237.0237 | 67.8295 | 2.7923 | 0.91571 | 110 | 168.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.2059 | 102.0198
CID=-1714458276 | 12 | 50 | 109.4012 | 4 | 44 | 8.8 | 1.7345 | 147.9949 | 21.1172 | 262.425 | 432.335 | 409.2305 | 32631.1164 | 2.6551 | 0.047196 | 3.5629 | 109.4011 | 389.7804 | 12 | 50 | 4 | 44 | 443.0145 | 1317.9055 | 70.3808 | 2.9749 | 0.91692 | 110 | 181.2783 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.3372 | 109.7483
CID=-1714458311 | 12 | 52.5 | 121.0435 | 4 | 46.5 | 9.3 | 1.7345 | 147.9949 | 21.1172 | 266.2308 | 433.6467 | 409.2305 | 33427.139 | 2.7896 | 0.053027 | 3.2956 | 121.0435 | 398.9159 | 12 | 52.5 | 4 | 46.5 | 443.0145 | 1402.6932 | 73.479 | 3.1662 | 0.91813 | 110 | 200.3049 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5194 | 121.423
CID=-1714458470 | 12 | 55 | 126.5794 | 4 | 49 | 9.8 | 1.7345 | 147.9949 | 21.1172 | 270.0745 | 434.934 | 409.2305 | 33856.9627 | 2.8461 | 0.056728 | 3.1289 | 126.5794 | 396.0516 | 12 | 55 | 4 | 49 | 443.0145 | 1491.5141 | 75.6926 | 3.3667 | 0.91853 | 110 | 209.3756 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.8145 | 126.9602
CID=-1714458497 | 12 | 57.5 | 126.6082 | 4 | 51.5 | 10.3 | 1.7345 | 147.9949 | 21.1172 | 273.9586 | 436.1972 | 409.2305 | 33944.3354 | 2.8302 | 0.058369 | 3.0239 | 126.6082 | 382.8518 | 12 | 57.5 | 4 | 51.5 | 443.0145 | 1584.4992 | 77.2846 | 3.5766 | 0.91853 | 110 | 209.4228 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.5802 | 126.9601
CID=-1714458400 | 12 | 60 | 126.6398 | 4 | 54 | 10.8 | 1.7345 | 147.9949 | 21.1172 | 277.8855 | 437.4365 | 409.2305 | 34021.6491 | 2.8159 | 0.060128 | 2.9205 | 126.6398 | 369.8502 | 12 | 60 | 4 | 54 | 443.0145 | 1681.7842 | 78.9152 | 3.7962 | 0.91853 | 110 | 209.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 62.8856 | 126.9602
CID=-1714458435 | 12 | 62.5 | 126.6759 | 4 | 56.5 | 11.3 | 1.7345 | 147.9949 | 21.1172 | 281.8586 | 438.6523 | 409.2305 | 34111.521 | 2.7876 | 0.062019 | 2.8029 | 126.6759 | 355.066 | 12 | 62.5 | 4 | 56.5 | 443.0145 | 1783.5096 | 80.7709 | 4.0258 | 0.91853 | 110 | 209.5338 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 70.1201 | 126.9601
CID=-1714458594 | 12 | 65 | 126.7063 | 4 | 59 | 11.8 | 1.7345 | 147.9949 | 21.1172 | 285.881 | 439.8448 | 409.2305 | 34221.3054 | 2.7546 | 0.064055 | 2.6816 | 126.7063 | 339.7793 | 12 | 65 | 4 | 59 | 443.0145 | 1889.8218 | 82.7388 | 4.2658 | 0.91854 | 110 | 209.5836 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 76.1762 | 126.9602
CID=-1714458621 | 12 | 67.5 | 126.7485 | 4 | 61.5 | 12.3 | 1.7345 | 147.9949 | 21.1172 | 289.9569 | 441.0144 | 409.2305 | 34343.6437 | 2.7013 | 0.066264 | 2.542 | 126.7485 | 322.1964 | 12 | 67.5 | 4 | 61.5 | 443.0145 | 2000.8736 | 85.0136 | 4.5165 | 0.91854 | 110 | 209.6528 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 84.6298 | 126.9602
CID=-1714458524 | 12 | 69.99 | 126.7989 | 4 | 63.99 | 12.798 | 1.7345 | 147.9949 | 21.1172 | 294.074 | 442.1569 | 409.2305 | 34500.6501 | 2.6366 | 0.068658 | 2.3945 | 126.7989 | 303.6178 | 12 | 69.99 | 4 | 63.99 | 443.0145 | 2116.3519 | 87.4888 | 4.7772 | 0.91854 | 110 | 209.7354 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 94.7107 | 126.9601
CID=94061280 | 15 | -5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061377 | 15 | -2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061342 | 15 | 0 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061183 | 15 | 2.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061156 | 15 | 5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061253 | 15 | 7.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061218 | 15 | 10 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061059 | 15 | 12.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061032 | 15 | 15 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94061129 | 15 | 17.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876598843 | 15 | 20 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876598746 | 15 | 22.5 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876598781 | 15 | 25 | 0 | 4 | 20 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876598940 | 15 | 27.5 | 0 | 4 | 21.5 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876598967 | 15 | 30 | 30.0307 | 4 | 24 | 4.8 | 1.7333 | 147.7132 | 23.2347 | 233.1226 | 420.5719 | 410.9364 | 22701.7202 | 1.4808 | 0.013949 | 8.7678 | 30.0307 | 263.3026 | 15 | 30 | 4 | 24 | 488.3739 | 770.1963 | 44.0437 | 1.5771 | 0.82653 | 110 | 55.2029 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.3198 | 30.1197
CID=-1876598870 | 15 | 32.5 | 37.4096 | 4 | 26.5 | 5.3 | 1.7333 | 147.7132 | 23.2347 | 236.688 | 422.0841 | 410.9364 | 24125.1159 | 1.6557 | 0.01659 | 7.7122 | 37.4096 | 288.5113 | 15 | 32.5 | 4 | 26.5 | 488.3739 | 827.0396 | 47.3168 | 1.6935 | 0.85194 | 110 | 66.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.0742 | 37.5319
CID=-1876598905 | 15 | 35 | 45.1406 | 4 | 29 | 5.8 | 1.7333 | 147.7132 | 23.2347 | 240.2788 | 423.5701 | 410.9364 | 25393.9421 | 1.8278 | 0.019469 | 6.91 | 45.1406 | 311.9207 | 15 | 35 | 4 | 29 | 488.3739 | 886.981 | 50.3873 | 1.8162 | 0.87119 | 110 | 78.7243 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.7101 | 45.2884
CID=-1876599064 | 15 | 37.5 | 53.7356 | 4 | 31.5 | 6.3 | 1.7333 | 147.7132 | 23.2347 | 243.8959 | 425.03 | 410.9364 | 26594.018 | 1.9964 | 0.022771 | 6.2059 | 53.7356 | 333.4758 | 15 | 37.5 | 4 | 31.5 | 488.3739 | 950.1287 | 53.5533 | 1.9455 | 0.88627 | 110 | 92.1193 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 18.4587 | 53.9129
CID=-1876599091 | 15 | 40 | 63.0977 | 4 | 34 | 6.8 | 1.7333 | 147.7132 | 23.2347 | 247.5407 | 426.4641 | 410.9364 | 27733.7449 | 2.1617 | 0.02649 | 5.5978 | 63.0977 | 353.2055 | 15 | 40 | 4 | 34 | 488.3739 | 1016.593 | 56.7595 | 2.0816 | 0.89745 | 110 | 106.8216 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.4735 | 63.3068
CID=-1876598994 | 15 | 42.5 | 70.3279 | 4 | 36.5 | 7.3 | 1.7333 | 147.7132 | 23.2347 | 251.2145 | 427.8727 | 410.9364 | 28559.217 | 2.2731 | 0.029639 | 5.1625 | 70.3279 | 363.0675 | 15 | 42.5 | 4 | 36.5 | 488.3739 | 1086.4865 | 59.5039 | 2.2247 | 0.90348 | 110 | 118.268 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.7682 | 70.5569
CID=-1553609558 | 15 | 45 | 81.0913 | 4 | 39 | 7.8 | 1.7333 | 147.7132 | 23.2347 | 254.9187 | 429.2559 | 410.9364 | 29615.8314 | 2.4318 | 0.034216 | 4.6788 | 81.0912 | 379.4064 | 15 | 45 | 4 | 39 | 488.3739 | 1159.9242 | 62.8199 | 2.3751 | 0.9096 | 110 | 135.4504 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.93 | 81.3534
CID=-1553609461 | 15 | 47.5 | 92.6478 | 4 | 41.5 | 8.3 | 1.7333 | 147.7132 | 23.2347 | 258.655 | 430.614 | 410.9364 | 30648.4988 | 2.5867 | 0.039317 | 4.2516 | 92.6478 | 393.9029 | 15 | 47.5 | 4 | 41.5 | 488.3739 | 1237.0237 | 66.1821 | 2.5329 | 0.91367 | 110 | 154.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.6346 | 92.9494
CID=-1553609496 | 15 | 50 | 104.6114 | 4 | 44 | 8.8 | 1.7333 | 147.7132 | 23.2347 | 262.425 | 431.9472 | 410.9364 | 31567.9373 | 2.7382 | 0.044841 | 3.8874 | 104.6114 | 406.6614 | 15 | 50 | 4 | 44 | 488.3739 | 1317.9055 | 69.4666 | 2.6986 | 0.91622 | 110 | 173.4749 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.943 | 104.9514
CID=-1553609655 | 15 | 52.5 | 116.3215 | 4 | 46.5 | 9.3 | 1.7333 | 147.7132 | 23.2347 | 266.2308 | 433.2557 | 410.9364 | 32357.0631 | 2.8786 | 0.050568 | 3.581 | 116.3215 | 416.5507 | 15 | 52.5 | 4 | 46.5 | 488.3739 | 1402.6932 | 72.5982 | 2.8722 | 0.91771 | 110 | 192.5789 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2093 | 116.6989
CID=-1553609682 | 15 | 55 | 125.2006 | 4 | 49 | 9.8 | 1.7333 | 147.7132 | 23.2347 | 270.0745 | 434.5399 | 410.9364 | 32903.4793 | 2.9814 | 0.055491 | 3.3543 | 125.2005 | 419.9598 | 15 | 55 | 4 | 49 | 488.3739 | 1491.5141 | 75.2326 | 3.054 | 0.91844 | 110 | 207.1151 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 46.8297 | 125.5944
CID=-1553609585 | 15 | 57.5 | 126.5839 | 4 | 51.5 | 10.3 | 1.7333 | 147.7132 | 23.2347 | 273.9586 | 435.7999 | 410.9364 | 33025.7166 | 2.987 | 0.057632 | 3.2322 | 126.5839 | 409.1495 | 15 | 57.5 | 4 | 51.5 | 488.3739 | 1584.4992 | 76.9352 | 3.2444 | 0.91853 | 110 | 209.3829 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.704 | 126.9601
CID=-1553609620 | 15 | 60 | 126.6162 | 4 | 54 | 10.8 | 1.7333 | 147.7132 | 23.2347 | 277.8855 | 437.0361 | 410.9364 | 33096.0824 | 2.9681 | 0.059347 | 3.119 | 126.6162 | 394.9103 | 15 | 60 | 4 | 54 | 488.3739 | 1681.7842 | 78.6063 | 3.4436 | 0.91853 | 110 | 209.4359 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.1896 | 126.9601
CID=-1553609779 | 15 | 62.5 | 126.6452 | 4 | 56.5 | 11.3 | 1.7333 | 147.7132 | 23.2347 | 281.8586 | 438.2486 | 410.9364 | 33196.9865 | 2.9413 | 0.061186 | 2.9978 | 126.6452 | 379.6564 | 15 | 62.5 | 4 | 56.5 | 488.3739 | 1783.5096 | 80.4198 | 3.6519 | 0.91853 | 110 | 209.4835 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.9624 | 126.9602
CID=-1553609806 | 15 | 65 | 126.6817 | 4 | 59 | 11.8 | 1.7333 | 147.7132 | 23.2347 | 285.881 | 439.4379 | 410.9364 | 33310.7119 | 2.9122 | 0.063171 | 2.8748 | 126.6818 | 364.19 | 15 | 65 | 4 | 59 | 488.3739 | 1889.8218 | 82.3164 | 3.8696 | 0.91854 | 110 | 209.5434 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 71.2677 | 126.9602
CID=-1553609709 | 15 | 67.5 | 126.7202 | 4 | 61.5 | 12.3 | 1.7333 | 147.7132 | 23.2347 | 289.9569 | 440.6043 | 410.9364 | 33439.2651 | 2.8701 | 0.065317 | 2.7401 | 126.7202 | 347.221 | 15 | 67.5 | 4 | 61.5 | 488.3739 | 2000.8736 | 84.4126 | 4.097 | 0.91854 | 110 | 209.6065 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 78.9695 | 126.9602
CID=-1746407793 | 15 | 69.99 | 126.7537 | 4 | 63.99 | 12.798 | 1.7333 | 147.7132 | 23.2347 | 294.074 | 441.7436 | 410.9364 | 33587.6199 | 2.8065 | 0.067634 | 2.5875 | 126.7537 | 327.98 | 15 | 69.99 | 4 | 63.99 | 488.3739 | 2116.3519 | 86.7949 | 4.3335 | 0.91854 | 110 | 209.6613 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 85.6595 | 126.9602
CID=-1746407696 | 18 | -5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746407731 | 18 | -2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746407890 | 18 | 0 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746407917 | 18 | 2.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746407820 | 18 | 5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746407855 | 18 | 7.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746408014 | 18 | 10 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746408041 | 18 | 12.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746407944 | 18 | 15 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489713917 | 18 | 17.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489713886 | 18 | 20 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489713855 | 18 | 22.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489713824 | 18 | 25 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489714041 | 18 | 27.5 | 0 | 4 | 23 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489714010 | 18 | 30 | 0 | 4 | 24 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489713979 | 18 | 32.5 | 32.2351 | 4 | 26.5 | 5.3 | 1.7322 | 147.3721 | 25.5211 | 236.688 | 421.7412 | 412.6163 | 22537.8389 | 1.6186 | 0.014794 | 8.8341 | 32.2351 | 284.7662 | 18 | 32.5 | 4 | 26.5 | 537.1767 | 827.0396 | 46.5194 | 1.5396 | 0.83498 | 110 | 58.6551 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 12.839 | 32.3325
CID=-1489713948 | 18 | 35 | 38.1074 | 4 | 29 | 5.8 | 1.7322 | 147.3721 | 25.5211 | 240.2788 | 423.2242 | 412.6163 | 23629.1674 | 1.7522 | 0.017 | 7.9243 | 38.1074 | 301.9729 | 18 | 35 | 4 | 29 | 537.1767 | 886.981 | 49.3545 | 1.6512 | 0.85396 | 110 | 67.8 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 13.112 | 38.233
CID=-1489714165 | 18 | 37.5 | 46.1446 | 4 | 31.5 | 6.3 | 1.7322 | 147.3721 | 25.5211 | 243.8959 | 424.6812 | 412.6163 | 24905.1426 | 1.9381 | 0.020025 | 7.0864 | 46.1445 | 326.9977 | 18 | 37.5 | 4 | 31.5 | 537.1767 | 950.1287 | 52.4055 | 1.7687 | 0.87325 | 110 | 80.2852 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.9579 | 46.2963
CID=-1489714134 | 18 | 40 | 55.01 | 4 | 34 | 6.8 | 1.7322 | 147.3721 | 25.5211 | 247.5407 | 426.1123 | 412.6163 | 26105.9272 | 2.1202 | 0.023474 | 6.3623 | 55.01 | 349.9926 | 18 | 40 | 4 | 34 | 537.1767 | 1016.593 | 55.5173 | 1.8925 | 0.88807 | 110 | 94.113 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.0416 | 55.1907
CID=-1682512152 | 18 | 42.5 | 64.6434 | 4 | 36.5 | 7.3 | 1.7322 | 147.3721 | 25.5211 | 251.2145 | 427.5179 | 412.6163 | 27230.0761 | 2.2986 | 0.027355 | 5.7392 | 64.6434 | 371.004 | 18 | 42.5 | 4 | 36.5 | 537.1767 | 1086.4865 | 58.6595 | 2.0226 | 0.8989 | 110 | 109.2619 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 21.9546 | 64.858
CID=-1682512121 | 18 | 45 | 72.0788 | 4 | 39 | 7.8 | 1.7322 | 147.3721 | 25.5211 | 254.9187 | 428.8982 | 412.6163 | 28037.6385 | 2.418 | 0.030643 | 5.2903 | 72.0788 | 381.3187 | 18 | 45 | 4 | 39 | 537.1767 | 1159.9242 | 61.3774 | 2.1593 | 0.90467 | 110 | 121.0517 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 25.0409 | 72.3151
CID=-1682512090 | 18 | 47.5 | 83.0666 | 4 | 41.5 | 8.3 | 1.7322 | 147.3721 | 25.5211 | 258.655 | 430.2533 | 412.6163 | 29082.7008 | 2.5893 | 0.035393 | 4.7992 | 83.0666 | 398.6497 | 18 | 47.5 | 4 | 41.5 | 537.1767 | 1237.0237 | 64.6005 | 2.3028 | 0.91044 | 110 | 138.6209 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.9027 | 83.3388
CID=-1682512059 | 18 | 50 | 95.1647 | 4 | 44 | 8.8 | 1.7322 | 147.3721 | 25.5211 | 262.425 | 431.5835 | 412.6163 | 30113.7854 | 2.7566 | 0.040806 | 4.3506 | 95.1647 | 414.0246 | 18 | 50 | 4 | 44 | 537.1767 | 1317.9055 | 67.9581 | 2.4534 | 0.91432 | 110 | 158.1369 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 33.7506 | 95.4733
CID=-1682512276 | 18 | 52.5 | 107.463 | 4 | 46.5 | 9.3 | 1.7322 | 147.3721 | 25.5211 | 266.2308 | 432.8891 | 412.6163 | 31031.7229 | 2.9201 | 0.046587 | 3.9778 | 107.463 | 427.4623 | 18 | 52.5 | 4 | 46.5 | 537.1767 | 1402.6932 | 71.178 | 2.6112 | 0.91665 | 110 | 178.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.0197 | 107.8119
CID=-1682512245 | 18 | 55 | 120.8592 | 4 | 49 | 9.8 | 1.7322 | 147.3721 | 25.5211 | 270.0745 | 434.1702 | 412.6163 | 31919.244 | 3.0797 | 0.053125 | 3.6322 | 120.8592 | 438.9903 | 18 | 55 | 4 | 49 | 537.1767 | 1491.5141 | 74.5248 | 2.7766 | 0.91812 | 110 | 200.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 42.9579 | 121.2507
CID=-1682512214 | 18 | 57.5 | 126.5637 | 4 | 51.5 | 10.3 | 1.7322 | 147.3721 | 25.5211 | 273.9586 | 435.4273 | 412.6163 | 32288.033 | 3.1434 | 0.056926 | 3.4438 | 126.5638 | 435.8636 | 18 | 57.5 | 4 | 51.5 | 537.1767 | 1584.4992 | 76.7438 | 2.9497 | 0.91853 | 110 | 209.3499 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.6837 | 126.9601
CID=-1682512183 | 18 | 60 | 126.591 | 4 | 54 | 10.8 | 1.7322 | 147.3721 | 25.5211 | 277.8855 | 436.6604 | 412.6163 | 32343.1587 | 3.1291 | 0.058596 | 3.3303 | 126.591 | 421.5816 | 18 | 60 | 4 | 54 | 537.1767 | 1681.7842 | 78.3555 | 3.1308 | 0.91853 | 110 | 209.3946 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 53.1459 | 126.9601
CID=-1682512400 | 18 | 62.5 | 126.6233 | 4 | 56.5 | 11.3 | 1.7322 | 147.3721 | 25.5211 | 281.8586 | 437.87 | 412.6163 | 32403.2735 | 3.106 | 0.060391 | 3.2074 | 126.6233 | 406.1301 | 18 | 62.5 | 4 | 56.5 | 537.1767 | 1783.5096 | 80.112 | 3.3202 | 0.91853 | 110 | 209.4476 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 59.592 | 126.9601
CID=-1682512369 | 18 | 65 | 126.6526 | 4 | 59 | 11.8 | 1.7322 | 147.3721 | 25.5211 | 285.881 | 439.0563 | 412.6163 | 32490.7855 | 3.0737 | 0.06232 | 3.0757 | 126.6526 | 389.5515 | 18 | 65 | 4 | 59 | 537.1767 | 1889.8218 | 82.0144 | 3.5181 | 0.91853 | 110 | 209.4956 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 65.4574 | 126.9601
CID=126007501 | 18 | 67.5 | 126.6862 | 4 | 61.5 | 12.3 | 1.7322 | 147.3721 | 25.5211 | 289.9569 | 440.2196 | 412.6163 | 32597.3361 | 3.0356 | 0.064407 | 2.9391 | 126.6862 | 372.3428 | 18 | 67.5 | 4 | 61.5 | 537.1767 | 2000.8736 | 84.0334 | 3.7248 | 0.91854 | 110 | 209.5506 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 72.1509 | 126.9602
CID=126007532 | 18 | 69.99 | 126.725 | 4 | 63.99 | 12.798 | 1.7322 | 147.3721 | 25.5211 | 294.074 | 441.3558 | 412.6163 | 32719.0455 | 2.9874 | 0.066662 | 2.7945 | 126.725 | 354.1348 | 18 | 69.99 | 4 | 63.99 | 537.1767 | 2116.3519 | 86.2028 | 3.9398 | 0.91854 | 110 | 209.6144 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79.9236 | 126.9602
CID=126007563 | 21 | -5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007594 | 21 | -2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007377 | 21 | 0 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007408 | 21 | 2.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007439 | 21 | 5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007470 | 21 | 7.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007253 | 21 | 10 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126007284 | 21 | 12.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652622 | 21 | 15 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652591 | 21 | 17.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652560 | 21 | 20 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652529 | 21 | 22.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652746 | 21 | 25 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652715 | 21 | 27.5 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652684 | 21 | 30 | 0 | 4 | 26 | 5.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652653 | 21 | 32.5 | 0 | 4 | 26.5 | 5.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844652870 | 21 | 35 | 24.4309 | 4 | 29 | 5.8 | 1.7312 | 146.9698 | 27.9878 | 240.2788 | 422.8982 | 414.2684 | 20469.1442 | 1.459 | 0.012476 | 10.3905 | 24.4309 | 253.85 | 21 | 35 | 4 | 29 | 589.5892 | 886.981 | 46.3869 | 1.5044 | 0.80108 | 87.9245 | 46.3359 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13.5732 | 24.4855
CID=-1844652839 | 21 | 37.5 | 38.6691 | 4 | 31.5 | 6.3 | 1.7312 | 146.9698 | 27.9878 | 243.8959 | 424.3523 | 414.2684 | 23130.4811 | 1.8513 | 0.01738 | 8.1567 | 38.6691 | 315.412 | 21 | 37.5 | 4 | 31.5 | 589.5892 | 950.1287 | 51.3832 | 1.6115 | 0.85553 | 110 | 68.6726 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 14.0444 | 38.7928
CID=-1521663337 | 21 | 40 | 47.0967 | 4 | 34 | 6.8 | 1.7312 | 146.9698 | 27.9878 | 247.5407 | 425.7807 | 414.2684 | 24421.1938 | 2.0515 | 0.020584 | 7.2627 | 47.0968 | 342.0497 | 21 | 40 | 4 | 34 | 589.5892 | 1016.593 | 54.4606 | 1.7242 | 0.87513 | 110 | 81.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5838 | 47.2501
CID=-1521663306 | 21 | 42.5 | 56.1861 | 4 | 36.5 | 7.3 | 1.7312 | 146.9698 | 27.9878 | 251.2145 | 427.1835 | 414.2684 | 25608.8054 | 2.2481 | 0.024169 | 6.524 | 56.1861 | 366.5581 | 21 | 42.5 | 4 | 36.5 | 589.5892 | 1086.4865 | 57.5053 | 1.8428 | 0.88965 | 110 | 95.9551 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.8198 | 56.3689
CID=-1521663275 | 21 | 45 | 66.1134 | 4 | 39 | 7.8 | 1.7312 | 146.9698 | 27.9878 | 254.9187 | 428.5609 | 414.2684 | 26731.5343 | 2.4404 | 0.028224 | 5.882 | 66.1134 | 388.8802 | 21 | 45 | 4 | 39 | 589.5892 | 1159.9242 | 60.601 | 1.9673 | 0.90019 | 110 | 111.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.9995 | 66.3301
CID=-1521663244 | 21 | 47.5 | 76.2749 | 4 | 41.5 | 8.3 | 1.7312 | 146.9698 | 27.9878 | 258.655 | 429.9132 | 414.2684 | 27746.7305 | 2.6157 | 0.032567 | 5.3364 | 76.2749 | 407.0356 | 21 | 47.5 | 4 | 41.5 | 589.5892 | 1237.0237 | 63.6707 | 2.0981 | 0.9072 | 110 | 127.7416 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2319 | 76.5263
CID=-1521663461 | 21 | 50 | 85.1107 | 4 | 44 | 8.8 | 1.7312 | 146.9698 | 27.9878 | 262.425 | 431.2407 | 414.2684 | 28574.1986 | 2.7526 | 0.036643 | 4.9109 | 85.1107 | 417.9708 | 21 | 50 | 4 | 44 | 589.5892 | 1317.9055 | 66.4841 | 2.2353 | 0.91125 | 110 | 141.9067 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.9299 | 85.388
CID=-1521663430 | 21 | 52.5 | 97.4557 | 4 | 46.5 | 9.3 | 1.7312 | 146.9698 | 27.9878 | 266.2308 | 432.5434 | 414.2684 | 29576.2539 | 2.9332 | 0.042269 | 4.4556 | 97.4556 | 434.2186 | 21 | 52.5 | 4 | 46.5 | 589.5892 | 1402.6932 | 69.7527 | 2.3791 | 0.91485 | 110 | 161.8494 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.5049 | 97.772
CID=-1521663399 | 21 | 55 | 110.5104 | 4 | 49 | 9.8 | 1.7312 | 146.9698 | 27.9878 | 270.0745 | 433.8218 | 414.2684 | 30541.9589 | 3.1093 | 0.048483 | 4.057 | 110.5104 | 448.3372 | 21 | 55 | 4 | 49 | 589.5892 | 1491.5141 | 73.0264 | 2.5298 | 0.91706 | 110 | 183.0878 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 38.7568 | 110.8709
CID=-1521663368 | 21 | 57.5 | 124.0551 | 4 | 51.5 | 10.3 | 1.7312 | 146.9698 | 27.9878 | 273.9586 | 435.076 | 414.2684 | 31414.2704 | 3.2814 | 0.05525 | 3.7114 | 124.0551 | 460.4162 | 21 | 57.5 | 4 | 51.5 | 589.5892 | 1584.4992 | 76.2542 | 2.6875 | 0.91836 | 110 | 205.2379 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 43.7196 | 124.4588
CID=-1521663585 | 21 | 60 | 126.5672 | 4 | 54 | 10.8 | 1.7312 | 146.9698 | 27.9878 | 277.8855 | 436.3063 | 414.2684 | 31601.3979 | 3.2987 | 0.057877 | 3.5546 | 126.5673 | 449.8904 | 21 | 60 | 4 | 54 | 589.5892 | 1681.7842 | 78.1634 | 2.8525 | 0.91853 | 110 | 209.3557 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 48.373 | 126.9601
CID=-1521663554 | 21 | 62.5 | 126.599 | 4 | 56.5 | 11.3 | 1.7312 | 146.9698 | 27.9878 | 281.8586 | 437.513 | 414.2684 | 31664.5573 | 3.2785 | 0.059627 | 3.429 | 126.599 | 434.1098 | 21 | 62.5 | 4 | 56.5 | 589.5892 | 1783.5096 | 79.8778 | 3.025 | 0.91853 | 110 | 209.4077 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 54.7306 | 126.9601
CID=-1714461572 | 21 | 65 | 126.6278 | 4 | 59 | 11.8 | 1.7312 | 146.9698 | 27.9878 | 285.881 | 438.6964 | 414.2684 | 31731.0612 | 3.2503 | 0.061508 | 3.2955 | 126.6278 | 417.3019 | 21 | 65 | 4 | 59 | 589.5892 | 1889.8218 | 81.7204 | 3.2053 | 0.91853 | 110 | 209.4549 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 60.4786 | 126.9602
CID=-1714461541 | 21 | 67.5 | 126.6606 | 4 | 61.5 | 12.3 | 1.7312 | 146.9698 | 27.9878 | 289.9569 | 439.8569 | 414.2684 | 31820.3129 | 3.2115 | 0.063539 | 3.152 | 126.6605 | 399.2289 | 21 | 67.5 | 4 | 61.5 | 589.5892 | 2000.8736 | 83.715 | 3.3937 | 0.91853 | 110 | 209.5086 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 67.0331 | 126.9602
CID=-1714461510 | 21 | 69.99 | 126.6961 | 4 | 63.99 | 12.798 | 1.7312 | 146.9698 | 27.9878 | 294.074 | 440.9902 | 414.2684 | 31931.8252 | 3.1684 | 0.065732 | 3.0058 | 126.6961 | 380.8222 | 21 | 69.99 | 4 | 63.99 | 589.5892 | 2116.3519 | 85.7998 | 3.5895 | 0.91854 | 110 | 209.5669 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 74.1546 | 126.9602
CID=-1714461479 | 24 | -5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714461696 | 24 | -2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714461665 | 24 | 0 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714461634 | 24 | 2.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714461603 | 24 | 5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714461820 | 24 | 7.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1714461789 | 24 | 10 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94058081 | 24 | 12.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94058112 | 24 | 15 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94058143 | 24 | 17.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94058174 | 24 | 20 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057957 | 24 | 22.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057988 | 24 | 25 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94058019 | 24 | 27.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94058050 | 24 | 30 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057833 | 24 | 32.5 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=94057864 | 24 | 35 | 0 | 4 | 29 | 5.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876602042 | 24 | 37.5 | 0 | 4 | 31.5 | 6.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1876602011 | 24 | 40 | 39.0189 | 4 | 34 | 6.8 | 1.7302 | 146.5045 | 30.6472 | 247.5407 | 425.4661 | 415.8906 | 22614.6476 | 1.9529 | 0.017704 | 8.426 | 39.0189 | 328.7714 | 24 | 40 | 4 | 34 | 645.7808 | 1016.593 | 53.3762 | 1.5742 | 0.85649 | 110 | 69.2159 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 15.4516 | 39.1373
CID=-1876601980 | 24 | 42.5 | 47.9628 | 4 | 36.5 | 7.3 | 1.7302 | 146.5045 | 30.6472 | 251.2145 | 426.8662 | 415.8906 | 23936.4247 | 2.1682 | 0.021135 | 7.4443 | 47.9628 | 357.0483 | 24 | 42.5 | 4 | 36.5 | 645.7808 | 1086.4865 | 56.5354 | 1.6824 | 0.87677 | 110 | 83.1142 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.6006 | 48.1204
CID=-1876601949 | 24 | 45 | 57.2976 | 4 | 39 | 7.8 | 1.7302 | 146.5045 | 30.6472 | 254.9187 | 428.241 | 415.8906 | 25120.7675 | 2.3796 | 0.024869 | 6.6853 | 57.2976 | 383.0508 | 24 | 45 | 4 | 39 | 645.7808 | 1159.9242 | 59.5341 | 1.7962 | 0.89106 | 110 | 97.6976 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 19.7334 | 57.4863
CID=-1876602166 | 24 | 47.5 | 67.6101 | 4 | 41.5 | 8.3 | 1.7302 | 146.5045 | 30.6472 | 258.655 | 429.5907 | 415.8906 | 26245.3106 | 2.5867 | 0.029138 | 6.0157 | 67.6102 | 406.7198 | 24 | 47.5 | 4 | 41.5 | 645.7808 | 1237.0237 | 62.6187 | 1.9155 | 0.90143 | 110 | 113.956 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 22.8929 | 67.8348
CID=-1876602135 | 24 | 50 | 78.7404 | 4 | 44 | 8.8 | 1.7302 | 146.5045 | 30.6472 | 262.425 | 430.9154 | 415.8906 | 27313.8786 | 2.7895 | 0.033924 | 5.4367 | 78.7404 | 428.0908 | 24 | 50 | 4 | 44 | 645.7808 | 1317.9055 | 65.7287 | 2.0408 | 0.90849 | 110 | 131.684 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 26.2397 | 79.0043
CID=-1876602104 | 24 | 52.5 | 87.0567 | 4 | 46.5 | 9.3 | 1.7302 | 146.5045 | 30.6472 | 266.2308 | 432.2155 | 415.8906 | 28056.5395 | 2.922 | 0.037908 | 5.0232 | 87.0567 | 437.3036 | 24 | 52.5 | 4 | 46.5 | 645.7808 | 1402.6932 | 68.4121 | 2.1721 | 0.91195 | 110 | 145.0395 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 29.8629 | 87.3441
CID=-1876602073 | 24 | 55 | 99.5964 | 4 | 49 | 9.8 | 1.7302 | 146.5045 | 30.6472 | 270.0745 | 433.4912 | 415.8906 | 29041.8223 | 3.1163 | 0.043738 | 4.5625 | 99.5964 | 454.4068 | 24 | 55 | 4 | 49 | 645.7808 | 1491.5141 | 71.5919 | 2.3096 | 0.91531 | 110 | 165.323 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 34.4237 | 99.9239
CID=-1876602290 | 24 | 57.5 | 113.3309 | 4 | 51.5 | 10.3 | 1.7302 | 146.5045 | 30.6472 | 273.9586 | 434.7427 | 415.8906 | 30019.3634 | 3.3061 | 0.050372 | 4.1404 | 113.3309 | 469.2357 | 24 | 57.5 | 4 | 51.5 | 645.7808 | 1584.4992 | 74.8914 | 2.4536 | 0.9174 | 110 | 187.692 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.2609 | 113.6981
CID=-1876602259 | 24 | 60 | 126.5503 | 4 | 54 | 10.8 | 1.7302 | 146.5045 | 30.6472 | 277.8855 | 435.9703 | 415.8906 | 30859.8542 | 3.4796 | 0.057189 | 3.7946 | 126.5502 | 480.2044 | 24 | 60 | 4 | 54 | 645.7808 | 1681.7842 | 78.0093 | 2.6043 | 0.91853 | 110 | 209.3277 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 44.9849 | 126.9601
CID=-1553612757 | 24 | 62.5 | 126.5776 | 4 | 56.5 | 11.3 | 1.7302 | 146.5045 | 30.6472 | 281.8586 | 437.1743 | 415.8906 | 30927.729 | 3.4649 | 0.058896 | 3.669 | 126.5777 | 464.4101 | 24 | 62.5 | 4 | 56.5 | 645.7808 | 1783.5096 | 79.6666 | 2.7618 | 0.91853 | 110 | 209.3727 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 50.4735 | 126.9601
CID=-1553612726 | 24 | 65 | 126.6045 | 4 | 59 | 11.8 | 1.7302 | 146.5045 | 30.6472 | 285.881 | 438.355 | 415.8906 | 30983.3587 | 3.4441 | 0.06073 | 3.5367 | 126.6045 | 447.7676 | 24 | 65 | 4 | 59 | 645.7808 | 1889.8218 | 81.4322 | 2.9264 | 0.91853 | 110 | 209.4168 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 55.832 | 126.9601
CID=-1553612695 | 24 | 67.5 | 126.6331 | 4 | 61.5 | 12.3 | 1.7302 | 146.5045 | 30.6472 | 289.9569 | 439.5127 | 415.8906 | 31048.3688 | 3.4095 | 0.062708 | 3.3907 | 126.633 | 429.3745 | 24 | 67.5 | 4 | 61.5 | 645.7808 | 2000.8736 | 83.3652 | 3.0984 | 0.91853 | 110 | 209.4635 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 61.542 | 126.9602
CID=-1553612664 | 24 | 69.99 | 126.6688 | 4 | 63.99 | 12.798 | 1.7302 | 146.5045 | 30.6472 | 294.074 | 440.6434 | 415.8906 | 31153.4968 | 3.3572 | 0.064844 | 3.2286 | 126.6688 | 408.9582 | 24 | 69.99 | 4 | 63.99 | 645.7808 | 2116.3519 | 85.4902 | 3.2772 | 0.91853 | 110 | 209.5221 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 68.6833 | 126.9601
CID=-1553612881 | 27 | -5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553612850 | 27 | -2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553612819 | 27 | 0 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553612788 | 27 | 2.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553613005 | 27 | 5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1553612974 | 27 | 7.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746410992 | 27 | 10 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746410961 | 27 | 12.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746410930 | 27 | 15 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746410899 | 27 | 17.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411116 | 27 | 20 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411085 | 27 | 22.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411054 | 27 | 25 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411023 | 27 | 27.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411240 | 27 | 30 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1746411209 | 27 | 32.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489712896 | 27 | 35 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489712799 | 27 | 37.5 | 0 | 4 | 32 | 6.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489712702 | 27 | 40 | 0 | 4 | 34 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1489712861 | 27 | 42.5 | 41.0038 | 4 | 36.5 | 7.3 | 1.7292 | 145.9744 | 33.5123 | 251.2145 | 426.563 | 417.481 | 22347.1336 | 2.106 | 0.018593 | 8.5396 | 41.0038 | 350.1568 | 27 | 42.5 | 4 | 36.5 | 705.9244 | 1086.4865 | 55.7238 | 1.5391 | 0.86169 | 110 | 72.2985 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.346 | 41.1277
CID=-1489713020 | 27 | 45 | 48.7136 | 4 | 39 | 7.8 | 1.7292 | 145.9744 | 33.5123 | 254.9187 | 427.9352 | 417.481 | 23447.4204 | 2.2875 | 0.021668 | 7.6336 | 48.7136 | 371.8622 | 27 | 45 | 4 | 39 | 705.9244 | 1159.9242 | 58.6234 | 1.6431 | 0.87814 | 110 | 84.2832 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16.5416 | 48.8753
CID=-1489712923 | 27 | 47.5 | 58.3849 | 4 | 41.5 | 8.3 | 1.7292 | 145.9744 | 33.5123 | 258.655 | 429.2823 | 417.481 | 24638.2298 | 2.5151 | 0.025589 | 6.842 | 58.3849 | 399.4707 | 27 | 47.5 | 4 | 41.5 | 705.9244 | 1237.0237 | 61.6116 | 1.7523 | 0.89238 | 110 | 99.4042 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.0626 | 58.5775
CID=-1489712826 | 27 | 50 | 68.9706 | 4 | 44 | 8.8 | 1.7292 | 145.9744 | 33.5123 | 262.425 | 430.6045 | 417.481 | 25759.2499 | 2.7381 | 0.03004 | 6.1557 | 68.9706 | 424.5645 | 27 | 50 | 4 | 44 | 705.9244 | 1317.9055 | 64.6496 | 1.8669 | 0.90248 | 110 | 116.1131 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23.8529 | 69.1973
CID=-1489712985 | 27 | 52.5 | 80.3836 | 4 | 46.5 | 9.3 | 1.7292 | 145.9744 | 33.5123 | 266.2308 | 431.902 | 417.481 | 26809.7659 | 2.9561 | 0.035031 | 5.5622 | 80.3835 | 447.1123 | 27 | 52.5 | 4 | 46.5 | 705.9244 | 1402.6932 | 67.7127 | 1.987 | 0.90928 | 110 | 134.3158 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 27.4146 | 80.6498
CID=-1489713144 | 27 | 55 | 89.6172 | 4 | 49 | 9.8 | 1.7292 | 145.9744 | 33.5123 | 270.0745 | 433.1751 | 417.481 | 27598.042 | 3.11 | 0.039463 | 5.1155 | 89.6172 | 458.4343 | 27 | 55 | 4 | 49 | 705.9244 | 1491.5141 | 70.4738 | 2.1129 | 0.91279 | 110 | 149.1682 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31.1505 | 89.9111
CID=-1489713047 | 27 | 57.5 | 101.8294 | 4 | 51.5 | 10.3 | 1.7292 | 145.9744 | 33.5123 | 273.9586 | 434.4241 | 417.481 | 28531.4966 | 3.3063 | 0.045311 | 4.66 | 101.8294 | 474.5288 | 27 | 57.5 | 4 | 51.5 | 705.9244 | 1584.4992 | 73.5322 | 2.2446 | 0.91574 | 110 | 168.9502 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 35.5589 | 102.1624
CID=-1682511131 | 27 | 60 | 115.8727 | 4 | 54 | 10.8 | 1.7292 | 145.9744 | 33.5123 | 277.8855 | 435.6491 | 417.481 | 29486.0624 | 3.5104 | 0.052239 | 4.2291 | 115.8727 | 490.0383 | 27 | 60 | 4 | 54 | 705.9244 | 1681.7842 | 76.7698 | 2.3824 | 0.91767 | 110 | 191.8452 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 40.7067 | 116.2504
CID=-1682511034 | 27 | 62.5 | 126.5532 | 4 | 56.5 | 11.3 | 1.7292 | 145.9744 | 33.5123 | 281.8586 | 436.8505 | 417.481 | 30175.6611 | 3.6537 | 0.058195 | 3.9155 | 126.5531 | 495.5173 | 27 | 62.5 | 4 | 56.5 | 705.9244 | 1783.5096 | 79.5663 | 2.5265 | 0.91853 | 110 | 209.3324 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 45.5787 | 126.9601
CID=-1682510937 | 27 | 65 | 126.5818 | 4 | 59 | 11.8 | 1.7292 | 145.9744 | 33.5123 | 285.881 | 438.0286 | 417.481 | 30246.9814 | 3.6346 | 0.059986 | 3.7787 | 126.5818 | 478.3099 | 27 | 65 | 4 | 59 | 705.9244 | 1889.8218 | 81.3078 | 2.6771 | 0.91853 | 110 | 209.3796 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51.2946 | 126.9601
CID=-1682511096 | 27 | 67.5 | 126.6077 | 4 | 61.5 | 12.3 | 1.7292 | 145.9744 | 33.5123 | 289.9569 | 439.1838 | 417.481 | 30310.0632 | 3.6067 | 0.061915 | 3.6328 | 126.6077 | 459.9424 | 27 | 67.5 | 4 | 61.5 | 705.9244 | 2000.8736 | 83.1712 | 2.8344 | 0.91853 | 110 | 209.4219 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 56.4575 | 126.9602
CID=-1682511255 | 27 | 69.99 | 126.6418 | 4 | 63.99 | 12.798 | 1.7292 | 145.9744 | 33.5123 | 294.074 | 440.3118 | 417.481 | 30392.2419 | 3.563 | 0.063996 | 3.472 | 126.6418 | 439.7042 | 27 | 69.99 | 4 | 63.99 | 705.9244 | 2116.3519 | 85.1994 | 2.998 | 0.91853 | 110 | 209.4779 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 63.2881 | 126.9602
CID=-1682511158 | 30 | -5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682511061 | 30 | -2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682511220 | 30 | 0 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682511379 | 30 | 2.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1682511282 | 30 | 5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008522 | 30 | 7.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008619 | 30 | 10 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008716 | 30 | 12.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008557 | 30 | 15 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008398 | 30 | 17.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008495 | 30 | 20 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008592 | 30 | 22.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008433 | 30 | 25 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008274 | 30 | 27.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=126008371 | 30 | 30 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844651601 | 30 | 32.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844651504 | 30 | 35 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844651407 | 30 | 37.5 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844651566 | 30 | 40 | 0 | 4 | 35 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844651725 | 30 | 42.5 | 0 | 4 | 36.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CID=-1844651628 | 30 | 45 | 35.1467 | 4 | 39 | 7.8 | 1.7283 | 145.3777 | 36.5977 | 254.9187 | 427.6403 | 419.0371 | 20963.447 | 2.0365 | 0.016846 | 9.5095 | 35.1467 | 334.2266 | 30 | 45 | 4 | 39 | 770.1963 | 1159.9242 | 56.5982 | 1.506 | 0.84499 | 110 | 63.196 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.2285 | 35.2368
CID=-1844651531 | 30 | 47.5 | 49.3261 | 4 | 41.5 | 8.3 | 1.7283 | 145.3777 | 36.5977 | 258.655 | 428.9849 | 419.0371 | 22957.7978 | 2.4102 | 0.022176 | 7.8365 | 49.3261 | 386.5458 | 30 | 47.5 | 4 | 41.5 | 770.1963 | 1237.0237 | 60.7132 | 1.6061 | 0.87923 | 110 | 85.2373 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17.3626 | 49.4867
CID=-1844651690 | 30 | 50 | 59.4076 | 4 | 44 | 8.8 | 1.7283 | 145.3777 | 36.5977 | 262.425 | 430.3047 | 419.0371 | 24159.5024 | 2.6545 | 0.026317 | 6.9979 | 59.4077 | 415.7318 | 30 | 50 | 4 | 44 | 770.1963 | 1317.9055 | 63.7215 | 1.7111 | 0.89357 | 110 | 101.011 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 20.758 | 59.6018
CID=-1844651849 | 30 | 52.5 | 70.2255 | 4 | 46.5 | 9.3 | 1.7283 | 145.3777 | 36.5977 | 266.2308 | 431.5997 | 419.0371 | 25268.5237 | 2.8941 | 0.030943 | 6.2974 | 70.2255 | 442.2401 | 30 | 52.5 | 4 | 46.5 | 770.1963 | 1402.6932 | 66.71 | 1.8212 | 0.9034 | 110 | 118.1053 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24.5286 | 70.4551
CID=-1844651752 | 30 | 55 | 81.9932 | 4 | 49 | 9.8 | 1.7283 | 145.3777 | 36.5977 | 270.0745 | 432.8703 | 419.0371 | 26319.6866 | 3.1283 | 0.036176 | 5.6834 | 81.9932 | 465.998 | 30 | 55 | 4 | 49 | 770.1963 | 1491.5141 | 69.7514 | 1.9365 | 0.90999 | 110 | 136.8974 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 28.2091 | 82.2635
CID=-1521662316 | 30 | 57.5 | 94.7442 | 4 | 51.5 | 10.3 | 1.7283 | 145.3777 | 36.5977 | 273.9586 | 434.1168 | 419.0371 | 27325.6625 | 3.3574 | 0.042081 | 5.1411 | 94.7443 | 487.0918 | 30 | 57.5 | 4 | 51.5 | 770.1963 | 1584.4992 | 72.847 | 2.0573 | 0.91422 | 110 | 157.4561 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32.0207 | 95.0594
CID=-1521662219 | 30 | 60 | 104.0155 | 4 | 54 | 10.8 | 1.7283 | 145.3777 | 36.5977 | 277.8855 | 435.3393 | 419.0371 | 28024.5604 | 3.5035 | 0.046942 | 4.7543 | 104.0155 | 494.5207 | 30 | 60 | 4 | 54 | 770.1963 | 1681.7842 | 75.5299 | 2.1836 | 0.91612 | 110 | 172.5052 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 36.1156 | 104.3567
CID=-1521662122 | 30 | 62.5 | 118.2301 | 4 | 56.5 | 11.3 | 1.7283 | 145.3777 | 36.5977 | 281.8586 | 436.5383 | 419.0371 | 28953.8798 | 3.7228 | 0.054125 | 4.3194 | 118.2301 | 510.6855 | 30 | 62.5 | 4 | 56.5 | 770.1963 | 1783.5096 | 78.686 | 2.3157 | 0.91789 | 110 | 195.7004 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 41.2449 | 118.617
CID=-1521662281 | 30 | 65 | 126.5619 | 4 | 59 | 11.8 | 1.7283 | 145.3777 | 36.5977 | 285.881 | 437.7139 | 419.0371 | 29495.1048 | 3.832 | 0.059277 | 4.0316 | 126.5619 | 510.2477 | 30 | 65 | 4 | 59 | 770.1963 | 1889.8218 | 81.2497 | 2.4537 | 0.91853 | 110 | 209.3469 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 47.3217 | 126.9601
CID=-1521662440 | 30 | 67.5 | 126.5892 | 4 | 61.5 | 12.3 | 1.7283 | 145.3777 | 36.5977 | 289.9569 | 438.8665 | 419.0371 | 29571.4424 | 3.8102 | 0.061161 | 3.8851 | 126.5893 | 491.8164 | 30 | 67.5 | 4 | 61.5 | 770.1963 | 2000.8736 | 83.0593 | 2.5979 | 0.91853 | 110 | 209.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 52.7777 | 126.9602
CID=-1521662343 | 30 | 69.99 | 126.6191 | 4 | 63.99 | 12.798 | 1.7283 | 145.3777 | 36.5977 | 294.074 | 439.9919 | 419.0371 | 29655.4632 | 3.7717 | 0.063189 | 3.7223 | 126.6192 | 471.3171 | 30 | 69.99 | 4 | 63.99 | 770.1963 | 2116.3519 | 85.028 | 2.7478 | 0.91853 | 110 | 209.4408 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 58.743 | 126.9602