## CoilStudioAuslegungVerdampfer4r
2022-10-26 12:13 - Software Version: V. 1.2.0.2
SeqID | Condensing dew point temperature | Evaporating dew point temperature | Air temp. Dry bulb | Air flow | Subcooling | Superheating | Tube spacing | Row spacing | Number tube per row | Finned block height | Nr. of Rows | Finned block depth | Fin spacing | Fins thickness | Fin type | Finned block lenght | Nr. of Circuits | Tube diameter | Tube thickness | Tube internal surface | Internal volume (without manifolds) | Air flow | Air front speed | Air pressure drops | Inlet dry bulb temperature | Inlet wet bulb temperature | Inlet relative humidity | Outlet dry bulb temperature | Outlet wet bulb temperature | Outlet relative humidity | Internal Fluid | Flow configuration | Evaporating dew temperature | Superheating | Condensation temp dewpoint | Subcooling | Flow | Pressure drops | Internal fluid Charge | PS | Total capacity | Latent capacity | Sensible capacity
| °C | °C | °C | m³/h | K | K | mm | mm |  | mm |  | mm | mm | mm |  | mm |  | mm | mm |  | dm³ | m³/h | m/s | Pa | °C | °C | % | °C | °C | % |  |  | °C | K | °C | K | kg/h | kPa | kg | bar | W | W | W
Baseline | 56 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.71 | -15.06 | 15.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 759.6 | 22 | 2.01 | - | 43194 | 0 | 43194
Baseline | 56 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.06 | -13.77 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 637.9 | 14.9 | 2.49 | - | 46339 | 0 | 46339
Baseline | 56 | -16 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.35 | -14.05 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 481.3 | 7.5 | 3.92 | - | 48994 | 0 | 48994
P00001 | 25 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.47 | -19.35 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 383.5 | 5.1 | 2.85 | - | 30875 | 0 | 30875
P00002 | 25 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.78 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 80 | 0.6 | 4.97 | - | 6571 | 0 | 6571
P00003 | 25 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.63 | -16.46 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 137.8 | 1.2 | 3.87 | - | 11272 | 0 | 11272
P00004 | 32.5 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.43 | -19.31 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 409.4 | 6.3 | 2.64 | - | 30617 | 0 | 30617
P00005 | 32.5 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.98 | -15.81 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 89.4 | 0.7 | 4.47 | - | 6775 | 0 | 6775
P00006 | 32.5 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.65 | -16.49 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 150.1 | 1.4 | 3.52 | - | 11424 | 0 | 11424
P00007 | 40 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.32 | -19.2 | 14.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 433.9 | 7.8 | 2.4 | - | 29894 | 0 | 29894
P00008 | 40 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.96 | -15.79 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 94.2 | 0.8 | 4.08 | - | 6642 | 0 | 6642
P00009 | 40 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.62 | -16.46 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 160 | 1.6 | 3.18 | - | 11229 | 0 | 11229
P00010 | 47.5 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.24 | -19.12 | 14.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 467.3 | 10 | 2.22 | - | 29337 | 0 | 29337
P00011 | 47.5 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.78 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 101.8 | 0.9 | 3.68 | - | 6557 | 0 | 6557
P00012 | 47.5 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.6 | -16.43 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 172.2 | 1.8 | 2.87 | - | 11034 | 0 | 11034
P00013 | 55 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.14 | -19.01 | 14.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 506.6 | 12.5 | 2.04 | - | 28594 | 0 | 28594
P00014 | 55 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.94 | -15.77 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 112 | 1 | 3.28 | - | 6504 | 0 | 6504
P00015 | 55 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.57 | -16.4 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 187.7 | 2 | 2.56 | - | 10838 | 0 | 10838
P00016 | 62.5 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -16.98 | -18.85 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 551.9 | 15 | 1.82 | - | 27489 | 0 | 27489
P00017 | 62.5 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.92 | -15.75 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 124.2 | 1.2 | 2.91 | - | 6384 | 0 | 6384
P00018 | 62.5 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.55 | -16.38 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 209.1 | 2.4 | 2.27 | - | 10686 | 0 | 10686
P00019 | 70 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -16.82 | -18.69 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 617.5 | 18.7 | 1.63 | - | 26434 | 0 | 26434
P00020 | 70 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.92 | -15.74 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 142.4 | 1.4 | 2.53 | - | 6326 | 0 | 6326
P00021 | 70 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.51 | -16.34 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 236.1 | 2.9 | 1.99 | - | 10412 | 0 | 10412
P00022 | 56 | -20 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.12 | -19 | 14.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 512.9 | 12.8 | 2.01 | - | 28503 | 0 | 28503
P00023 | 56 | -15 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.94 | -15.77 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 114 | 1.1 | 3.23 | - | 6518 | 0 | 6518
P00024 | 56 | -16 | -13 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.63 | -16.46 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 197.5 | 2.2 | 2.53 | - | 11232 | 0 | 11232
P00025 | 25 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.1 | -18.97 | 14.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 432.1 | 7.2 | 2.75 | - | 34792 | 0 | 34792
P00026 | 25 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.91 | -15.74 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 94.4 | 0.8 | 4.62 | - | 7755 | 0 | 7755
P00027 | 25 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.51 | -16.34 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 156.5 | 1.4 | 3.62 | - | 12805 | 0 | 12805
P00028 | 32.5 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.99 | -18.87 | 14.5 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 453.4 | 8.6 | 2.51 | - | 33913 | 0 | 33913
P00029 | 32.5 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.9 | -15.73 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 100.2 | 0.8 | 4.19 | - | 7657 | 0 | 7657
P00030 | 32.5 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.53 | -16.36 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 170.3 | 1.6 | 3.31 | - | 12954 | 0 | 12954
P00031 | 40 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.92 | -18.8 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 483.8 | 10.7 | 2.34 | - | 33327 | 0 | 33327
P00032 | 40 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.72 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 107.2 | 0.9 | 3.79 | - | 7559 | 0 | 7559
P00033 | 40 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.5 | -16.33 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 181.4 | 1.8 | 2.99 | - | 12728 | 0 | 12728
P00034 | 47.5 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.86 | -18.73 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 521.9 | 12.7 | 2.16 | - | 32768 | 0 | 32768
P00035 | 47.5 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 114.9 | 1 | 3.43 | - | 7398 | 0 | 7398
P00036 | 47.5 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.51 | -16.35 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 200.7 | 2.1 | 2.71 | - | 12857 | 0 | 12857
P00037 | 55 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.75 | -18.62 | 14.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 564.4 | 15 | 1.99 | - | 31853 | 0 | 31853
P00038 | 55 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.9 | -15.73 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 131.3 | 1.2 | 3.04 | - | 7625 | 0 | 7625
P00039 | 55 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.49 | -16.32 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 218.7 | 2.5 | 2.43 | - | 12625 | 0 | 12625
P00040 | 62.5 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.58 | -18.45 | 13.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 610.8 | 17.8 | 1.78 | - | 30424 | 0 | 30424
P00041 | 62.5 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.71 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 146.5 | 1.5 | 2.69 | - | 7533 | 0 | 7533
P00042 | 62.5 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.46 | -16.29 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 242.1 | 2.9 | 2.15 | - | 12371 | 0 | 12371
P00043 | 70 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.41 | -18.27 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 677 | 21.9 | 1.61 | - | 28981 | 0 | 28981
P00044 | 70 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.84 | -15.67 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 160.5 | 1.7 | 2.36 | - | 7128 | 0 | 7128
P00045 | 70 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.42 | -16.25 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 273.5 | 3.6 | 1.89 | - | 12062 | 0 | 12062
P00046 | 56 | -20 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.74 | -18.6 | 14.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 570.9 | 15.4 | 1.96 | - | 31731 | 0 | 31731
P00047 | 56 | -15 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 128.1 | 1.2 | 3.02 | - | 7325 | 0 | 7325
P00048 | 56 | -16 | -13 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.49 | -16.32 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 222.3 | 2.5 | 2.39 | - | 12639 | 0 | 12639
P00049 | 25 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.77 | -18.64 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 474 | 9.4 | 2.69 | - | 38166 | 0 | 38166
P00050 | 25 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 104.9 | 0.9 | 4.36 | - | 8619 | 0 | 8619
P00051 | 25 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.45 | -16.28 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 179.3 | 1.7 | 3.47 | - | 14671 | 0 | 14671
P00052 | 32.5 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.67 | -18.53 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 496 | 11 | 2.47 | - | 37097 | 0 | 37097
P00053 | 32.5 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.84 | -15.67 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 111.4 | 1 | 3.95 | - | 8508 | 0 | 8508
P00054 | 32.5 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.42 | -16.25 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 189 | 1.9 | 3.14 | - | 14380 | 0 | 14380
P00055 | 40 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.6 | -18.47 | 13.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 529.2 | 12.7 | 2.29 | - | 36461 | 0 | 36461
P00056 | 40 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.82 | -15.65 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 118.2 | 1.1 | 3.58 | - | 8333 | 0 | 8333
P00057 | 40 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.44 | -16.27 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 207.6 | 2.2 | 2.87 | - | 14568 | 0 | 14568
P00058 | 47.5 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.51 | -18.37 | 13.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 565.7 | 14.6 | 2.13 | - | 35515 | 0 | 35515
P00059 | 47.5 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 133.3 | 1.2 | 3.21 | - | 8583 | 0 | 8583
P00060 | 47.5 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.42 | -16.25 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 223.7 | 2.5 | 2.58 | - | 14336 | 0 | 14336
P00061 | 55 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.32 | -18.18 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 594.9 | 16.7 | 1.89 | - | 33576 | 0 | 33576
P00062 | 55 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.83 | -15.66 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 146.2 | 1.4 | 2.87 | - | 8439 | 0 | 8439
P00063 | 55 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.38 | -16.21 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 242.4 | 2.8 | 2.31 | - | 13995 | 0 | 13995
P00064 | 62.5 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.25 | -18.11 | 13.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 661.2 | 20.4 | 1.75 | - | 32932 | 0 | 32932
P00065 | 62.5 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.82 | -15.64 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 160.9 | 1.6 | 2.55 | - | 8271 | 0 | 8271
P00066 | 62.5 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.35 | -16.18 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 266.5 | 3.3 | 2.06 | - | 13616 | 0 | 13616
P00067 | 70 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.08 | -17.94 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 727.7 | 24.8 | 1.59 | - | 31185 | 0 | 31185
P00068 | 70 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 182.8 | 2 | 2.23 | - | 8121 | 0 | 8121
P00069 | 70 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.31 | -16.14 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 300.5 | 4.1 | 1.81 | - | 13254 | 0 | 13254
P00070 | 56 | -20 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.31 | -18.17 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 603.3 | 17.2 | 1.87 | - | 33530 | 0 | 33530
P00071 | 56 | -15 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.84 | -15.67 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 148.5 | 1.5 | 2.82 | - | 8495 | 0 | 8495
P00072 | 56 | -16 | -13 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.38 | -16.22 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 246.3 | 2.9 | 2.28 | - | 14007 | 0 | 14007
P00073 | 25 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.44 | -18.3 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 501.8 | 10.9 | 2.61 | - | 40403 | 0 | 40403
P00074 | 25 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 114.3 | 1 | 4.16 | - | 9385 | 0 | 9385
P00075 | 25 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.36 | -16.19 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 195.6 | 1.9 | 3.33 | - | 16001 | 0 | 16001
P00076 | 32.5 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.39 | -18.25 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 532.8 | 12.5 | 2.43 | - | 39852 | 0 | 39852
P00077 | 32.5 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.79 | -15.62 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 121.5 | 1.1 | 3.76 | - | 9287 | 0 | 9287
P00078 | 32.5 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.34 | -16.17 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 206.4 | 2.1 | 3.03 | - | 15702 | 0 | 15702
P00079 | 40 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.33 | -18.19 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 567.5 | 14.3 | 2.25 | - | 39099 | 0 | 39099
P00080 | 40 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 133.9 | 1.2 | 3.42 | - | 9439 | 0 | 9439
P00081 | 40 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.35 | -16.18 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 225.7 | 2.4 | 2.76 | - | 15843 | 0 | 15843
P00082 | 47.5 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.19 | -18.05 | 13.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 596.7 | 16.2 | 2.06 | - | 37464 | 0 | 37464
P00083 | 47.5 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.76 | -15.59 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 138.4 | 1.3 | 3.09 | - | 8910 | 0 | 8910
P00084 | 47.5 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.32 | -16.15 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 242.3 | 2.8 | 2.5 | - | 15524 | 0 | 15524
P00085 | 55 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.1 | -17.96 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 646.3 | 19.1 | 1.9 | - | 36478 | 0 | 36478
P00086 | 55 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.75 | -15.57 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 151.3 | 1.5 | 2.77 | - | 8784 | 0 | 8784
P00087 | 55 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.33 | -16.16 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 270.5 | 3.3 | 2.26 | - | 15617 | 0 | 15617
P00088 | 62.5 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -15.95 | -17.8 | 13.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 695.8 | 22.5 | 1.7 | - | 34657 | 0 | 34657
P00089 | 62.5 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.73 | -15.56 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 167.5 | 1.7 | 2.46 | - | 8613 | 0 | 8613
P00090 | 62.5 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.29 | -16.12 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 297.6 | 3.9 | 2.01 | - | 15207 | 0 | 15207
P00091 | 70 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -15.78 | -17.63 | 12.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 762.4 | 27 | 1.55 | - | 32638 | 0 | 32638
P00092 | 70 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.72 | -15.54 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 189.2 | 2.1 | 2.15 | - | 8403 | 0 | 8403
P00093 | 70 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.26 | -16.09 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 336.6 | 4.8 | 1.75 | - | 14843 | 0 | 14843
P00094 | 56 | -20 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.09 | -17.94 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 653.3 | 19.5 | 1.88 | - | 36309 | 0 | 36309
P00095 | 56 | -15 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.75 | -15.58 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 153.7 | 1.5 | 2.73 | - | 8790 | 0 | 8790
P00096 | 56 | -16 | -13 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.29 | -16.12 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 266.7 | 3.3 | 2.21 | - | 15168 | 0 | 15168
P00097 | 25 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.23 | -18.09 | 13.5 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 534.9 | 12.2 | 2.56 | - | 43073 | 0 | 43073
P00098 | 25 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 129.6 | 1.1 | 4.07 | - | 10647 | 0 | 10647
P00099 | 25 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.29 | -16.12 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 210.5 | 2.1 | 3.23 | - | 17220 | 0 | 17220
P00100 | 32.5 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.16 | -18.02 | 13.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 563.6 | 13.7 | 2.4 | - | 42156 | 0 | 42156
P00101 | 32.5 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.74 | -15.57 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 129.8 | 1.1 | 3.64 | - | 9921 | 0 | 9921
P00102 | 32.5 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.3 | -16.13 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 228.2 | 2.4 | 2.96 | - | 17361 | 0 | 17361
P00103 | 40 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.1 | -17.96 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 600.3 | 15.7 | 2.24 | - | 41359 | 0 | 41359
P00104 | 40 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.73 | -15.56 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 138.3 | 1.3 | 3.29 | - | 9752 | 0 | 9752
P00105 | 40 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.28 | -16.11 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 242.5 | 2.7 | 2.68 | - | 17016 | 0 | 17016
P00106 | 47.5 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.03 | -17.88 | 13.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 642.8 | 18.2 | 2.07 | - | 40360 | 0 | 40360
P00107 | 47.5 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.72 | -15.54 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 148.1 | 1.4 | 2.98 | - | 9540 | 0 | 9540
P00108 | 47.5 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.29 | -16.12 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 267.5 | 3.1 | 2.44 | - | 17140 | 0 | 17140
P00109 | 55 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -15.88 | -17.73 | 13 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 680.8 | 20.9 | 1.88 | - | 38425 | 0 | 38425
P00110 | 55 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.73 | -15.56 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 168.7 | 1.7 | 2.66 | - | 9795 | 0 | 9795
P00111 | 55 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.25 | -16.08 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 289.4 | 3.6 | 2.19 | - | 16710 | 0 | 16710
P00112 | 62.5 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -15.72 | -17.57 | 12.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 727.7 | 24.3 | 1.69 | - | 36300 | 0 | 36300
P00113 | 62.5 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.72 | -15.54 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 185.9 | 2 | 2.36 | - | 9558 | 0 | 9558
P00114 | 62.5 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.23 | -16.06 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 320 | 4.3 | 1.94 | - | 16350 | 0 | 16350
P00115 | 70 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -15.56 | -17.4 | 12.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 795.7 | 29 | 1.55 | - | 34063 | 0 | 34063
P00116 | 70 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.7 | -15.53 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 210.9 | 2.4 | 2.07 | - | 9367 | 0 | 9367
P00117 | 70 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.14 | -15.97 | 11.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 343.8 | 5 | 1.71 | - | 15160 | 0 | 15160
P00118 | 56 | -20 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -15.87 | -17.73 | 13 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 689.5 | 21.4 | 1.85 | - | 38321 | 0 | 38321
P00119 | 56 | -15 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.7 | -15.53 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 164.1 | 1.7 | 2.63 | - | 9382 | 0 | 9382
P00120 | 56 | -16 | -13 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.26 | -16.09 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 296.1 | 3.8 | 2.15 | - | 16836 | 0 | 16836
P00121 | 25 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.84 | -18.71 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 447.9 | 8.1 | 2.68 | - | 36067 | 0 | 36067
P00122 | 25 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.88 | -15.71 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 100.4 | 0.8 | 4.47 | - | 8243 | 0 | 8243
P00123 | 25 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.49 | -16.33 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 171.4 | 1.6 | 3.55 | - | 14018 | 0 | 14018
P00124 | 32.5 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.82 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 478.6 | 10.1 | 2.48 | - | 35800 | 0 | 35800
P00125 | 32.5 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 106.1 | 0.9 | 4.05 | - | 8104 | 0 | 8104
P00126 | 32.5 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.47 | -16.3 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 181.1 | 1.8 | 3.21 | - | 13782 | 0 | 13782
P00127 | 40 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.74 | -18.6 | 14.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 508.8 | 11.8 | 2.31 | - | 35051 | 0 | 35051
P00128 | 40 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 113.2 | 1 | 3.67 | - | 7983 | 0 | 7983
P00129 | 40 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.44 | -16.27 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 192.7 | 2 | 2.91 | - | 13521 | 0 | 13521
P00130 | 47.5 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.61 | -18.47 | 13.9 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 539.4 | 13.6 | 2.1 | - | 33867 | 0 | 33867
P00131 | 47.5 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 126.8 | 1.2 | 3.3 | - | 8163 | 0 | 8163
P00132 | 47.5 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.46 | -16.29 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 213.4 | 2.3 | 2.64 | - | 13672 | 0 | 13672
P00133 | 55 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.5 | -18.36 | 13.8 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 581.9 | 15.9 | 1.94 | - | 32842 | 0 | 32842
P00134 | 55 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 138.8 | 1.3 | 2.95 | - | 8057 | 0 | 8057
P00135 | 55 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.43 | -16.26 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 231.8 | 2.7 | 2.36 | - | 13379 | 0 | 13379
P00136 | 62.5 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.39 | -18.25 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 638.6 | 19.2 | 1.77 | - | 31810 | 0 | 31810
P00137 | 62.5 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 154.7 | 1.6 | 2.61 | - | 7954 | 0 | 7954
P00138 | 62.5 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.4 | -16.23 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 257.1 | 3.2 | 2.09 | - | 13140 | 0 | 13140
P00139 | 70 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.19 | -18.05 | 13.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 699.3 | 23.3 | 1.57 | - | 29936 | 0 | 29936
P00140 | 70 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.83 | -15.66 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 177.1 | 1.9 | 2.27 | - | 7824 | 0 | 7824
P00141 | 70 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.35 | -16.19 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 288.1 | 3.8 | 1.84 | - | 12704 | 0 | 12704
P00142 | 56 | -20 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.51 | -18.38 | 13.8 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 593 | 16.5 | 1.91 | - | 32955 | 0 | 32955
P00143 | 56 | -15 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 141.3 | 1.4 | 2.9 | - | 8080 | 0 | 8080
P00144 | 56 | -16 | -13 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.43 | -16.26 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 235.4 | 2.7 | 2.33 | - | 13389 | 0 | 13389
P00145 | 25 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.93 | -16.62 | 22.2 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 745.7 | 19.8 | 2.75 | - | 60040 | 0 | 60040
P00146 | 25 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.95 | -15.34 | 16.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 487 | 8.5 | 3.04 | - | 39995 | 0 | 39995
P00147 | 25 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.45 | -11.56 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 197.1 | 1.5 | 3.97 | - | 16502 | 0 | 16502
P00148 | 25 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.58 | -14.25 | 17.9 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 540.8 | 10.4 | 2.95 | - | 44244 | 0 | 44244
P00149 | 32.5 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.73 | -16.42 | 21.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 784.7 | 22.6 | 2.53 | - | 58694 | 0 | 58694
P00150 | 32.5 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.82 | -15.14 | 16.7 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 512.2 | 9.6 | 2.78 | - | 39134 | 0 | 39134
P00151 | 32.5 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.41 | -11.52 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 207.6 | 1.7 | 3.59 | - | 16192 | 0 | 16192
P00152 | 32.5 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.52 | -14.2 | 17.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 576.4 | 12 | 2.73 | - | 43852 | 0 | 43852
P00153 | 40 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.57 | -16.26 | 21.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 836.4 | 26.2 | 2.35 | - | 57624 | 0 | 57624
P00154 | 40 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.76 | -15.05 | 16.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 549.4 | 11.3 | 2.57 | - | 38736 | 0 | 38736
P00155 | 40 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.43 | -11.54 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 226.8 | 1.9 | 3.26 | - | 16354 | 0 | 16354
P00156 | 40 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.42 | -14.1 | 17.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 615.2 | 13.9 | 2.53 | - | 43177 | 0 | 43177
P00157 | 47.5 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.35 | -16.03 | 21 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 894.1 | 30.4 | 2.18 | - | 56136 | 0 | 56136
P00158 | 47.5 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.69 | -14.94 | 16.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 594 | 13.3 | 2.36 | - | 38248 | 0 | 38248
P00159 | 47.5 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.46 | -11.56 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 250.2 | 2.3 | 2.96 | - | 16510 | 0 | 16510
P00160 | 47.5 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.31 | -13.99 | 17.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 662.4 | 16.4 | 2.33 | - | 42441 | 0 | 42441
P00161 | 55 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.03 | -15.71 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 956.9 | 35.6 | 1.99 | - | 54009 | 0 | 54009
P00162 | 55 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.53 | -14.72 | 16.3 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 640.5 | 15.8 | 2.13 | - | 37182 | 0 | 37182
P00163 | 55 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.41 | -11.52 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 272.2 | 2.6 | 2.65 | - | 16235 | 0 | 16235
P00164 | 55 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.13 | -13.81 | 17.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 714.3 | 19.5 | 2.11 | - | 41235 | 0 | 41235
P00165 | 62.5 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -13.8 | -15.48 | 20 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1053.5 | 43.1 | 1.85 | - | 52472 | 0 | 52472
P00166 | 62.5 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.4 | -14.55 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 706.9 | 19.4 | 1.94 | - | 36345 | 0 | 36345
P00167 | 62.5 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.43 | -11.53 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 308.1 | 3.2 | 2.37 | - | 16332 | 0 | 16332
P00168 | 62.5 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.95 | -15.34 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 782.8 | 23.6 | 1.93 | - | 39998 | 0 | 39998
P00169 | 70 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -13.32 | -15 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1150.4 | 52.1 | 1.66 | - | 49251 | 0 | 49251
P00170 | 70 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.15 | -14.15 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 779.8 | 23.9 | 1.73 | - | 34638 | 0 | 34638
P00171 | 70 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.38 | -11.49 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 347.8 | 4.1 | 2.07 | - | 16002 | 0 | 16002
P00172 | 70 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.66 | -14.91 | 16.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 863.6 | 29.1 | 1.71 | - | 38083 | 0 | 38083
P00173 | 56 | -20 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14 | -15.68 | 20.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 968.1 | 36.5 | 1.97 | - | 53802 | 0 | 53802
P00174 | 56 | -15 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.51 | -14.7 | 16.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 648.4 | 16.3 | 2.11 | - | 37081 | 0 | 37081
P00175 | 56 | -10 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.42 | -11.52 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 276.4 | 2.7 | 2.61 | - | 16244 | 0 | 16244
P00176 | 56 | -16 | -6 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.11 | -13.79 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 722.8 | 20 | 2.08 | - | 41104 | 0 | 41104
P00177 | 25 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.14 | -15.82 | 20.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 835.6 | 24.1 | 2.69 | - | 67281 | 0 | 67281
P00178 | 25 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.4 | -14.54 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 543.3 | 10.3 | 2.9 | - | 44624 | 0 | 44624
P00179 | 25 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.23 | -11.37 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 220.1 | 1.8 | 3.69 | - | 18425 | 0 | 18425
P00180 | 25 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.05 | -13.73 | 17 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 611.4 | 12.9 | 2.85 | - | 50020 | 0 | 50020
P00181 | 32.5 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.94 | -15.62 | 20.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 876.9 | 27.4 | 2.48 | - | 65588 | 0 | 65588
P00182 | 32.5 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.35 | -14.48 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 578.4 | 11.9 | 2.69 | - | 44189 | 0 | 44189
P00183 | 32.5 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.25 | -11.39 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 238.7 | 2 | 3.37 | - | 18617 | 0 | 18617
P00184 | 32.5 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.99 | -15.41 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 650.4 | 14.8 | 2.65 | - | 49488 | 0 | 49488
P00185 | 40 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.78 | -15.46 | 19.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 932.9 | 31.6 | 2.31 | - | 64270 | 0 | 64270
P00186 | 40 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.28 | -14.39 | 15.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 619.2 | 13.9 | 2.49 | - | 43653 | 0 | 43653
P00187 | 40 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.27 | -11.4 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 259.7 | 2.3 | 3.07 | - | 18725 | 0 | 18725
P00188 | 40 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.88 | -15.24 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 692.2 | 17.1 | 2.46 | - | 48578 | 0 | 48578
P00189 | 47.5 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.54 | -15.22 | 19.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 992.7 | 36.3 | 2.16 | - | 62327 | 0 | 62327
P00190 | 47.5 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.15 | -14.15 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 660.8 | 16.2 | 2.27 | - | 42554 | 0 | 42554
P00191 | 47.5 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.22 | -11.36 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 277.6 | 2.6 | 2.78 | - | 18319 | 0 | 18319
P00192 | 47.5 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.71 | -14.98 | 16.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 736.4 | 19.9 | 2.24 | - | 47187 | 0 | 47187
P00193 | 55 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.24 | -14.91 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1059.9 | 42.3 | 1.97 | - | 59822 | 0 | 59822
P00194 | 55 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.04 | -14.04 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 716.9 | 19.3 | 2.08 | - | 41616 | 0 | 41616
P00195 | 55 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.24 | -11.37 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 310.3 | 3.2 | 2.51 | - | 18507 | 0 | 18507
P00196 | 55 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.58 | -14.79 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 798.3 | 23.6 | 2.06 | - | 46088 | 0 | 46088
P00197 | 62.5 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.98 | -14.65 | 18.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1157.9 | 50.5 | 1.84 | - | 57673 | 0 | 57673
P00198 | 62.5 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -10.88 | -13.88 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 784.4 | 23.3 | 1.9 | - | 40335 | 0 | 40335
P00199 | 62.5 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.2 | -11.34 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 342.7 | 3.9 | 2.23 | - | 18165 | 0 | 18165
P00200 | 62.5 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.38 | -14.52 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 870 | 28.3 | 1.89 | - | 44456 | 0 | 44456
P00201 | 70 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.52 | -14.2 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1258.1 | 60.4 | 1.66 | - | 53860 | 0 | 53860
P00202 | 70 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -10.63 | -13.63 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 861.8 | 28.5 | 1.69 | - | 38283 | 0 | 38283
P00203 | 70 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.18 | -11.32 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 390.7 | 5.7 | 1.98 | - | 17979 | 0 | 17979
P00204 | 70 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.09 | -14.09 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 954.4 | 34.6 | 1.69 | - | 42089 | 0 | 42089
P00205 | 56 | -20 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.21 | -14.88 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1071.7 | 43.3 | 1.95 | - | 59560 | 0 | 59560
P00206 | 56 | -15 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.02 | -14.02 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 725.5 | 19.8 | 2.06 | - | 41491 | 0 | 41491
P00207 | 56 | -10 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.24 | -11.38 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 315 | 3.3 | 2.47 | - | 18516 | 0 | 18516
P00208 | 56 | -16 | -6 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.56 | -14.76 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 807.6 | 24.2 | 2.04 | - | 45924 | 0 | 45924
P00209 | 25 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.47 | -15.15 | 19.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 913.9 | 28.1 | 2.66 | - | 73588 | 0 | 73588
P00210 | 25 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.02 | -14.02 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 602 | 12.4 | 2.82 | - | 49441 | 0 | 49441
P00211 | 25 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.13 | -11.28 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 250.5 | 2.1 | 3.56 | - | 20975 | 0 | 20975
P00212 | 25 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.59 | -14.81 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 673.4 | 15.2 | 2.79 | - | 55094 | 0 | 55094
P00213 | 32.5 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.27 | -14.95 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 957.7 | 31.8 | 2.46 | - | 71628 | 0 | 71628
P00214 | 32.5 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.93 | -13.93 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 636 | 14.1 | 2.63 | - | 48595 | 0 | 48595
P00215 | 32.5 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.09 | -11.25 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 264.4 | 2.3 | 3.22 | - | 20619 | 0 | 20619
P00216 | 32.5 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.52 | -14.71 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 715 | 17.5 | 2.59 | - | 54399 | 0 | 54399
P00217 | 40 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.11 | -14.79 | 18.8 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1016.9 | 36.5 | 2.29 | - | 70055 | 0 | 70055
P00218 | 40 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.88 | -13.88 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 681 | 16.4 | 2.43 | - | 48014 | 0 | 48014
P00219 | 40 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.11 | -11.27 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 288.5 | 2.7 | 2.94 | - | 20800 | 0 | 20800
P00220 | 40 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.35 | -14.47 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 750 | 19.8 | 2.39 | - | 52636 | 0 | 52636
P00221 | 47.5 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -12.89 | -14.57 | 18.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1080.8 | 41.9 | 2.15 | - | 67857 | 0 | 67857
P00222 | 47.5 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.79 | -13.79 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 731.8 | 19.2 | 2.25 | - | 47125 | 0 | 47125
P00223 | 47.5 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.08 | -11.24 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 310.4 | 3.1 | 2.65 | - | 20480 | 0 | 20480
P00224 | 47.5 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 805.2 | 23.2 | 2.21 | - | 51590 | 0 | 51590
P00225 | 55 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -12.58 | -14.26 | 17.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1148.1 | 48.4 | 1.96 | - | 64801 | 0 | 64801
P00226 | 55 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.62 | -13.62 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 782.9 | 22.5 | 2.04 | - | 45445 | 0 | 45445
P00227 | 55 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.04 | -11.21 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 336.8 | 3.6 | 2.38 | - | 20088 | 0 | 20088
P00228 | 55 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.1 | -14.1 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 870.1 | 27.4 | 2.04 | - | 50234 | 0 | 50234
P00229 | 62.5 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -12.31 | -13.99 | 17.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1247.3 | 57 | 1.84 | - | 62124 | 0 | 62124
P00230 | 62.5 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.46 | -13.46 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 853.2 | 26.9 | 1.87 | - | 43869 | 0 | 43869
P00231 | 62.5 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.02 | -11.19 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 374.7 | 4.9 | 2.16 | - | 19863 | 0 | 19863
P00232 | 62.5 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.9 | -13.9 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 944.4 | 32.6 | 1.87 | - | 48259 | 0 | 48259
P00233 | 70 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.87 | -15.22 | 16.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1350.6 | 67.9 | 1.65 | - | 57822 | 0 | 57822
P00234 | 70 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.21 | -13.21 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 931.7 | 32.5 | 1.68 | - | 41429 | 0 | 41429
P00235 | 70 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8 | -11.17 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 427.1 | 7.3 | 1.92 | - | 19652 | 0 | 19652
P00236 | 70 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.62 | -13.62 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1031.2 | 39.5 | 1.67 | - | 45478 | 0 | 45478
P00237 | 56 | -20 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -12.54 | -14.22 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1159.3 | 49.5 | 1.94 | - | 64429 | 0 | 64429
P00238 | 56 | -15 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.6 | -13.6 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 791.7 | 23 | 2.02 | - | 45277 | 0 | 45277
P00239 | 56 | -10 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.04 | -11.21 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 341.8 | 3.7 | 2.35 | - | 20091 | 0 | 20091
P00240 | 56 | -16 | -6 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.08 | -14.08 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 879.8 | 28.1 | 2.01 | - | 50032 | 0 | 50032
P00241 | 25 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.83 | -14.51 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 970.3 | 31.5 | 2.6 | - | 78131 | 0 | 78131
P00242 | 25 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.68 | -13.68 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 651.2 | 14.2 | 2.77 | - | 53482 | 0 | 53482
P00243 | 25 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8.01 | -11.18 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 274.2 | 2.3 | 3.43 | - | 22957 | 0 | 22957
P00244 | 25 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.14 | -14.14 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 718 | 17.3 | 2.71 | - | 58739 | 0 | 58739
P00245 | 32.5 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.71 | -14.39 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1025.8 | 35.8 | 2.44 | - | 76722 | 0 | 76722
P00246 | 32.5 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.61 | -13.61 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 690.1 | 16.3 | 2.58 | - | 52730 | 0 | 52730
P00247 | 32.5 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.98 | -11.15 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 289.5 | 2.6 | 3.11 | - | 22577 | 0 | 22577
P00248 | 32.5 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.03 | -14.03 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 756.5 | 19.5 | 2.53 | - | 57555 | 0 | 57555
P00249 | 40 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.55 | -14.23 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1087.5 | 40.9 | 2.28 | - | 74922 | 0 | 74922
P00250 | 40 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.51 | -13.51 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 731.5 | 18.5 | 2.4 | - | 51574 | 0 | 51574
P00251 | 40 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.99 | -11.16 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 315 | 3 | 2.84 | - | 22709 | 0 | 22709
P00252 | 40 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.96 | -13.96 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 807.3 | 22.5 | 2.36 | - | 56658 | 0 | 56658
P00253 | 47.5 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.36 | -14.04 | 17.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1159 | 47.1 | 2.13 | - | 72768 | 0 | 72768
P00254 | 47.5 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.43 | -13.43 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 786.9 | 21.7 | 2.22 | - | 50672 | 0 | 50672
P00255 | 47.5 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.95 | -11.13 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 337.7 | 3.5 | 2.57 | - | 22283 | 0 | 22283
P00256 | 47.5 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.83 | -13.83 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 861.8 | 26.1 | 2.19 | - | 55221 | 0 | 55221
P00257 | 55 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.09 | -13.77 | 17.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1232.8 | 53.9 | 1.99 | - | 69577 | 0 | 69577
P00258 | 55 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.27 | -13.27 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 840.4 | 25.4 | 2.03 | - | 48785 | 0 | 48785
P00259 | 55 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.94 | -11.13 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 372.3 | 4.7 | 2.34 | - | 22206 | 0 | 22206
P00260 | 55 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.64 | -13.64 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 918.7 | 30.3 | 1.99 | - | 53039 | 0 | 53039
P00261 | 62.5 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.7 | -14.96 | 16.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1307.8 | 62 | 1.82 | - | 65141 | 0 | 65141
P00262 | 62.5 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.11 | -13.11 | 14.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 914.5 | 30.3 | 1.85 | - | 47021 | 0 | 47021
P00263 | 62.5 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.88 | -11.08 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 406.1 | 6.2 | 2.09 | - | 21530 | 0 | 21530
P00264 | 62.5 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.52 | -13.52 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1011.9 | 36.7 | 1.86 | - | 51708 | 0 | 51708
P00265 | 70 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.32 | -14.43 | 15.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1419.5 | 73.5 | 1.66 | - | 60769 | 0 | 60769
P00266 | 70 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -9.89 | -12.89 | 14 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1000.7 | 36.6 | 1.69 | - | 44453 | 0 | 44453
P00267 | 70 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.8 | -11.01 | 11.7 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 446 | 8.2 | 1.87 | - | 20523 | 0 | 20523
P00268 | 70 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.23 | -13.23 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1095.3 | 43.7 | 1.67 | - | 48302 | 0 | 48302
P00269 | 56 | -20 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.05 | -13.73 | 17 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1244.3 | 55 | 1.97 | - | 69153 | 0 | 69153
P00270 | 56 | -15 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.24 | -13.24 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 848.2 | 25.9 | 2 | - | 48507 | 0 | 48507
P00271 | 56 | -10 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.94 | -11.13 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 377.4 | 4.9 | 2.31 | - | 22182 | 0 | 22182
P00272 | 56 | -16 | -6 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.62 | -13.62 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 928.5 | 31 | 1.97 | - | 52798 | 0 | 52798
P00273 | 25 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.42 | -14.1 | 17.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1034.1 | 35 | 2.59 | - | 83267 | 0 | 83267
P00274 | 25 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.38 | -13.38 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 691.3 | 15.8 | 2.74 | - | 56778 | 0 | 56778
P00275 | 25 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.91 | -11.1 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 295.4 | 2.6 | 3.32 | - | 24729 | 0 | 24729
P00276 | 25 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.87 | -13.87 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 772.5 | 19.3 | 2.72 | - | 63197 | 0 | 63197
P00277 | 32.5 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.29 | -13.97 | 17.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1091.3 | 39.8 | 2.43 | - | 81627 | 0 | 81627
P00278 | 32.5 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.31 | -13.31 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 732 | 18 | 2.54 | - | 55926 | 0 | 55926
P00279 | 32.5 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.92 | -11.11 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 319.4 | 3 | 3.05 | - | 24910 | 0 | 24910
P00280 | 32.5 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.73 | -13.73 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 807.1 | 21.8 | 2.5 | - | 61404 | 0 | 61404
P00281 | 40 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.1 | -13.78 | 17.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1147.6 | 44.7 | 2.28 | - | 79060 | 0 | 79060
P00282 | 40 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.24 | -13.24 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 780.7 | 20.8 | 2.37 | - | 55044 | 0 | 55044
P00283 | 40 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.89 | -11.08 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 340.2 | 3.4 | 2.76 | - | 24524 | 0 | 24524
P00284 | 40 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.64 | -13.64 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 856.7 | 25 | 2.33 | - | 60127 | 0 | 60127
P00285 | 47.5 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.9 | -15.26 | 16.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1217.9 | 51.1 | 2.13 | - | 76467 | 0 | 76467
P00286 | 47.5 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.15 | -13.15 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 835.2 | 24.1 | 2.2 | - | 53782 | 0 | 53782
P00287 | 47.5 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.89 | -11.08 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 371.1 | 4.5 | 2.53 | - | 24490 | 0 | 24490
P00288 | 47.5 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.53 | -13.53 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 916.6 | 29 | 2.17 | - | 58729 | 0 | 58729
P00289 | 55 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.59 | -14.81 | 16.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1285.2 | 58.2 | 1.96 | - | 72535 | 0 | 72535
P00290 | 55 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.02 | -13.02 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 897 | 28.2 | 2.04 | - | 52068 | 0 | 52068
P00291 | 55 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.82 | -11.03 | 11.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 395.5 | 5.5 | 2.29 | - | 23592 | 0 | 23592
P00292 | 55 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.36 | -13.36 | 14.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 980.2 | 33.6 | 2.01 | - | 56587 | 0 | 56587
P00293 | 62.5 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.27 | -14.37 | 15.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1371.9 | 67.1 | 1.82 | - | 68333 | 0 | 68333
P00294 | 62.5 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -9.81 | -12.81 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 962 | 33 | 1.85 | - | 49463 | 0 | 49463
P00295 | 62.5 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.79 | -11 | 11.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 438.4 | 7.6 | 2.09 | - | 23240 | 0 | 23240
P00296 | 62.5 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.13 | -13.13 | 14.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1049.4 | 39.3 | 1.83 | - | 53620 | 0 | 53620
P00297 | 70 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.89 | -13.89 | 15.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1482.8 | 78.9 | 1.66 | - | 63479 | 0 | 63479
P00298 | 70 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -9.57 | -12.57 | 13.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1041.5 | 39.4 | 1.66 | - | 46263 | 0 | 46263
P00299 | 70 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.72 | -10.95 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 485.6 | 9.4 | 1.84 | - | 22343 | 0 | 22343
P00300 | 70 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -9.91 | -12.91 | 14.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1147.3 | 47.3 | 1.66 | - | 50651 | 0 | 50651
P00301 | 56 | -20 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.55 | -14.75 | 16.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1296.3 | 59.3 | 1.94 | - | 72043 | 0 | 72043
P00302 | 56 | -15 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10 | -13 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 906.3 | 28.8 | 2.02 | - | 51827 | 0 | 51827
P00303 | 56 | -10 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.82 | -11.02 | 11.7 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 400.8 | 5.8 | 2.26 | - | 23557 | 0 | 23557
P00304 | 56 | -16 | -6 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.34 | -13.34 | 14.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 990 | 34.3 | 1.99 | - | 56300 | 0 | 56300
P00305 | 25 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.72 | -15.4 | 19.8 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 875.4 | 26.4 | 2.63 | - | 70490 | 0 | 70490
P00306 | 25 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 582.5 | 11.6 | 2.9 | - | 47842 | 0 | 47842
P00307 | 25 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.19 | -11.33 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 239 | 1.9 | 3.64 | - | 20007 | 0 | 20007
P00308 | 25 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.73 | -15 | 16.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 638.8 | 14.1 | 2.78 | - | 52258 | 0 | 52258
P00309 | 32.5 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.54 | -15.21 | 19.5 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 919.9 | 29.8 | 2.47 | - | 68805 | 0 | 68805
P00310 | 32.5 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.14 | -14.14 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 613.4 | 13.2 | 2.64 | - | 46866 | 0 | 46866
P00311 | 32.5 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.16 | -11.31 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 252.8 | 2.2 | 3.29 | - | 19714 | 0 | 19714
P00312 | 32.5 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.65 | -14.89 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 677.5 | 16.1 | 2.58 | - | 51546 | 0 | 51546
P00313 | 40 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.36 | -15.04 | 19.2 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 975.5 | 34.1 | 2.3 | - | 67207 | 0 | 67207
P00314 | 40 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.06 | -14.06 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 655.3 | 15.3 | 2.45 | - | 46201 | 0 | 46201
P00315 | 40 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.17 | -11.32 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 275.2 | 2.5 | 3 | - | 19837 | 0 | 19837
P00316 | 40 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.56 | -14.76 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 723.2 | 18.6 | 2.4 | - | 50753 | 0 | 50753
P00317 | 47.5 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.19 | -14.87 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1045.4 | 39.6 | 2.14 | - | 65634 | 0 | 65634
P00318 | 47.5 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.98 | -13.98 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 705.9 | 18 | 2.27 | - | 45459 | 0 | 45459
P00319 | 47.5 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.14 | -11.29 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 295.8 | 2.9 | 2.71 | - | 19522 | 0 | 19522
P00320 | 47.5 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.44 | -14.59 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 774.3 | 21.7 | 2.23 | - | 49613 | 0 | 49613
P00321 | 55 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -12.92 | -14.6 | 18.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1119.4 | 46 | 1.99 | - | 63178 | 0 | 63178
P00322 | 55 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.85 | -13.85 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 762.1 | 21.3 | 2.09 | - | 44243 | 0 | 44243
P00323 | 55 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.16 | -11.3 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 329.8 | 3.5 | 2.44 | - | 19673 | 0 | 19673
P00324 | 55 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 828.2 | 25.4 | 2.02 | - | 47813 | 0 | 47813
P00325 | 62.5 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -12.55 | -14.23 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1200.1 | 54 | 1.81 | - | 59776 | 0 | 59776
P00326 | 62.5 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.65 | -13.65 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 824.5 | 25.4 | 1.88 | - | 42394 | 0 | 42394
P00327 | 62.5 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.09 | -11.25 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 360.5 | 4.4 | 2.19 | - | 19108 | 0 | 19108
P00328 | 62.5 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.07 | -14.07 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 904.8 | 30.5 | 1.85 | - | 46235 | 0 | 46235
P00329 | 70 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -12.13 | -13.81 | 17.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1307 | 64.2 | 1.66 | - | 55955 | 0 | 55955
P00330 | 70 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.43 | -13.43 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 911.1 | 31.1 | 1.71 | - | 40472 | 0 | 40472
P00331 | 70 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.02 | -11.19 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 400 | 6.1 | 1.94 | - | 18406 | 0 | 18406
P00332 | 70 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.8 | -13.8 | 15.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 993.8 | 37.1 | 1.68 | - | 43828 | 0 | 43828
P00333 | 56 | -20 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -12.88 | -14.56 | 18.4 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1130.6 | 47 | 1.97 | - | 62835 | 0 | 62835
P00334 | 56 | -15 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.83 | -13.83 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 770.8 | 21.8 | 2.07 | - | 44081 | 0 | 44081
P00335 | 56 | -10 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.15 | -11.3 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 334.3 | 3.6 | 2.42 | - | 19648 | 0 | 19648
P00336 | 56 | -16 | -6 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.22 | -14.22 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 837.3 | 26 | 2 | - | 47617 | 0 | 47617
P00337 | 25 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.21 | -13.64 | 30.9 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1075 | 35.9 | 2.73 | - | 86560 | 0 | 86560
P00338 | 25 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.58 | -12.16 | 24.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 843.9 | 20.8 | 2.9 | - | 69313 | 0 | 69313
P00339 | 25 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.47 | -9.61 | 18.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 584.2 | 9.8 | 3.21 | - | 48913 | 0 | 48913
P00340 | 25 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3.03 | -7.15 | 13.9 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 309.8 | 2.2 | 3.96 | - | 26420 | 0 | 26420
P00341 | 25 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 29.3 | 0.1 | 10.56 | - | 2543 | 0 | 2543
P00342 | 25 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.15 | -12.69 | 25.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 892.9 | 23.5 | 2.86 | - | 73047 | 0 | 73047
P00343 | 32.5 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.02 | -13.45 | 30.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1140.6 | 41.1 | 2.56 | - | 85307 | 0 | 85307
P00344 | 32.5 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.45 | -12.04 | 24.1 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 896.4 | 24 | 2.7 | - | 68487 | 0 | 68487
P00345 | 32.5 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.42 | -9.57 | 18.5 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 622.8 | 11.3 | 2.96 | - | 48574 | 0 | 48574
P00346 | 32.5 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 329.1 | 2.5 | 3.56 | - | 26182 | 0 | 26182
P00347 | 32.5 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 31.2 | 0.2 | 9.87 | - | 2530 | 0 | 2530
P00348 | 32.5 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.96 | -12.51 | 25.2 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 943.9 | 26.9 | 2.67 | - | 71820 | 0 | 71820
P00349 | 40 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -11.75 | -14.42 | 29.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1212.8 | 47.5 | 2.38 | - | 83551 | 0 | 83551
P00350 | 40 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.26 | -11.87 | 23.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 953 | 27.7 | 2.52 | - | 67190 | 0 | 67190
P00351 | 40 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.36 | -9.53 | 18.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 668.8 | 13.3 | 2.73 | - | 48220 | 0 | 48220
P00352 | 40 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 355.3 | 3.3 | 3.25 | - | 26174 | 0 | 26174
P00353 | 40 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.59 | -4.75 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 36.1 | 0.2 | 8.95 | - | 2712 | 0 | 2712
P00354 | 40 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.77 | -12.33 | 24.8 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1005.4 | 31.2 | 2.49 | - | 70559 | 0 | 70559
P00355 | 47.5 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -11.38 | -13.98 | 28.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1291.9 | 54.7 | 2.23 | - | 81110 | 0 | 81110
P00356 | 47.5 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.07 | -11.7 | 23.3 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1023.9 | 32.6 | 2.34 | - | 65937 | 0 | 65937
P00357 | 47.5 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.27 | -9.46 | 18.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 721.8 | 15.8 | 2.52 | - | 47627 | 0 | 47627
P00358 | 47.5 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.99 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 386.6 | 4.3 | 2.97 | - | 26115 | 0 | 26115
P00359 | 47.5 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.56 | -4.76 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 41.7 | 0.2 | 8.07 | - | 2879 | 0 | 2879
P00360 | 47.5 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.53 | -12.11 | 24.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1076.2 | 36.7 | 2.28 | - | 68957 | 0 | 68957
P00361 | 55 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.9 | -13.45 | 27.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1381.5 | 64.1 | 2.04 | - | 77973 | 0 | 77973
P00362 | 55 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -8.78 | -11.45 | 22.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1103.1 | 38.8 | 2.13 | - | 64035 | 0 | 64035
P00363 | 55 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.08 | -9.32 | 18 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 777.7 | 18.8 | 2.28 | - | 46384 | 0 | 46384
P00364 | 55 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.96 | -7.1 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 423.5 | 5.8 | 2.7 | - | 25921 | 0 | 25921
P00365 | 55 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.58 | -4.75 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 43.4 | 0.2 | 7.5 | - | 2725 | 0 | 2725
P00366 | 55 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.26 | -11.87 | 23.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1163.9 | 43.6 | 2.1 | - | 67190 | 0 | 67190
P00367 | 62.5 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.36 | -12.9 | 26.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1494.7 | 75.6 | 1.89 | - | 74447 | 0 | 74447
P00368 | 62.5 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -8.44 | -11.16 | 22.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1202 | 46.6 | 1.96 | - | 61807 | 0 | 61807
P00369 | 62.5 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -5.92 | -9.2 | 17.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 854.8 | 23 | 2.08 | - | 45314 | 0 | 45314
P00370 | 62.5 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.89 | -7.05 | 13.7 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 466.9 | 7.2 | 2.41 | - | 25484 | 0 | 25484
P00371 | 62.5 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.58 | -4.75 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 48.4 | 0.3 | 6.77 | - | 2746 | 0 | 2746
P00372 | 62.5 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -8.87 | -11.53 | 22.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1264.7 | 52.1 | 1.94 | - | 64622 | 0 | 64622
P00373 | 70 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.68 | -12.25 | 24.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1634.7 | 90.8 | 1.73 | - | 69984 | 0 | 69984
P00374 | 70 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -7.96 | -10.77 | 21.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1321.6 | 57.3 | 1.75 | - | 58705 | 0 | 58705
P00375 | 70 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -5.72 | -9.05 | 17.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 956.7 | 29 | 1.87 | - | 44020 | 0 | 44020
P00376 | 70 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.84 | -7.02 | 13.6 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 528.1 | 9.2 | 2.15 | - | 25130 | 0 | 25130
P00377 | 70 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.6 | -4.74 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 52.8 | 0.3 | 6.14 | - | 2592 | 0 | 2592
P00378 | 70 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -8.38 | -11.12 | 22 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1393.7 | 63.8 | 1.77 | - | 61463 | 0 | 61463
P00379 | 56 | -20 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.84 | -13.38 | 27.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1396.1 | 65.6 | 2.02 | - | 77589 | 0 | 77589
P00380 | 56 | -15 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -8.74 | -11.42 | 22.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1115.8 | 39.7 | 2.1 | - | 63808 | 0 | 63808
P00381 | 56 | -10 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.06 | -9.31 | 17.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 787.2 | 19.3 | 2.26 | - | 46270 | 0 | 46270
P00382 | 56 | -5 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.96 | -7.1 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 429.3 | 6 | 2.66 | - | 25907 | 0 | 25907
P00383 | 56 | 0 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.58 | -4.75 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 43.9 | 0.2 | 7.42 | - | 2745 | 0 | 2745
P00384 | 56 | -16 | 1 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.22 | -11.83 | 23.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1177 | 44.7 | 2.08 | - | 66930 | 0 | 66930
P00385 | 25 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.06 | -13.62 | 27.8 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1206.1 | 43.6 | 2.7 | - | 97114 | 0 | 97114
P00386 | 25 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.7 | -11.39 | 22.6 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 950.7 | 25.6 | 2.85 | - | 78077 | 0 | 78077
P00387 | 25 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.91 | -9.19 | 17.7 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 663.7 | 12.2 | 3.1 | - | 55570 | 0 | 55570
P00388 | 25 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.72 | -6.93 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 350.5 | 2.9 | 3.7 | - | 29894 | 0 | 29894
P00389 | 25 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.64 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 32.9 | 0.2 | 10.01 | - | 2858 | 0 | 2858
P00390 | 25 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.25 | -11.86 | 23.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1008.6 | 29.1 | 2.81 | - | 82516 | 0 | 82516
P00391 | 32.5 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.85 | -13.39 | 27.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1275 | 49.8 | 2.52 | - | 95365 | 0 | 95365
P00392 | 32.5 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.52 | -11.24 | 22.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1003 | 29.1 | 2.67 | - | 76636 | 0 | 76636
P00393 | 32.5 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.86 | -9.16 | 17.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 707.5 | 14.2 | 2.87 | - | 55182 | 0 | 55182
P00394 | 32.5 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.71 | -6.93 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 375.5 | 3.7 | 3.38 | - | 29881 | 0 | 29881
P00395 | 32.5 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.64 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 35.3 | 0.2 | 9.29 | - | 2864 | 0 | 2864
P00396 | 32.5 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.05 | -11.69 | 23.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1063.4 | 33 | 2.63 | - | 80910 | 0 | 80910
P00397 | 40 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.58 | -13.11 | 26.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1352.6 | 57 | 2.37 | - | 93186 | 0 | 93186
P00398 | 40 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.38 | -11.12 | 21.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1070.8 | 33.9 | 2.48 | - | 75497 | 0 | 75497
P00399 | 40 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.78 | -9.09 | 17.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 756.3 | 16.5 | 2.65 | - | 54524 | 0 | 54524
P00400 | 40 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.71 | -6.93 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 404.7 | 4.8 | 3.1 | - | 29815 | 0 | 29815
P00401 | 40 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.64 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 38 | 0.2 | 8.61 | - | 2857 | 0 | 2857
P00402 | 40 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.86 | -11.52 | 22.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1130.2 | 38.1 | 2.45 | - | 79324 | 0 | 79324
P00403 | 47.5 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.19 | -12.73 | 25.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1434.4 | 65 | 2.22 | - | 90061 | 0 | 90061
P00404 | 47.5 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.13 | -10.91 | 21.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1140.8 | 39.5 | 2.28 | - | 73463 | 0 | 73463
P00405 | 47.5 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.68 | -9.03 | 17.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 814.8 | 19.5 | 2.45 | - | 53764 | 0 | 53764
P00406 | 47.5 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.7 | -6.92 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 440 | 6 | 2.84 | - | 29724 | 0 | 29724
P00407 | 47.5 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.64 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 41.4 | 0.2 | 7.91 | - | 2857 | 0 | 2857
P00408 | 47.5 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.57 | -11.27 | 22.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1201.7 | 44.3 | 2.25 | - | 76999 | 0 | 76999
P00409 | 55 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.71 | -12.28 | 24.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1527.8 | 75.6 | 2.03 | - | 86231 | 0 | 86231
P00410 | 55 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -7.88 | -10.71 | 21 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1231.3 | 46.8 | 2.1 | - | 71475 | 0 | 71475
P00411 | 55 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.47 | -8.87 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 873 | 23 | 2.23 | - | 52067 | 0 | 52067
P00412 | 55 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.61 | -6.86 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 474.1 | 7.2 | 2.56 | - | 29022 | 0 | 29022
P00413 | 55 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.64 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 45.7 | 0.2 | 7.2 | - | 2867 | 0 | 2867
P00414 | 55 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.26 | -11.02 | 21.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1291.5 | 52 | 2.09 | - | 74559 | 0 | 74559
P00415 | 62.5 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.17 | -11.79 | 23.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1643.4 | 88.2 | 1.89 | - | 81857 | 0 | 81857
P00416 | 62.5 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -7.52 | -10.42 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1334.2 | 55.6 | 1.94 | - | 68600 | 0 | 68600
P00417 | 62.5 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.31 | -8.76 | 16.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 957.9 | 28 | 2.04 | - | 50777 | 0 | 50777
P00418 | 62.5 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.57 | -6.84 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 526.6 | 8.8 | 2.32 | - | 28744 | 0 | 28744
P00419 | 62.5 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 55.4 | 0.3 | 6.25 | - | 3106 | 0 | 3106
P00420 | 62.5 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -7.91 | -10.73 | 21.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1402.9 | 62 | 1.93 | - | 71683 | 0 | 71683
P00421 | 70 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.5 | -11.22 | 22.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1786.6 | 104.7 | 1.74 | - | 76485 | 0 | 76485
P00422 | 70 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -7.02 | -10.02 | 19.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1453.3 | 67.1 | 1.75 | - | 64559 | 0 | 64559
P00423 | 70 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.11 | -8.61 | 16.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1068.5 | 35.2 | 1.84 | - | 49165 | 0 | 49165
P00424 | 70 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 594.9 | 11.3 | 2.07 | - | 28308 | 0 | 28308
P00425 | 70 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 63.7 | 0.3 | 5.51 | - | 3127 | 0 | 3127
P00426 | 70 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -7.41 | -10.33 | 20.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1534.4 | 74.8 | 1.77 | - | 67668 | 0 | 67668
P00427 | 56 | -20 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.66 | -12.23 | 24.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1543.1 | 77.2 | 2.01 | - | 85760 | 0 | 85760
P00428 | 56 | -15 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -7.85 | -10.68 | 20.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1244.7 | 47.9 | 2.08 | - | 71180 | 0 | 71180
P00429 | 56 | -10 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.45 | -8.86 | 17 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 883.3 | 23.6 | 2.21 | - | 51918 | 0 | 51918
P00430 | 56 | -5 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.61 | -6.86 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 480.6 | 7.4 | 2.53 | - | 29002 | 0 | 29002
P00431 | 56 | 0 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 50.2 | 0.3 | 6.87 | - | 3106 | 0 | 3106
P00432 | 56 | -16 | 1 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.22 | -10.99 | 21.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1305 | 53.2 | 2.07 | - | 74212 | 0 | 74212
P00433 | 25 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.06 | -12.6 | 25.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1317.5 | 50.7 | 2.68 | - | 106082 | 0 | 106082
P00434 | 25 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.98 | -10.79 | 21.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1048.3 | 30.3 | 2.82 | - | 86093 | 0 | 86093
P00435 | 25 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.41 | -8.83 | 17 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 734.7 | 14.6 | 3.03 | - | 61511 | 0 | 61511
P00436 | 25 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.51 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 395 | 4.1 | 3.61 | - | 33687 | 0 | 33687
P00437 | 25 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 36.7 | 0.2 | 9.51 | - | 3185 | 0 | 3185
P00438 | 25 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.45 | -11.18 | 22.1 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1108.2 | 34.2 | 2.78 | - | 90659 | 0 | 90659
P00439 | 32.5 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -9.85 | -12.4 | 25 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1391.3 | 57.6 | 2.51 | - | 104061 | 0 | 104061
P00440 | 32.5 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.85 | -10.68 | 20.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1110.8 | 34.8 | 2.63 | - | 84873 | 0 | 84873
P00441 | 32.5 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.34 | -8.77 | 16.9 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 779.2 | 16.8 | 2.81 | - | 60775 | 0 | 60775
P00442 | 32.5 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.51 | -6.79 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 422.4 | 5.2 | 3.31 | - | 33611 | 0 | 33611
P00443 | 32.5 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 39.3 | 0.2 | 8.81 | - | 3185 | 0 | 3185
P00444 | 32.5 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.26 | -11.02 | 21.7 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1167.4 | 38.8 | 2.6 | - | 88822 | 0 | 88822
P00445 | 40 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -9.58 | -12.15 | 24.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1472.5 | 65.6 | 2.36 | - | 101444 | 0 | 101444
P00446 | 40 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.65 | -10.52 | 20.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1176.2 | 39.8 | 2.46 | - | 82923 | 0 | 82923
P00447 | 40 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.26 | -8.72 | 16.7 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 832.6 | 19.6 | 2.6 | - | 60029 | 0 | 60029
P00448 | 40 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.45 | -6.75 | 13.2 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 449.1 | 6.1 | 2.99 | - | 33084 | 0 | 33084
P00449 | 40 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.67 | -4.69 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 42.1 | 0.2 | 8.14 | - | 3166 | 0 | 3166
P00450 | 40 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.05 | -10.85 | 21.3 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1237.1 | 44.5 | 2.43 | - | 86826 | 0 | 86826
P00451 | 47.5 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -9.19 | -11.81 | 23.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1556.7 | 74.3 | 2.22 | - | 97736 | 0 | 97736
P00452 | 47.5 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.37 | -10.3 | 20.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1246.9 | 46 | 2.26 | - | 80298 | 0 | 80298
P00453 | 47.5 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.07 | -8.58 | 16.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 882.7 | 22.6 | 2.39 | - | 58248 | 0 | 58248
P00454 | 47.5 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.4 | -6.72 | 13.1 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 482.5 | 7.2 | 2.71 | - | 32599 | 0 | 32599
P00455 | 47.5 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 47.1 | 0.2 | 7.36 | - | 3220 | 0 | 3220
P00456 | 47.5 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.76 | -10.61 | 20.8 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1311 | 51.4 | 2.24 | - | 84002 | 0 | 84002
P00457 | 55 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.68 | -11.37 | 22.5 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1644.7 | 85 | 2.05 | - | 92827 | 0 | 92827
P00458 | 55 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.12 | -10.12 | 19.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1341 | 54.1 | 2.09 | - | 77844 | 0 | 77844
P00459 | 55 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -4.96 | -8.5 | 16.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 958 | 27.1 | 2.2 | - | 57140 | 0 | 57140
P00460 | 55 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.37 | -6.7 | 13.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 527.9 | 8.6 | 2.47 | - | 32312 | 0 | 32312
P00461 | 55 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 52 | 0.3 | 6.68 | - | 3223 | 0 | 3223
P00462 | 55 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.45 | -10.36 | 20.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1404.2 | 59.8 | 2.08 | - | 81063 | 0 | 81063
P00463 | 62.5 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.17 | -10.94 | 21.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1765.6 | 98.7 | 1.9 | - | 87939 | 0 | 87939
P00464 | 62.5 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -6.76 | -9.82 | 19 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1446.5 | 63.6 | 1.94 | - | 74378 | 0 | 74378
P00465 | 62.5 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -4.8 | -8.38 | 16.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1048.3 | 32.8 | 2.01 | - | 55571 | 0 | 55571
P00466 | 62.5 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.33 | -6.67 | 13.1 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 584.2 | 10.6 | 2.24 | - | 31884 | 0 | 31884
P00467 | 62.5 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 56.8 | 0.3 | 6.09 | - | 3185 | 0 | 3185
P00468 | 62.5 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.08 | -10.08 | 19.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1516 | 70.6 | 1.92 | - | 77462 | 0 | 77462
P00469 | 70 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.56 | -10.45 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1917.9 | 116.7 | 1.75 | - | 82105 | 0 | 82105
P00470 | 70 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -6.25 | -9.45 | 18.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1566.1 | 75.9 | 1.76 | - | 69569 | 0 | 69569
P00471 | 70 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -4.59 | -8.23 | 15.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1163.9 | 40.8 | 1.82 | - | 53554 | 0 | 53554
P00472 | 70 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.25 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 654.3 | 13.4 | 2.02 | - | 31134 | 0 | 31134
P00473 | 70 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.56 | -4.76 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 85.8 | 0.5 | 4.78 | - | 4215 | 0 | 4215
P00474 | 70 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -6.6 | -9.71 | 18.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1652.9 | 84.4 | 1.77 | - | 72892 | 0 | 72892
P00475 | 56 | -20 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.62 | -11.32 | 22.4 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1660 | 86.7 | 2.03 | - | 92256 | 0 | 92256
P00476 | 56 | -15 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.08 | -10.08 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1355 | 55.3 | 2.07 | - | 77485 | 0 | 77485
P00477 | 56 | -10 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -4.93 | -8.48 | 16.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 967.5 | 27.6 | 2.17 | - | 56867 | 0 | 56867
P00478 | 56 | -5 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.37 | -6.69 | 13.1 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 534.6 | 8.9 | 2.44 | - | 32263 | 0 | 32263
P00479 | 56 | 0 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 51.5 | 0.3 | 6.69 | - | 3185 | 0 | 3185
P00480 | 56 | -16 | 1 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.41 | -10.33 | 20.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1418.1 | 61.1 | 2.06 | - | 80644 | 0 | 80644
P00481 | 25 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.24 | -11.85 | 23.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1415.7 | 57.1 | 2.67 | - | 113991 | 0 | 113991
P00482 | 25 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.27 | -10.27 | 19.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1121.1 | 34.4 | 2.75 | - | 92073 | 0 | 92073
P00483 | 25 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.99 | -8.52 | 16.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 796.6 | 16.9 | 2.98 | - | 66695 | 0 | 66695
P00484 | 25 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.26 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 424.8 | 5.2 | 3.46 | - | 36236 | 0 | 36236
P00485 | 25 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 36.8 | 0.2 | 9.36 | - | 3198 | 0 | 3198
P00486 | 25 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.77 | -10.62 | 20.8 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1193.7 | 38.9 | 2.76 | - | 97653 | 0 | 97653
P00487 | 32.5 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.99 | -11.64 | 23.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1488.1 | 64.3 | 2.51 | - | 111298 | 0 | 111298
P00488 | 32.5 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.09 | -10.09 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1178.6 | 38.8 | 2.59 | - | 90048 | 0 | 90048
P00489 | 32.5 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.92 | -8.47 | 16.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 844.9 | 19.4 | 2.77 | - | 65902 | 0 | 65902
P00490 | 32.5 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.25 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 455.1 | 6 | 3.18 | - | 36214 | 0 | 36214
P00491 | 32.5 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 41.8 | 0.2 | 8.52 | - | 3435 | 0 | 3435
P00492 | 32.5 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.62 | -10.5 | 20.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1261.3 | 44.4 | 2.58 | - | 95962 | 0 | 95962
P00493 | 40 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.73 | -11.41 | 22.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1573.2 | 73.1 | 2.36 | - | 108381 | 0 | 108381
P00494 | 40 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.94 | -9.94 | 19.3 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1253.9 | 44.8 | 2.41 | - | 88400 | 0 | 88400
P00495 | 40 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.76 | -8.36 | 16 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 890.2 | 22.2 | 2.54 | - | 64178 | 0 | 64178
P00496 | 40 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.24 | -6.61 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 490.1 | 7.1 | 2.92 | - | 36102 | 0 | 36102
P00497 | 40 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 44.9 | 0.2 | 7.86 | - | 3423 | 0 | 3423
P00498 | 40 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.39 | -10.32 | 20.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1331.4 | 50.4 | 2.42 | - | 93440 | 0 | 93440
P00499 | 47.5 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.36 | -11.1 | 21.9 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1659.6 | 82.4 | 2.22 | - | 104200 | 0 | 104200
P00500 | 47.5 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.72 | -9.8 | 19 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1334.7 | 51.7 | 2.25 | - | 85947 | 0 | 85947
P00501 | 47.5 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.66 | -8.29 | 15.9 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 955.2 | 26 | 2.35 | - | 63034 | 0 | 63034
P00502 | 47.5 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.23 | -6.6 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 531.8 | 8.4 | 2.67 | - | 35928 | 0 | 35928
P00503 | 47.5 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 49.2 | 0.2 | 7.17 | - | 3395 | 0 | 3395
P00504 | 47.5 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.14 | -10.14 | 19.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1414.5 | 57.9 | 2.26 | - | 90633 | 0 | 90633
P00505 | 55 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.94 | -10.76 | 21.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1763.9 | 94.3 | 2.08 | - | 99555 | 0 | 99555
P00506 | 55 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.47 | -9.61 | 18.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1432.7 | 60.5 | 2.08 | - | 83169 | 0 | 83169
P00507 | 55 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.55 | -8.21 | 15.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1036.8 | 31.1 | 2.17 | - | 61839 | 0 | 61839
P00508 | 55 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 571.7 | 9.9 | 2.41 | - | 34993 | 0 | 34993
P00509 | 55 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 58.9 | 0.3 | 6.27 | - | 3694 | 0 | 3694
P00510 | 55 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.8 | -9.8 | 19.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1504.9 | 67.2 | 2.07 | - | 86877 | 0 | 86877
P00511 | 62.5 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.39 | -10.31 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1875.3 | 108.5 | 1.91 | - | 93403 | 0 | 93403
P00512 | 62.5 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.12 | -9.35 | 18 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1541.3 | 70.7 | 1.94 | - | 79252 | 0 | 79252
P00513 | 62.5 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.37 | -8.08 | 15.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1126.8 | 37.2 | 2 | - | 59732 | 0 | 59732
P00514 | 62.5 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.1 | -6.51 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 631.3 | 12.2 | 2.19 | - | 34455 | 0 | 34455
P00515 | 62.5 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 65.9 | 0.3 | 5.62 | - | 3694 | 0 | 3694
P00516 | 62.5 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.41 | -9.56 | 18.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1614.6 | 78.1 | 1.93 | - | 82504 | 0 | 82504
P00517 | 70 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.77 | -9.83 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2020.4 | 126.4 | 1.76 | - | 86497 | 0 | 86497
P00518 | 70 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.63 | -8.99 | 17.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1662.3 | 83.8 | 1.75 | - | 73840 | 0 | 73840
P00519 | 70 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.09 | -7.88 | 15.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1231.2 | 45.2 | 1.79 | - | 56651 | 0 | 56651
P00520 | 70 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -1.99 | -6.44 | 12.7 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 698.5 | 15.1 | 1.95 | - | 33239 | 0 | 33239
P00521 | 70 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 70 | 0.4 | 5.13 | - | 3486 | 0 | 3486
P00522 | 70 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.94 | -9.22 | 17.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1753.3 | 93 | 1.77 | - | 77320 | 0 | 77320
P00523 | 56 | -20 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.81 | -10.65 | 20.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1765.6 | 95.5 | 2.04 | - | 98125 | 0 | 98125
P00524 | 56 | -15 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.43 | -9.58 | 18.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1447.1 | 61.8 | 2.06 | - | 82756 | 0 | 82756
P00525 | 56 | -10 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.54 | -8.2 | 15.7 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1048.8 | 31.8 | 2.14 | - | 61644 | 0 | 61644
P00526 | 56 | -5 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 579.8 | 10.2 | 2.38 | - | 34993 | 0 | 34993
P00527 | 56 | 0 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 59.7 | 0.3 | 6.19 | - | 3694 | 0 | 3694
P00528 | 56 | -16 | 1 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.76 | -9.83 | 19.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1519.5 | 68.6 | 2.05 | - | 86408 | 0 | 86408
P00529 | 25 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.6 | -11.3 | 22.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1505.6 | 63.3 | 2.66 | - | 121226 | 0 | 121226
P00530 | 25 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.82 | -9.82 | 19.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1203 | 38.4 | 2.78 | - | 98800 | 0 | 98800
P00531 | 25 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.64 | -8.27 | 15.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 851.3 | 19 | 2.94 | - | 71276 | 0 | 71276
P00532 | 25 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.1 | -6.52 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 459.3 | 6 | 3.36 | - | 39177 | 0 | 39177
P00533 | 25 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.73 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 39.8 | 0.2 | 9.01 | - | 3452 | 0 | 3452
P00534 | 25 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.19 | -10.19 | 19.8 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1265.2 | 43 | 2.74 | - | 103502 | 0 | 103502
P00535 | 32.5 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.32 | -11.07 | 21.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1573.6 | 70.4 | 2.52 | - | 117696 | 0 | 117696
P00536 | 32.5 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.59 | -9.7 | 18.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1254.5 | 43.3 | 2.57 | - | 95848 | 0 | 95848
P00537 | 32.5 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.57 | -8.22 | 15.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 902.1 | 21.7 | 2.73 | - | 70361 | 0 | 70361
P00538 | 32.5 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.1 | -6.52 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 492 | 6.9 | 3.08 | - | 39147 | 0 | 39147
P00539 | 32.5 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 45.5 | 0.2 | 8.16 | - | 3686 | 0 | 3686
P00540 | 32.5 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.97 | -9.97 | 19.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1322.4 | 48.5 | 2.54 | - | 100612 | 0 | 100612
P00541 | 40 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.05 | -10.85 | 21.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1660.2 | 79.8 | 2.36 | - | 114373 | 0 | 114373
P00542 | 40 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.43 | -9.58 | 18.5 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1330.6 | 49.6 | 2.4 | - | 93808 | 0 | 93808
P00543 | 40 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.46 | -8.15 | 15.6 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 957.3 | 25 | 2.55 | - | 69013 | 0 | 69013
P00544 | 40 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.08 | -6.5 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 527.7 | 8.1 | 2.84 | - | 38873 | 0 | 38873
P00545 | 40 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 48.4 | 0.2 | 7.55 | - | 3636 | 0 | 3636
P00546 | 40 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.78 | -9.85 | 19.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1400.9 | 55.5 | 2.38 | - | 98320 | 0 | 98320
P00547 | 47.5 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.68 | -10.55 | 20.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1747.2 | 89.4 | 2.23 | - | 109698 | 0 | 109698
P00548 | 47.5 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.23 | -9.43 | 18.2 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1418 | 57.3 | 2.24 | - | 91316 | 0 | 91316
P00549 | 47.5 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.38 | -8.08 | 15.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1028.8 | 29.3 | 2.36 | - | 67886 | 0 | 67886
P00550 | 47.5 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.05 | -6.48 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 569.8 | 9.5 | 2.61 | - | 38498 | 0 | 38498
P00551 | 47.5 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 52.6 | 0.3 | 6.9 | - | 3631 | 0 | 3631
P00552 | 47.5 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.52 | -9.65 | 18.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1482.4 | 63.1 | 2.23 | - | 94983 | 0 | 94983
P00553 | 55 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.23 | -10.23 | 19.8 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1842.8 | 101.7 | 2.06 | - | 104011 | 0 | 104011
P00554 | 55 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -5.93 | -9.21 | 17.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1507.8 | 65.7 | 2.09 | - | 87530 | 0 | 87530
P00555 | 55 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.19 | -7.95 | 15.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1098.6 | 34.3 | 2.16 | - | 65523 | 0 | 65523
P00556 | 55 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.95 | -6.42 | 12.7 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 608.9 | 11.1 | 2.38 | - | 37270 | 0 | 37270
P00557 | 55 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 58 | 0.3 | 6.25 | - | 3638 | 0 | 3638
P00558 | 55 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.23 | -9.43 | 18.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1581.2 | 72.9 | 2.07 | - | 91284 | 0 | 91284
P00559 | 62.5 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.72 | -9.8 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1958.8 | 115.9 | 1.92 | - | 97562 | 0 | 97562
P00560 | 62.5 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -5.52 | -8.91 | 17.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1602 | 75.9 | 1.91 | - | 82372 | 0 | 82372
P00561 | 62.5 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.02 | -7.83 | 15.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1196.5 | 41.3 | 1.98 | - | 63427 | 0 | 63427
P00562 | 62.5 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.9 | -6.38 | 12.6 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 671.5 | 13.6 | 2.16 | - | 36651 | 0 | 36651
P00563 | 62.5 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 66.5 | 0.4 | 5.52 | - | 3697 | 0 | 3697
P00564 | 62.5 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -5.86 | -9.16 | 17.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1696.8 | 84.7 | 1.94 | - | 86704 | 0 | 86704
P00565 | 70 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.14 | -9.36 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2107.1 | 134.9 | 1.77 | - | 90207 | 0 | 90207
P00566 | 70 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -5.12 | -8.62 | 16.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1739.5 | 90.1 | 1.76 | - | 77270 | 0 | 77270
P00567 | 70 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -3.77 | -7.65 | 14.7 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1308.3 | 49.8 | 1.81 | - | 60201 | 0 | 60201
P00568 | 70 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.79 | -6.31 | 12.5 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 739.6 | 16.7 | 1.92 | - | 35193 | 0 | 35193
P00569 | 70 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 76 | 0.4 | 4.88 | - | 3733 | 0 | 3733
P00570 | 70 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -5.4 | -8.82 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1833.8 | 99.7 | 1.78 | - | 80870 | 0 | 80870
P00571 | 56 | -20 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.17 | -10.17 | 19.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1857.6 | 103.5 | 2.04 | - | 103238 | 0 | 103238
P00572 | 56 | -15 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -5.89 | -9.18 | 17.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1522.8 | 67.1 | 2.07 | - | 87083 | 0 | 87083
P00573 | 56 | -10 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.17 | -7.94 | 15.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1111.1 | 35.2 | 2.13 | - | 65310 | 0 | 65310
P00574 | 56 | -5 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.95 | -6.41 | 12.6 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 616.4 | 11.4 | 2.35 | - | 37199 | 0 | 37199
P00575 | 56 | 0 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 60.5 | 0.3 | 6.07 | - | 3708 | 0 | 3708
P00576 | 56 | -16 | 1 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.19 | -9.4 | 18.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1596.5 | 74.4 | 2.06 | - | 90787 | 0 | 90787
P00577 | 25 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.55 | -13.08 | 26.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1274.9 | 47.9 | 2.68 | - | 102656 | 0 | 102656
P00578 | 25 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.18 | -10.95 | 21.6 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 993.7 | 27.9 | 2.81 | - | 81611 | 0 | 81611
P00579 | 25 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.61 | -8.98 | 17.3 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 702.2 | 13.5 | 3.07 | - | 58790 | 0 | 58790
P00580 | 25 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.64 | -6.88 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 378.8 | 3.7 | 3.66 | - | 32305 | 0 | 32305
P00581 | 25 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 35.8 | 0.2 | 9.62 | - | 3060 | 0 | 3060
P00582 | 25 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.75 | -11.43 | 22.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1060 | 31.6 | 2.8 | - | 86714 | 0 | 86714
P00583 | 32.5 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.25 | -12.78 | 25.9 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1337.1 | 53.9 | 2.52 | - | 100009 | 0 | 100009
P00584 | 32.5 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.07 | -10.86 | 21.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1055.3 | 32.1 | 2.61 | - | 80627 | 0 | 80627
P00585 | 32.5 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.59 | -8.96 | 17.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 750.8 | 15.8 | 2.83 | - | 58557 | 0 | 58557
P00586 | 32.5 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.56 | -6.83 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 397.9 | 4.4 | 3.32 | - | 31656 | 0 | 31656
P00587 | 32.5 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 37.2 | 0.2 | 9.04 | - | 3018 | 0 | 3018
P00588 | 32.5 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.54 | -11.25 | 22.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1114.6 | 36.2 | 2.58 | - | 84801 | 0 | 84801
P00589 | 40 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.98 | -12.53 | 25.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1417.3 | 61.5 | 2.37 | - | 97641 | 0 | 97641
P00590 | 40 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.92 | -10.74 | 21.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1124.3 | 37.2 | 2.43 | - | 79266 | 0 | 79266
P00591 | 40 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.48 | -8.88 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 799.1 | 18.2 | 2.63 | - | 57615 | 0 | 57615
P00592 | 40 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.55 | -6.82 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 428.5 | 5.6 | 3.05 | - | 31563 | 0 | 31563
P00593 | 40 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.56 | -4.76 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 52 | 0.3 | 7.8 | - | 3907 | 0 | 3907
P00594 | 40 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.37 | -11.11 | 21.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1186.5 | 41.8 | 2.41 | - | 83271 | 0 | 83271
P00595 | 47.5 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.65 | -12.22 | 24.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1508.3 | 70.8 | 2.21 | - | 94702 | 0 | 94702
P00596 | 47.5 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.68 | -10.55 | 20.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1198.7 | 43 | 2.27 | - | 77194 | 0 | 77194
P00597 | 47.5 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.31 | -8.76 | 16.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 850.1 | 21.2 | 2.4 | - | 56095 | 0 | 56095
P00598 | 47.5 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.55 | -6.82 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 466.5 | 6.7 | 2.78 | - | 31518 | 0 | 31518
P00599 | 47.5 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.56 | -4.76 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 56.6 | 0.3 | 7.08 | - | 3907 | 0 | 3907
P00600 | 47.5 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.17 | -10.95 | 21.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1272.6 | 48.4 | 2.27 | - | 81539 | 0 | 81539
P00601 | 55 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.2 | -11.81 | 23.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1606.1 | 81.2 | 2.07 | - | 90647 | 0 | 90647
P00602 | 55 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.41 | -10.33 | 20.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1288.3 | 50.5 | 2.1 | - | 74786 | 0 | 74786
P00603 | 55 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.19 | -8.67 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 922.7 | 25.4 | 2.21 | - | 55030 | 0 | 55030
P00604 | 55 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.53 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 512 | 8.1 | 2.54 | - | 31342 | 0 | 31342
P00605 | 55 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 48.1 | 0.2 | 6.99 | - | 3015 | 0 | 3015
P00606 | 55 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.81 | -10.65 | 20.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1357.2 | 56.6 | 2.08 | - | 78353 | 0 | 78353
P00607 | 62.5 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.61 | -11.31 | 22.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1714.7 | 94.2 | 1.9 | - | 85405 | 0 | 85405
P00608 | 62.5 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.11 | -10.11 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1402.2 | 60.6 | 1.93 | - | 72098 | 0 | 72098
P00609 | 62.5 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5 | -8.53 | 16.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1006 | 30.5 | 2.03 | - | 53327 | 0 | 53327
P00610 | 62.5 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.44 | -6.75 | 13.2 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 560.3 | 9.9 | 2.27 | - | 30579 | 0 | 30579
P00611 | 62.5 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 54.8 | 0.3 | 6.23 | - | 3045 | 0 | 3045
P00612 | 62.5 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.43 | -10.35 | 20.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1466.7 | 66.8 | 1.92 | - | 74943 | 0 | 74943
P00613 | 70 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.95 | -10.77 | 21.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1858.7 | 111.1 | 1.75 | - | 79573 | 0 | 79573
P00614 | 70 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -6.59 | -9.7 | 18.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1518.3 | 72.2 | 1.75 | - | 67444 | 0 | 67444
P00615 | 70 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -4.74 | -8.35 | 16 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1109.5 | 37.8 | 1.81 | - | 51050 | 0 | 51050
P00616 | 70 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.33 | -6.67 | 13.1 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 621.1 | 12.3 | 2.02 | - | 29553 | 0 | 29553
P00617 | 70 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 63.4 | 0.3 | 5.47 | - | 3113 | 0 | 3113
P00618 | 70 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -6.91 | -9.91 | 19.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1593.3 | 80 | 1.74 | - | 70266 | 0 | 70266
P00619 | 56 | -20 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.14 | -11.76 | 23.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1621.3 | 82.8 | 2.05 | - | 90104 | 0 | 90104
P00620 | 56 | -15 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.38 | -10.31 | 20.1 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1303.2 | 51.7 | 2.08 | - | 74528 | 0 | 74528
P00621 | 56 | -10 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.17 | -8.65 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 933.3 | 26 | 2.18 | - | 54858 | 0 | 54858
P00622 | 56 | -5 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 518.6 | 8.3 | 2.51 | - | 31296 | 0 | 31296
P00623 | 56 | 0 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 49.8 | 0.3 | 6.83 | - | 3049 | 0 | 3049
P00624 | 56 | -16 | 1 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.77 | -10.62 | 20.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1371.4 | 57.9 | 2.06 | - | 77988 | 0 | 77988
P00625 | 25 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -9.66 | -11.66 | 40.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1401.3 | 54.3 | 2.78 | - | 112833 | 0 | 112833
P00626 | 25 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.14 | -9.63 | 32.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1177.7 | 35.9 | 2.89 | - | 96723 | 0 | 96723
P00627 | 25 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.23 | -7.53 | 25 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 932.7 | 21 | 3.11 | - | 78083 | 0 | 78083
P00628 | 25 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.13 | -5.45 | 19.3 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 683.5 | 10.7 | 3.48 | - | 58295 | 0 | 58295
P00629 | 25 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.34 | -3.23 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 416.3 | 4.1 | 4.15 | - | 36140 | 0 | 36140
P00630 | 25 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.2 | -0.87 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 130.4 | 0.5 | 6.38 | - | 11518 | 0 | 11518
P00631 | 25 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.69 | -10.05 | 33.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1224.8 | 39.4 | 2.85 | - | 100202 | 0 | 100202
P00632 | 32.5 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -9.26 | -11.26 | 38.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1474.3 | 62.1 | 2.58 | - | 110272 | 0 | 110272
P00633 | 32.5 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.9 | -9.45 | 31.5 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1245.2 | 41.1 | 2.7 | - | 95138 | 0 | 95138
P00634 | 32.5 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.12 | -7.45 | 24.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 992 | 24.3 | 2.89 | - | 77375 | 0 | 77375
P00635 | 32.5 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.05 | -5.39 | 19.2 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 725.8 | 12.4 | 3.2 | - | 57751 | 0 | 57751
P00636 | 32.5 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.31 | -3.25 | 14.9 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 447.9 | 4.8 | 3.75 | - | 36316 | 0 | 36316
P00637 | 32.5 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.16 | -0.89 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 141.8 | 0.6 | 5.75 | - | 11718 | 0 | 11718
P00638 | 32.5 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.41 | -9.83 | 32.9 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1293.4 | 45 | 2.67 | - | 98404 | 0 | 98404
P00639 | 40 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -8.83 | -10.95 | 37.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1560.5 | 70.8 | 2.42 | - | 107508 | 0 | 107508
P00640 | 40 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.63 | -9.25 | 30.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1325.1 | 47.6 | 2.51 | - | 93420 | 0 | 93420
P00641 | 40 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.03 | -7.39 | 24.6 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1065.1 | 28.7 | 2.68 | - | 76790 | 0 | 76790
P00642 | 40 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.97 | -5.34 | 19.1 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 777.8 | 14.6 | 2.94 | - | 57296 | 0 | 57296
P00643 | 40 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.31 | -3.25 | 14.9 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 482.8 | 5.7 | 3.42 | - | 36301 | 0 | 36301
P00644 | 40 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.19 | -0.88 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 150.7 | 0.7 | 5.18 | - | 11562 | 0 | 11562
P00645 | 40 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.1 | -9.6 | 32.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1374.3 | 52 | 2.49 | - | 96454 | 0 | 96454
P00646 | 47.5 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -8.33 | -10.55 | 35.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1661.1 | 81.6 | 2.26 | - | 104290 | 0 | 104290
P00647 | 47.5 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.34 | -9.03 | 30 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1422 | 55.8 | 2.35 | - | 91572 | 0 | 91572
P00648 | 47.5 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -3.84 | -7.26 | 24.2 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1146.1 | 34.1 | 2.47 | - | 75628 | 0 | 75628
P00649 | 47.5 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.81 | -5.24 | 18.8 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 832.7 | 17.3 | 2.68 | - | 56256 | 0 | 56256
P00650 | 47.5 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.41 | -3.19 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 517 | 6.7 | 3.09 | - | 35712 | 0 | 35712
P00651 | 47.5 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.16 | -0.9 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 166.7 | 0.8 | 4.66 | - | 11770 | 0 | 11770
P00652 | 47.5 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.79 | -9.36 | 31.2 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1473.8 | 60.9 | 2.32 | - | 94437 | 0 | 94437
P00653 | 55 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -7.75 | -10.09 | 33.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1782.1 | 94.8 | 2.12 | - | 100583 | 0 | 100583
P00654 | 55 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -5.95 | -8.74 | 29 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1534.2 | 66.2 | 2.17 | - | 89060 | 0 | 89060
P00655 | 55 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -3.58 | -7.08 | 23.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1239.4 | 40.6 | 2.28 | - | 73922 | 0 | 73922
P00656 | 55 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.71 | -5.17 | 18.6 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 908.3 | 21 | 2.45 | - | 55600 | 0 | 55600
P00657 | 55 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.44 | -3.17 | 14.7 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 565.8 | 8.2 | 2.81 | - | 35491 | 0 | 35491
P00658 | 55 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.17 | -0.89 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 180.6 | 0.9 | 4.18 | - | 11651 | 0 | 11651
P00659 | 55 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.32 | -9.02 | 29.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1583.7 | 71.3 | 2.16 | - | 91428 | 0 | 91428
P00660 | 62.5 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -7.05 | -9.56 | 31.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1930.3 | 111.9 | 1.96 | - | 96142 | 0 | 96142
P00661 | 62.5 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -5.39 | -8.39 | 27.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1663.5 | 78.6 | 2.01 | - | 85532 | 0 | 85532
P00662 | 62.5 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -3.21 | -6.83 | 23 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1349.9 | 49.3 | 2.07 | - | 71560 | 0 | 71560
P00663 | 62.5 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.55 | -5.07 | 18.4 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1000.6 | 25.9 | 2.23 | - | 54611 | 0 | 54611
P00664 | 62.5 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.55 | -3.1 | 14.6 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 620.1 | 10 | 2.51 | - | 34785 | 0 | 34785
P00665 | 62.5 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.15 | -0.9 | 11.4 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 205.3 | 1.1 | 3.71 | - | 11833 | 0 | 11833
P00666 | 62.5 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -5.71 | -8.57 | 28.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1713.6 | 85.1 | 1.98 | - | 87559 | 0 | 87559
P00667 | 70 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -6.12 | -8.87 | 29.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2106.6 | 133.5 | 1.81 | - | 90185 | 0 | 90185
P00668 | 70 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.64 | -7.81 | 25.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 1816.9 | 95.2 | 1.82 | - | 80708 | 0 | 80708
P00669 | 70 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -2.76 | -6.53 | 22.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1492.9 | 61.1 | 1.89 | - | 68695 | 0 | 68695
P00670 | 70 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.33 | -4.93 | 18.1 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1117.6 | 32.7 | 2.02 | - | 53181 | 0 | 53181
P00671 | 70 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.61 | -3.06 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 700.7 | 12.9 | 2.25 | - | 34403 | 0 | 34403
P00672 | 70 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.16 | -0.9 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 232.3 | 1.4 | 3.25 | - | 11765 | 0 | 11765
P00673 | 70 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.97 | -8.04 | 26.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1877.7 | 102.7 | 1.82 | - | 82808 | 0 | 82808
P00674 | 56 | -20 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -7.66 | -10.03 | 33.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1800 | 96.8 | 2.1 | - | 100036 | 0 | 100036
P00675 | 56 | -15 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -5.89 | -8.7 | 28.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1551 | 67.8 | 2.14 | - | 88694 | 0 | 88694
P00676 | 56 | -10 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -3.54 | -7.06 | 23.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1253.6 | 41.6 | 2.26 | - | 73687 | 0 | 73687
P00677 | 56 | -5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.69 | -5.16 | 18.6 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 919.6 | 21.5 | 2.43 | - | 55499 | 0 | 55499
P00678 | 56 | 0 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.45 | -3.16 | 14.7 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 573.1 | 8.4 | 2.77 | - | 35456 | 0 | 35456
P00679 | 56 | 5 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.16 | -0.89 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 184.7 | 1 | 4.1 | - | 11713 | 0 | 11713
P00680 | 56 | -16 | 8 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.25 | -8.97 | 29.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1600.5 | 73 | 2.14 | - | 91013 | 0 | 91013
P00681 | 25 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.04 | -10.32 | 34.8 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1563.5 | 65.7 | 2.74 | - | 125896 | 0 | 125896
P00682 | 25 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.91 | -8.72 | 28.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1328.9 | 44.3 | 2.85 | - | 109144 | 0 | 109144
P00683 | 25 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.32 | -6.9 | 23.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1060.4 | 26.3 | 3.05 | - | 88778 | 0 | 88778
P00684 | 25 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.47 | -5.02 | 18.3 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 778.9 | 13.5 | 3.36 | - | 66436 | 0 | 66436
P00685 | 25 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.67 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 481.5 | 5.3 | 3.93 | - | 41798 | 0 | 41798
P00686 | 25 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.31 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 150.2 | 0.6 | 5.93 | - | 13271 | 0 | 13271
P00687 | 25 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.33 | -9.03 | 30 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1374.9 | 48.1 | 2.83 | - | 112476 | 0 | 112476
P00688 | 32.5 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -7.7 | -10.06 | 33.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1647.5 | 74.6 | 2.57 | - | 123222 | 0 | 123222
P00689 | 32.5 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.64 | -8.52 | 28.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1400.7 | 50.3 | 2.67 | - | 107023 | 0 | 107023
P00690 | 32.5 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.22 | -6.84 | 23 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1128.8 | 30.6 | 2.83 | - | 88044 | 0 | 88044
P00691 | 32.5 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.38 | -4.96 | 18.1 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 825.7 | 15.6 | 3.1 | - | 65701 | 0 | 65701
P00692 | 32.5 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.68 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 514.9 | 6.2 | 3.58 | - | 41749 | 0 | 41749
P00693 | 32.5 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.33 | -0.79 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 158.1 | 0.7 | 5.34 | - | 13066 | 0 | 13066
P00694 | 32.5 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.07 | -8.84 | 29.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1451.2 | 54.9 | 2.64 | - | 110412 | 0 | 110412
P00695 | 40 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -7.25 | -9.72 | 32.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1737.3 | 84.3 | 2.42 | - | 119690 | 0 | 119690
P00696 | 40 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.34 | -8.34 | 27.5 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1484.8 | 57.9 | 2.49 | - | 104685 | 0 | 104685
P00697 | 40 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.06 | -6.73 | 22.7 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1203.1 | 35.6 | 2.62 | - | 86736 | 0 | 86736
P00698 | 40 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.23 | -4.86 | 17.9 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 875.9 | 18.2 | 2.83 | - | 64523 | 0 | 64523
P00699 | 40 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.78 | -2.96 | 14.4 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 544.9 | 7.1 | 3.24 | - | 40967 | 0 | 40967
P00700 | 40 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.3 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 173.5 | 0.8 | 4.81 | - | 13312 | 0 | 13312
P00701 | 40 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.77 | -8.62 | 28.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1539.3 | 63 | 2.47 | - | 108029 | 0 | 108029
P00702 | 47.5 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -6.77 | -9.35 | 31.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1846 | 96.5 | 2.27 | - | 115900 | 0 | 115900
P00703 | 47.5 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.04 | -8.04 | 26.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1589 | 67.5 | 2.32 | - | 102325 | 0 | 102325
P00704 | 47.5 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -2.87 | -6.6 | 22.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1292.5 | 42 | 2.43 | - | 85291 | 0 | 85291
P00705 | 47.5 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.12 | -4.79 | 17.8 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 942.9 | 21.5 | 2.61 | - | 63699 | 0 | 63699
P00706 | 47.5 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.81 | -2.94 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 589.7 | 8.5 | 2.96 | - | 40734 | 0 | 40734
P00707 | 47.5 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.33 | -0.8 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 185.7 | 0.9 | 4.34 | - | 13115 | 0 | 13115
P00708 | 47.5 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.44 | -8.38 | 27.8 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1646 | 73.3 | 2.31 | - | 105465 | 0 | 105465
P00709 | 55 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -6.18 | -8.92 | 29.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1971.2 | 111.2 | 2.12 | - | 111255 | 0 | 111255
P00710 | 55 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.6 | -7.79 | 25.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1702.9 | 78.6 | 2.17 | - | 98855 | 0 | 98855
P00711 | 55 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -2.58 | -6.41 | 21.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1391.6 | 49.6 | 2.26 | - | 82999 | 0 | 82999
P00712 | 55 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.03 | -4.73 | 17.6 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1029.2 | 26.1 | 2.4 | - | 63002 | 0 | 63002
P00713 | 55 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.85 | -2.91 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 643.7 | 10.3 | 2.7 | - | 40382 | 0 | 40382
P00714 | 55 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.29 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 208 | 1.1 | 3.89 | - | 13368 | 0 | 13368
P00715 | 55 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.95 | -8.03 | 26.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1760.4 | 84.9 | 2.16 | - | 101629 | 0 | 101629
P00716 | 62.5 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -5.45 | -8.38 | 27.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2118.2 | 129.1 | 1.98 | - | 105505 | 0 | 105505
P00717 | 62.5 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.03 | -7.39 | 24.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1835.3 | 92.9 | 1.99 | - | 94368 | 0 | 94368
P00718 | 62.5 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -2.19 | -6.19 | 21.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1507.8 | 59.7 | 2.05 | - | 79928 | 0 | 79928
P00719 | 62.5 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 0.13 | -4.63 | 17.4 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1130.9 | 32.1 | 2.19 | - | 61726 | 0 | 61726
P00720 | 62.5 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.95 | -2.85 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 705.8 | 12.6 | 2.42 | - | 39592 | 0 | 39592
P00721 | 62.5 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.31 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 230.2 | 1.3 | 3.45 | - | 13268 | 0 | 13268
P00722 | 62.5 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.34 | -7.61 | 25.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1894.3 | 100.1 | 1.98 | - | 96796 | 0 | 96796
P00723 | 70 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -4.56 | -7.76 | 25.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2301.5 | 152.7 | 1.83 | - | 98530 | 0 | 98530
P00724 | 70 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.33 | -6.91 | 23.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2000.8 | 111.2 | 1.83 | - | 88878 | 0 | 88878
P00725 | 70 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -1.73 | -5.84 | 20.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1657.9 | 72.9 | 1.88 | - | 76283 | 0 | 76283
P00726 | 70 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 0.46 | -4.42 | 17 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1243.4 | 39.6 | 1.97 | - | 59163 | 0 | 59163
P00727 | 70 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 3.03 | -2.8 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 793 | 16 | 2.17 | - | 38937 | 0 | 38937
P00728 | 70 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.33 | -0.79 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 258.1 | 1.6 | 3.05 | - | 13074 | 0 | 13074
P00729 | 70 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.58 | -7.09 | 23.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2060.7 | 119.1 | 1.83 | - | 90878 | 0 | 90878
P00730 | 56 | -20 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -6.07 | -8.83 | 29.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1985.8 | 113.3 | 2.1 | - | 110364 | 0 | 110364
P00731 | 56 | -15 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.53 | -7.74 | 25.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1719.4 | 80.2 | 2.15 | - | 98325 | 0 | 98325
P00732 | 56 | -10 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -2.46 | -6.32 | 21.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1395.9 | 50.5 | 2.21 | - | 82047 | 0 | 82047
P00733 | 56 | -5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.01 | -4.72 | 17.6 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1040.4 | 26.8 | 2.37 | - | 62785 | 0 | 62785
P00734 | 56 | 0 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.86 | -2.91 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 651.9 | 10.5 | 2.66 | - | 40331 | 0 | 40331
P00735 | 56 | 5 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.29 | -0.82 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 211.6 | 1.2 | 3.83 | - | 13416 | 0 | 13416
P00736 | 56 | -16 | 8 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.89 | -7.99 | 26.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1778 | 86.7 | 2.14 | - | 101107 | 0 | 101107
P00737 | 25 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -6.72 | -9.31 | 31 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1709.4 | 76.1 | 2.74 | - | 137642 | 0 | 137642
P00738 | 25 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.83 | -7.95 | 26.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1461.2 | 52.2 | 2.82 | - | 120012 | 0 | 120012
P00739 | 25 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.51 | -6.36 | 21.7 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1174.1 | 31.5 | 3 | - | 98300 | 0 | 98300
P00740 | 25 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.12 | -4.63 | 17.4 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 863.5 | 16.3 | 3.28 | - | 73651 | 0 | 73651
P00741 | 25 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3 | -2.82 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 538.7 | 6.4 | 3.78 | - | 46761 | 0 | 46761
P00742 | 25 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.42 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 167.5 | 0.7 | 5.62 | - | 14803 | 0 | 14803
P00743 | 25 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.26 | -8.26 | 27.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1515.5 | 56.9 | 2.8 | - | 123985 | 0 | 123985
P00744 | 32.5 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -6.37 | -9.06 | 30.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1796.6 | 85.9 | 2.57 | - | 134374 | 0 | 134374
P00745 | 32.5 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.56 | -7.76 | 25.7 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1536.9 | 59 | 2.65 | - | 117428 | 0 | 117428
P00746 | 32.5 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.38 | -6.27 | 21.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1243.8 | 36.3 | 2.79 | - | 97011 | 0 | 97011
P00747 | 32.5 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.29 | -4.52 | 17.2 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 905.6 | 18.6 | 3 | - | 72053 | 0 | 72053
P00748 | 32.5 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.08 | -2.77 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 567.6 | 7.4 | 3.41 | - | 46021 | 0 | 46021
P00749 | 32.5 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.4 | -0.75 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 181.3 | 0.8 | 5.08 | - | 14978 | 0 | 14978
P00750 | 32.5 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.94 | -8.02 | 26.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1589.7 | 64 | 2.63 | - | 120953 | 0 | 120953
P00751 | 40 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -5.93 | -8.73 | 28.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1890.2 | 96.5 | 2.43 | - | 130225 | 0 | 130225
P00752 | 40 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.26 | -7.55 | 25.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1626.5 | 67.5 | 2.48 | - | 114676 | 0 | 114676
P00753 | 40 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.15 | -6.15 | 21 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1315.7 | 42 | 2.57 | - | 94858 | 0 | 94858
P00754 | 40 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.38 | -4.47 | 17.1 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 967.5 | 21.7 | 2.78 | - | 71272 | 0 | 71272
P00755 | 40 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.13 | -2.74 | 14 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 605.9 | 8.6 | 3.13 | - | 45552 | 0 | 45552
P00756 | 40 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.41 | -0.75 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 193.4 | 1 | 4.56 | - | 14841 | 0 | 14841
P00757 | 40 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.63 | -7.8 | 25.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1682.1 | 73.1 | 2.47 | - | 118053 | 0 | 118053
P00758 | 47.5 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -5.42 | -8.37 | 27.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1998.9 | 109.3 | 2.28 | - | 125502 | 0 | 125502
P00759 | 47.5 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.94 | -7.33 | 24.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1733.7 | 78 | 2.32 | - | 111639 | 0 | 111639
P00760 | 47.5 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -1.95 | -5.95 | 20.7 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1410.2 | 49.2 | 2.39 | - | 93057 | 0 | 93057
P00761 | 47.5 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.45 | -4.42 | 17 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1044.1 | 25.8 | 2.56 | - | 70540 | 0 | 70540
P00762 | 47.5 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.16 | -2.72 | 14 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 654.5 | 10.2 | 2.87 | - | 45206 | 0 | 45206
P00763 | 47.5 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.39 | -0.76 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 213.3 | 1.1 | 4.12 | - | 15063 | 0 | 15063
P00764 | 47.5 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.29 | -7.57 | 25.2 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1793.9 | 84.4 | 2.3 | - | 114945 | 0 | 114945
P00765 | 55 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -4.86 | -7.97 | 26.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2130.6 | 125.5 | 2.14 | - | 120254 | 0 | 120254
P00766 | 55 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.55 | -7.06 | 23.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1859.5 | 90.9 | 2.16 | - | 107945 | 0 | 107945
P00767 | 55 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -1.64 | -5.78 | 20.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1511.6 | 57.6 | 2.21 | - | 90154 | 0 | 90154
P00768 | 55 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.56 | -4.35 | 16.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1136 | 31.1 | 2.36 | - | 69536 | 0 | 69536
P00769 | 55 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.21 | -2.69 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 713.9 | 12.3 | 2.63 | - | 44781 | 0 | 44781
P00770 | 55 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.41 | -0.75 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 231.7 | 1.3 | 3.69 | - | 14894 | 0 | 14894
P00771 | 55 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.8 | -7.24 | 24.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1911.9 | 97.1 | 2.16 | - | 110376 | 0 | 110376
P00772 | 62.5 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -4.15 | -7.48 | 24.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2280.9 | 144.5 | 2 | - | 113606 | 0 | 113606
P00773 | 62.5 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.91 | -6.63 | 22.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1983.1 | 105.4 | 1.99 | - | 101967 | 0 | 101967
P00774 | 62.5 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -1.32 | -5.57 | 19.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1644.3 | 69.2 | 2.04 | - | 87165 | 0 | 87165
P00775 | 62.5 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.8 | -4.2 | 16.6 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1233.6 | 37.6 | 2.14 | - | 67333 | 0 | 67333
P00776 | 62.5 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.27 | -2.65 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 787.7 | 15.2 | 2.38 | - | 44189 | 0 | 44189
P00777 | 62.5 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.42 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 255.6 | 1.5 | 3.28 | - | 14736 | 0 | 14736
P00778 | 62.5 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.17 | -6.81 | 22.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2044.1 | 112.9 | 1.99 | - | 104449 | 0 | 104449
P00779 | 70 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -3.34 | -6.92 | 23.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2476 | 170.1 | 1.85 | - | 106000 | 0 | 106000
P00780 | 70 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.25 | -6.18 | 21.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2157.6 | 125.5 | 1.84 | - | 95844 | 0 | 95844
P00781 | 70 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -0.86 | -5.27 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1799.1 | 83.6 | 1.88 | - | 82783 | 0 | 82783
P00782 | 70 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 1.07 | -4.03 | 16.2 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1361.8 | 46.5 | 1.95 | - | 64797 | 0 | 64797
P00783 | 70 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.41 | -2.59 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 874.2 | 19.1 | 2.12 | - | 42922 | 0 | 42922
P00784 | 70 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.43 | -0.73 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 289.1 | 1.9 | 2.88 | - | 14640 | 0 | 14640
P00785 | 70 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.49 | -6.34 | 21.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2223.4 | 134.2 | 1.84 | - | 98052 | 0 | 98052
P00786 | 56 | -20 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -4.78 | -7.91 | 26.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2150.1 | 127.9 | 2.12 | - | 119497 | 0 | 119497
P00787 | 56 | -15 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.43 | -6.98 | 23.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1868.9 | 92 | 2.15 | - | 106878 | 0 | 106878
P00788 | 56 | -10 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -1.61 | -5.76 | 20.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1527.7 | 59 | 2.19 | - | 89796 | 0 | 89796
P00789 | 56 | -5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.59 | -4.34 | 16.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1148.4 | 31.9 | 2.33 | - | 69303 | 0 | 69303
P00790 | 56 | 0 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.22 | -2.68 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 722.8 | 12.6 | 2.59 | - | 44714 | 0 | 44714
P00791 | 56 | 5 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.4 | -0.75 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 235.3 | 1.3 | 3.63 | - | 14919 | 0 | 14919
P00792 | 56 | -16 | 8 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.74 | -7.19 | 24 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1930.1 | 99 | 2.14 | - | 109759 | 0 | 109759
P00793 | 25 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -5.57 | -8.47 | 28.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1829.6 | 85.2 | 2.73 | - | 147320 | 0 | 147320
P00794 | 25 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.91 | -7.31 | 24.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1573.5 | 59.1 | 2.81 | - | 129233 | 0 | 129233
P00795 | 25 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.83 | -5.9 | 20.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1273.9 | 36.4 | 2.97 | - | 106653 | 0 | 106653
P00796 | 25 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.7 | -4.3 | 16.7 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 928.6 | 18.7 | 3.19 | - | 79202 | 0 | 79202
P00797 | 25 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.35 | -2.6 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 580.9 | 7.4 | 3.63 | - | 50430 | 0 | 50430
P00798 | 25 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.5 | -0.69 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 183.7 | 0.8 | 5.38 | - | 16228 | 0 | 16228
P00799 | 25 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.29 | -7.57 | 25.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1630.2 | 64.3 | 2.79 | - | 133361 | 0 | 133361
P00800 | 32.5 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -5.28 | -8.28 | 27.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1927.8 | 96.1 | 2.57 | - | 144187 | 0 | 144187
P00801 | 32.5 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.68 | -7.15 | 23.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1659.7 | 67.2 | 2.64 | - | 126811 | 0 | 126811
P00802 | 32.5 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.67 | -5.8 | 20.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1345.3 | 41.7 | 2.76 | - | 104930 | 0 | 104930
P00803 | 32.5 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.81 | -4.19 | 16.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 980.4 | 21.3 | 2.97 | - | 78010 | 0 | 78010
P00804 | 32.5 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.37 | -2.63 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 619.7 | 8.6 | 3.32 | - | 50250 | 0 | 50250
P00805 | 32.5 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.48 | -0.7 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 199 | 0.9 | 4.86 | - | 16444 | 0 | 16444
P00806 | 32.5 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.05 | -7.4 | 24.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1718.6 | 72.9 | 2.62 | - | 130755 | 0 | 130755
P00807 | 40 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -4.82 | -7.94 | 26.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2020.6 | 107 | 2.44 | - | 139208 | 0 | 139208
P00808 | 40 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.36 | -6.93 | 23.3 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1748.5 | 76 | 2.48 | - | 123276 | 0 | 123276
P00809 | 40 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.43 | -5.64 | 19.8 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1420.1 | 47.9 | 2.55 | - | 102379 | 0 | 102379
P00810 | 40 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.85 | -4.15 | 16.5 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1052.7 | 25.2 | 2.74 | - | 77551 | 0 | 77551
P00811 | 40 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.4 | -2.6 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 663.8 | 10.1 | 3.05 | - | 49908 | 0 | 49908
P00812 | 40 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.5 | -0.69 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 212 | 1.1 | 4.36 | - | 16263 | 0 | 16263
P00813 | 40 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.67 | -7.15 | 23.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1805.4 | 82.1 | 2.46 | - | 126706 | 0 | 126706
P00814 | 47.5 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -4.37 | -7.62 | 25.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2137.9 | 121.4 | 2.29 | - | 134230 | 0 | 134230
P00815 | 47.5 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3 | -6.69 | 22.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1854 | 87 | 2.32 | - | 119390 | 0 | 119390
P00816 | 47.5 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.22 | -5.5 | 19.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1516.5 | 55.8 | 2.37 | - | 100070 | 0 | 100070
P00817 | 47.5 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.96 | -4.1 | 16.4 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1131.4 | 29.7 | 2.54 | - | 76433 | 0 | 76433
P00818 | 47.5 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.44 | -2.56 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 715.7 | 12 | 2.8 | - | 49437 | 0 | 49437
P00819 | 47.5 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.47 | -0.71 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 234.5 | 1.3 | 3.93 | - | 16563 | 0 | 16563
P00820 | 47.5 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.33 | -6.91 | 23.2 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1919.8 | 94.1 | 2.32 | - | 123012 | 0 | 123012
P00821 | 55 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -3.77 | -7.21 | 24.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2263.2 | 137.4 | 2.16 | - | 127734 | 0 | 127734
P00822 | 55 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.62 | -6.43 | 21.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1985.1 | 101.1 | 2.16 | - | 115236 | 0 | 115236
P00823 | 55 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -0.93 | -5.32 | 19 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1625.8 | 65.2 | 2.21 | - | 96966 | 0 | 96966
P00824 | 55 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 1.09 | -4.01 | 16.2 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1225.1 | 35.5 | 2.33 | - | 74993 | 0 | 74993
P00825 | 55 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.49 | -2.51 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 779.6 | 14.4 | 2.56 | - | 48904 | 0 | 48904
P00826 | 55 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.5 | -0.7 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 253.8 | 1.5 | 3.53 | - | 16316 | 0 | 16316
P00827 | 55 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.86 | -6.59 | 22.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2042.1 | 107.8 | 2.17 | - | 117890 | 0 | 117890
P00828 | 62.5 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -3.13 | -6.78 | 22.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2425.1 | 158.3 | 2.01 | - | 120788 | 0 | 120788
P00829 | 62.5 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.02 | -6.02 | 20.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2115.2 | 116.8 | 2 | - | 108758 | 0 | 108758
P00830 | 62.5 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -0.58 | -5.08 | 18.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1755.7 | 77.2 | 2.04 | - | 93071 | 0 | 93071
P00831 | 62.5 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 1.32 | -3.87 | 15.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1327.4 | 42.8 | 2.12 | - | 72453 | 0 | 72453
P00832 | 62.5 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.63 | -2.43 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 844.7 | 17.3 | 2.32 | - | 47386 | 0 | 47386
P00833 | 62.5 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.51 | -0.69 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 280 | 1.8 | 3.15 | - | 16139 | 0 | 16139
P00834 | 62.5 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.23 | -6.17 | 21.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2172.4 | 124.3 | 2 | - | 111006 | 0 | 111006
P00835 | 70 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -2.32 | -6.23 | 21.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2615.3 | 184.2 | 1.87 | - | 111964 | 0 | 111964
P00836 | 70 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.36 | -5.6 | 19.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2287.7 | 137.4 | 1.85 | - | 101622 | 0 | 101622
P00837 | 70 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -0.13 | -4.8 | 17.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1918 | 93 | 1.88 | - | 88254 | 0 | 88254
P00838 | 70 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 1.58 | -3.7 | 15.6 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1463.2 | 52.6 | 1.93 | - | 69624 | 0 | 69624
P00839 | 70 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.77 | -2.34 | 13.4 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 935 | 21.6 | 2.07 | - | 45908 | 0 | 45908
P00840 | 70 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.53 | -0.67 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 314.2 | 2.4 | 2.78 | - | 15913 | 0 | 15913
P00841 | 70 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.56 | -5.73 | 20 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2353.3 | 146.5 | 1.85 | - | 103784 | 0 | 103784
P00842 | 56 | -20 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -3.69 | -7.16 | 23.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2282.7 | 139.9 | 2.14 | - | 126867 | 0 | 126867
P00843 | 56 | -15 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.52 | -6.37 | 21.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1997.4 | 102.3 | 2.16 | - | 114226 | 0 | 114226
P00844 | 56 | -10 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -0.89 | -5.29 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1642.2 | 66.7 | 2.19 | - | 96528 | 0 | 96528
P00845 | 56 | -5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 1.11 | -4 | 16.2 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1238.9 | 36.4 | 2.31 | - | 74767 | 0 | 74767
P00846 | 56 | 0 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.5 | -2.5 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 789.1 | 14.8 | 2.53 | - | 48819 | 0 | 48819
P00847 | 56 | 5 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.49 | -0.7 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 257.8 | 1.5 | 3.48 | - | 16347 | 0 | 16347
P00848 | 56 | -16 | 8 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.8 | -6.55 | 22.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2060.7 | 110.1 | 2.14 | - | 117182 | 0 | 117182
P00849 | 25 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -4.67 | -7.83 | 26 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1937.3 | 93.4 | 2.74 | - | 155994 | 0 | 155994
P00850 | 25 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.13 | -6.78 | 22.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1668.9 | 65.3 | 2.81 | - | 137063 | 0 | 137063
P00851 | 25 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.26 | -5.53 | 19.5 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1361.7 | 40.9 | 2.94 | - | 114001 | 0 | 114001
P00852 | 25 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.09 | -4.01 | 16.2 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 996.7 | 20.9 | 3.2 | - | 85014 | 0 | 85014
P00853 | 25 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.56 | -2.44 | 13.6 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 628.9 | 8.4 | 3.61 | - | 54598 | 0 | 54598
P00854 | 25 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.57 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 198.7 | 0.9 | 5.18 | - | 17552 | 0 | 17552
P00855 | 25 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.47 | -7.01 | 23.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1726.4 | 70.8 | 2.79 | - | 141236 | 0 | 141236
P00856 | 32.5 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -4.34 | -7.61 | 25.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 2031.6 | 104.5 | 2.58 | - | 151955 | 0 | 151955
P00857 | 32.5 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.91 | -6.63 | 22.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1757.8 | 73.9 | 2.64 | - | 134304 | 0 | 134304
P00858 | 32.5 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.06 | -5.4 | 19.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1430.7 | 46.3 | 2.76 | - | 111589 | 0 | 111589
P00859 | 32.5 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.17 | -3.97 | 16.1 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1057.2 | 24.5 | 2.92 | - | 84117 | 0 | 84117
P00860 | 32.5 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.64 | -2.42 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 662.2 | 9.7 | 3.27 | - | 53694 | 0 | 53694
P00861 | 32.5 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.55 | -0.66 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 215.3 | 1.1 | 4.68 | - | 17791 | 0 | 17791
P00862 | 32.5 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.22 | -6.84 | 23 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1816.2 | 79.8 | 2.62 | - | 138186 | 0 | 138186
P00863 | 40 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -3.91 | -7.31 | 24.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2128.5 | 116.1 | 2.45 | - | 146641 | 0 | 146641
P00864 | 40 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.63 | -6.44 | 21.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1856.1 | 84 | 2.47 | - | 130862 | 0 | 130862
P00865 | 40 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.91 | -5.3 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1521.6 | 53.5 | 2.57 | - | 109704 | 0 | 109704
P00866 | 40 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.23 | -3.92 | 16 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1130.7 | 28.6 | 2.7 | - | 83294 | 0 | 83294
P00867 | 40 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.67 | -2.4 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 709.3 | 11.4 | 3 | - | 53325 | 0 | 53325
P00868 | 40 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.57 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 229 | 1.2 | 4.2 | - | 17571 | 0 | 17571
P00869 | 40 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.93 | -6.64 | 22.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1918.6 | 90.7 | 2.46 | - | 134652 | 0 | 134652
P00870 | 47.5 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -3.45 | -6.99 | 23.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2244.8 | 130.6 | 2.31 | - | 140942 | 0 | 140942
P00871 | 47.5 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.25 | -6.19 | 21.2 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1960.8 | 95.3 | 2.33 | - | 126269 | 0 | 126269
P00872 | 47.5 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.68 | -5.15 | 18.6 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1618.7 | 61.9 | 2.39 | - | 106817 | 0 | 106817
P00873 | 47.5 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.35 | -3.85 | 15.9 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1211.8 | 33.5 | 2.5 | - | 81869 | 0 | 81869
P00874 | 47.5 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.71 | -2.38 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 764.2 | 13.4 | 2.75 | - | 52784 | 0 | 52784
P00875 | 47.5 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.55 | -0.66 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 252.4 | 1.4 | 3.8 | - | 17824 | 0 | 17824
P00876 | 47.5 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.54 | -6.38 | 21.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 2025.8 | 102.8 | 2.31 | - | 129806 | 0 | 129806
P00877 | 55 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -2.9 | -6.62 | 22.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2379 | 148.3 | 2.16 | - | 134273 | 0 | 134273
P00878 | 55 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.83 | -5.9 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 2084.1 | 109 | 2.18 | - | 120984 | 0 | 120984
P00879 | 55 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.36 | -4.94 | 18.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1725 | 72.2 | 2.2 | - | 102883 | 0 | 102883
P00880 | 55 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.48 | -3.77 | 15.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1311.1 | 40 | 2.31 | - | 80258 | 0 | 80258
P00881 | 55 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.8 | -2.32 | 13.4 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 823.6 | 16 | 2.49 | - | 51661 | 0 | 51661
P00882 | 55 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.57 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 273.7 | 1.6 | 3.41 | - | 17594 | 0 | 17594
P00883 | 55 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.07 | -6.07 | 20.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2148.8 | 116.9 | 2.18 | - | 124052 | 0 | 124052
P00884 | 62.5 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -2.29 | -6.21 | 21.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2542.8 | 170 | 2.02 | - | 126653 | 0 | 126653
P00885 | 62.5 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.34 | -5.58 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2235.4 | 126.7 | 2.03 | - | 114942 | 0 | 114942
P00886 | 62.5 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 0.01 | -4.71 | 17.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1856.6 | 84.7 | 2.04 | - | 98420 | 0 | 98420
P00887 | 62.5 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.71 | -3.63 | 15.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1419.2 | 47.7 | 2.13 | - | 77463 | 0 | 77463
P00888 | 62.5 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.88 | -2.27 | 13.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 904.1 | 19.5 | 2.28 | - | 50715 | 0 | 50715
P00889 | 62.5 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.58 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 302.7 | 2.1 | 3.03 | - | 17446 | 0 | 17446
P00890 | 62.5 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.54 | -5.72 | 20 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2299.5 | 135.3 | 2.02 | - | 117500 | 0 | 117500
P00891 | 70 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -1.46 | -5.66 | 19.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2721.8 | 195.2 | 1.88 | - | 116522 | 0 | 116522
P00892 | 70 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.65 | -5.13 | 18.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2396.3 | 147.6 | 1.86 | - | 106444 | 0 | 106444
P00893 | 70 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 0.43 | -4.44 | 17 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 2025.7 | 101.9 | 1.88 | - | 93211 | 0 | 93211
P00894 | 70 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 2 | -3.44 | 15.2 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1552.5 | 58.4 | 1.92 | - | 73873 | 0 | 73873
P00895 | 70 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 4 | -2.2 | 13.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1003 | 24.3 | 2.07 | - | 49248 | 0 | 49248
P00896 | 70 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.58 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 345.6 | 3.1 | 2.7 | - | 17503 | 0 | 17503
P00897 | 70 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.81 | -5.24 | 18.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2459.9 | 156.5 | 1.87 | - | 108484 | 0 | 108484
P00898 | 56 | -20 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -2.81 | -6.56 | 22.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2395.5 | 150.6 | 2.14 | - | 133131 | 0 | 133131
P00899 | 56 | -15 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.77 | -5.86 | 20.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 2102.8 | 111.1 | 2.16 | - | 120252 | 0 | 120252
P00900 | 56 | -10 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.32 | -4.92 | 18 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1742.3 | 73.8 | 2.18 | - | 102410 | 0 | 102410
P00901 | 56 | -5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.5 | -3.75 | 15.7 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1325.6 | 41 | 2.29 | - | 79999 | 0 | 79999
P00902 | 56 | 0 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.82 | -2.31 | 13.4 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 832 | 16.4 | 2.47 | - | 51474 | 0 | 51474
P00903 | 56 | 5 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.56 | -0.66 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 278.6 | 1.7 | 3.36 | - | 17666 | 0 | 17666
P00904 | 56 | -16 | 8 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.01 | -6.01 | 20.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2167.7 | 119.1 | 2.16 | - | 123270 | 0 | 123270
P00905 | 25 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.26 | -9.72 | 32.5 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1642.8 | 71.4 | 2.74 | - | 132275 | 0 | 132275
P00906 | 25 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.24 | -8.24 | 27.3 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1397.6 | 48.4 | 2.83 | - | 114784 | 0 | 114784
P00907 | 25 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.89 | -6.62 | 22.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1127.5 | 29.4 | 3.02 | - | 94399 | 0 | 94399
P00908 | 25 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.06 | -4.75 | 17.7 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 818.8 | 15 | 3.28 | - | 69837 | 0 | 69837
P00909 | 25 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.87 | -2.9 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 512.1 | 5.9 | 3.85 | - | 44452 | 0 | 44452
P00910 | 25 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.37 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 159.4 | 0.7 | 5.77 | - | 14088 | 0 | 14088
P00911 | 25 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.73 | -8.59 | 28.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1455 | 52.9 | 2.82 | - | 119036 | 0 | 119036
P00912 | 32.5 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -6.89 | -9.44 | 31.5 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1725.5 | 80.4 | 2.57 | - | 129060 | 0 | 129060
P00913 | 32.5 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.04 | -8.09 | 26.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1479.2 | 55.3 | 2.65 | - | 113015 | 0 | 113015
P00914 | 32.5 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.78 | -6.54 | 22.1 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1197.2 | 34 | 2.8 | - | 93381 | 0 | 93381
P00915 | 32.5 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.01 | -4.7 | 17.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 869.8 | 17.3 | 3.02 | - | 69207 | 0 | 69207
P00916 | 32.5 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.89 | -2.89 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 546.2 | 6.8 | 3.51 | - | 44285 | 0 | 44285
P00917 | 32.5 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.35 | -0.78 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 172.7 | 0.8 | 5.21 | - | 14270 | 0 | 14270
P00918 | 32.5 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.47 | -8.4 | 27.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1534.7 | 60.4 | 2.63 | - | 116764 | 0 | 116764
P00919 | 40 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -6.52 | -9.17 | 30.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1826.7 | 91.6 | 2.41 | - | 125849 | 0 | 125849
P00920 | 40 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.78 | -7.91 | 26.2 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1571 | 63.7 | 2.48 | - | 110761 | 0 | 110761
P00921 | 40 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.56 | -6.39 | 21.7 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1268.9 | 39.1 | 2.61 | - | 91481 | 0 | 91481
P00922 | 40 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.09 | -4.65 | 17.4 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 929.8 | 20.2 | 2.79 | - | 68497 | 0 | 68497
P00923 | 40 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.95 | -2.85 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 581.8 | 8 | 3.17 | - | 43741 | 0 | 43741
P00924 | 40 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.37 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 184.2 | 0.9 | 4.68 | - | 14133 | 0 | 14133
P00925 | 40 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.13 | -8.13 | 27 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1621.4 | 68.7 | 2.47 | - | 113792 | 0 | 113792
P00926 | 47.5 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -5.98 | -8.77 | 29.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1930.3 | 103.7 | 2.27 | - | 121192 | 0 | 121192
P00927 | 47.5 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.4 | -7.65 | 25.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1668.7 | 73.1 | 2.33 | - | 107457 | 0 | 107457
P00928 | 47.5 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.31 | -6.22 | 21.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1353.4 | 45.8 | 2.4 | - | 89307 | 0 | 89307
P00929 | 47.5 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.23 | -4.56 | 17.3 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 996.5 | 23.7 | 2.59 | - | 67320 | 0 | 67320
P00930 | 47.5 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.99 | -2.82 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 628.6 | 9.5 | 2.9 | - | 43422 | 0 | 43422
P00931 | 47.5 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.38 | -0.76 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 198.2 | 1 | 4.2 | - | 13997 | 0 | 13997
P00932 | 47.5 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.75 | -7.89 | 26.2 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1724.7 | 79.1 | 2.31 | - | 110513 | 0 | 110513
P00933 | 55 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -5.41 | -8.36 | 27.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2059.5 | 118.9 | 2.14 | - | 116239 | 0 | 116239
P00934 | 55 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.91 | -7.31 | 24.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1778.2 | 85.1 | 2.14 | - | 103224 | 0 | 103224
P00935 | 55 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.05 | -6.05 | 20.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1459.9 | 54.3 | 2.22 | - | 87070 | 0 | 87070
P00936 | 55 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.32 | -4.51 | 17.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1087.1 | 28.8 | 2.38 | - | 66546 | 0 | 66546
P00937 | 55 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3.04 | -2.79 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 685.6 | 11.5 | 2.65 | - | 43005 | 0 | 43005
P00938 | 55 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.36 | -0.78 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 220.8 | 1.2 | 3.78 | - | 14195 | 0 | 14195
P00939 | 55 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.33 | -7.6 | 25.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1850.8 | 92.4 | 2.15 | - | 106846 | 0 | 106846
P00940 | 62.5 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -4.71 | -7.86 | 26.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2211.1 | 138.1 | 1.98 | - | 110130 | 0 | 110130
P00941 | 62.5 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.37 | -6.94 | 23.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 1916.6 | 99.7 | 2 | - | 98549 | 0 | 98549
P00942 | 62.5 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -1.68 | -5.81 | 20.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1583 | 64.8 | 2.05 | - | 83914 | 0 | 83914
P00943 | 62.5 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.54 | -4.36 | 16.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1184 | 35 | 2.15 | - | 64624 | 0 | 64624
P00944 | 62.5 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3.17 | -2.71 | 14 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 745.9 | 13.9 | 2.39 | - | 41841 | 0 | 41841
P00945 | 62.5 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.38 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 244 | 1.4 | 3.36 | - | 14064 | 0 | 14064
P00946 | 62.5 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.74 | -7.19 | 24 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 1990.7 | 107.7 | 2.01 | - | 101722 | 0 | 101722
P00947 | 70 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -3.79 | -7.23 | 24.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2387.4 | 161.9 | 1.82 | - | 102206 | 0 | 102206
P00948 | 70 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.71 | -6.49 | 22 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2088.5 | 119 | 1.84 | - | 92775 | 0 | 92775
P00949 | 70 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -1.25 | -5.53 | 19.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1742.2 | 79.4 | 1.87 | - | 80165 | 0 | 80165
P00950 | 70 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.78 | -4.22 | 16.6 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1315 | 43.7 | 1.95 | - | 62574 | 0 | 62574
P00951 | 70 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3.25 | -2.66 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 837.7 | 17.7 | 2.15 | - | 41132 | 0 | 41132
P00952 | 70 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.35 | -0.78 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 282.8 | 1.8 | 2.95 | - | 14324 | 0 | 14324
P00953 | 70 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.96 | -6.66 | 22.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2153.5 | 127.7 | 1.83 | - | 94971 | 0 | 94971
P00954 | 56 | -20 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -5.33 | -8.33 | 27.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2078.4 | 121.2 | 2.12 | - | 115511 | 0 | 115511
P00955 | 56 | -15 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.85 | -7.27 | 24.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1796.2 | 87 | 2.12 | - | 102721 | 0 | 102721
P00956 | 56 | -10 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.01 | -6.01 | 20.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1475.8 | 55.6 | 2.19 | - | 86748 | 0 | 86748
P00957 | 56 | -5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.34 | -4.49 | 17.1 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1099.9 | 29.5 | 2.35 | - | 66376 | 0 | 66376
P00958 | 56 | 0 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3.04 | -2.79 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 694.2 | 11.8 | 2.62 | - | 42946 | 0 | 42946
P00959 | 56 | 5 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.36 | -0.78 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 224.3 | 1.2 | 3.72 | - | 14221 | 0 | 14221
P00960 | 56 | -16 | 8 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.22 | -7.52 | 25 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 1862.2 | 93.6 | 2.14 | - | 105896 | 0 | 105896
P00961 | 25 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.04 | -8.82 | 50.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1706.2 | 73.8 | 2.83 | - | 137383 | 0 | 137383
P00962 | 25 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.75 | -7.22 | 41.6 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1499.2 | 53.1 | 2.9 | - | 123125 | 0 | 123125
P00963 | 25 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.12 | -5.45 | 33.3 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1274.1 | 34.9 | 3.11 | - | 106670 | 0 | 106670
P00964 | 25 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.97 | -3.48 | 26 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 1025.1 | 21.1 | 3.35 | - | 87431 | 0 | 87431
P00965 | 25 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.18 | -1.5 | 20.7 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 776.4 | 11.4 | 3.75 | - | 67400 | 0 | 67400
P00966 | 25 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.76 | 0.61 | 16.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 510.5 | 4.8 | 4.48 | - | 45107 | 0 | 45107
P00967 | 25 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.55 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 25 | 1 | 239.1 | 0.9 | 6.03 | - | 21479 | 0 | 21479
P00968 | 25 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.29 | -7.59 | 43.6 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1546.1 | 56.8 | 2.91 | - | 126483 | 0 | 126483
P00969 | 32.5 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.61 | -8.51 | 48.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1800.7 | 83.9 | 2.66 | - | 134685 | 0 | 134685
P00970 | 32.5 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.39 | -6.97 | 40.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1581.9 | 60.5 | 2.72 | - | 120862 | 0 | 120862
P00971 | 32.5 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.85 | -5.27 | 32.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1346 | 40.5 | 2.86 | - | 104981 | 0 | 104981
P00972 | 32.5 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.1 | -3.4 | 25.8 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1088.5 | 24.5 | 3.1 | - | 86607 | 0 | 86607
P00973 | 32.5 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.25 | -1.46 | 20.6 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 826 | 13.3 | 3.42 | - | 66979 | 0 | 66979
P00974 | 32.5 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.81 | 0.64 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 541.8 | 5.7 | 3.99 | - | 44773 | 0 | 44773
P00975 | 32.5 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.57 | 2.76 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 1 | 254 | 1 | 5.32 | - | 21369 | 0 | 21369
P00976 | 32.5 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.95 | -7.35 | 42.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1634.7 | 65 | 2.73 | - | 124373 | 0 | 124373
P00977 | 40 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.97 | -8.06 | 46.2 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1897.7 | 95.8 | 2.47 | - | 130738 | 0 | 130738
P00978 | 40 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.99 | -6.7 | 39 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1679 | 69.8 | 2.54 | - | 118377 | 0 | 118377
P00979 | 40 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.63 | -5.13 | 32 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1437.2 | 47.3 | 2.66 | - | 103616 | 0 | 103616
P00980 | 40 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.24 | -3.31 | 25.5 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1163.7 | 28.8 | 2.86 | - | 85727 | 0 | 85727
P00981 | 40 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.32 | -1.42 | 20.5 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 885.3 | 15.7 | 3.14 | - | 66558 | 0 | 66558
P00982 | 40 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.83 | 0.66 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 581.8 | 6.7 | 3.62 | - | 44642 | 0 | 44642
P00983 | 40 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.55 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 1 | 274.8 | 1.2 | 4.79 | - | 21491 | 0 | 21491
P00984 | 40 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.48 | -7.03 | 40.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1730.2 | 75.1 | 2.53 | - | 121433 | 0 | 121433
P00985 | 47.5 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.4 | -7.66 | 44 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2025.6 | 110.3 | 2.32 | - | 127177 | 0 | 127177
P00986 | 47.5 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.58 | -6.42 | 37.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 1798.6 | 81.6 | 2.37 | - | 115823 | 0 | 115823
P00987 | 47.5 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.35 | -4.95 | 31.2 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1543.8 | 55.9 | 2.47 | - | 101874 | 0 | 101874
P00988 | 47.5 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.42 | -3.2 | 25.2 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1252.8 | 34.2 | 2.63 | - | 84636 | 0 | 84636
P00989 | 47.5 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.41 | -1.36 | 20.4 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 955.4 | 18.8 | 2.88 | - | 65995 | 0 | 65995
P00990 | 47.5 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.87 | 0.68 | 16 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 628.8 | 8 | 3.29 | - | 44409 | 0 | 44409
P00991 | 47.5 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.52 | 2.73 | 12.6 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 1 | 300.8 | 1.6 | 4.3 | - | 21687 | 0 | 21687
P00992 | 47.5 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.01 | -6.71 | 39.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 1849.1 | 87.4 | 2.36 | - | 118484 | 0 | 118484
P00993 | 55 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.63 | -7.13 | 41.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2168.2 | 127.6 | 2.17 | - | 122376 | 0 | 122376
P00994 | 55 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -2.99 | -5.99 | 35.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 1931.1 | 95.2 | 2.22 | - | 112099 | 0 | 112099
P00995 | 55 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -0.92 | -4.68 | 30.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1663.6 | 66.1 | 2.3 | - | 99223 | 0 | 99223
P00996 | 55 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.69 | -3.03 | 24.7 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1355.1 | 41.3 | 2.4 | - | 82950 | 0 | 82950
P00997 | 55 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.6 | -1.25 | 20.1 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 1033 | 22.6 | 2.62 | - | 64798 | 0 | 64798
P00998 | 55 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.91 | 0.7 | 16 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 687 | 9.7 | 2.99 | - | 44156 | 0 | 44156
P00999 | 55 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.56 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 1 | 325.6 | 2.1 | 3.85 | - | 21414 | 0 | 21414
P01000 | 55 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.36 | -6.27 | 37 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 1982.2 | 101.6 | 2.21 | - | 114434 | 0 | 114434
P01001 | 62.5 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.69 | -6.49 | 38 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2338.3 | 149.1 | 2.02 | - | 116466 | 0 | 116466
P01002 | 62.5 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -2.3 | -5.57 | 33.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2097 | 113.4 | 2.06 | - | 107822 | 0 | 107822
P01003 | 62.5 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -0.37 | -4.32 | 28.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 1806.8 | 79.9 | 2.09 | - | 95780 | 0 | 95780
P01004 | 62.5 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.96 | -2.86 | 24.2 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1488.2 | 50.7 | 2.2 | - | 81228 | 0 | 81228
P01005 | 62.5 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.75 | -1.16 | 19.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 1138.1 | 28 | 2.38 | - | 63846 | 0 | 63846
P01006 | 62.5 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.97 | 0.73 | 15.9 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 760 | 12.1 | 2.71 | - | 43808 | 0 | 43808
P01007 | 62.5 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.56 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 1 | 362.5 | 3 | 3.45 | - | 21433 | 0 | 21433
P01008 | 62.5 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -2.59 | -5.76 | 34.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2145.2 | 120.2 | 2.05 | - | 109613 | 0 | 109613
P01009 | 70 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -2.53 | -5.72 | 34.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2552.3 | 177.2 | 1.87 | - | 109266 | 0 | 109266
P01010 | 70 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -1.33 | -4.94 | 31.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2291.1 | 136.6 | 1.88 | - | 101774 | 0 | 101774
P01011 | 70 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.3 | -3.9 | 27.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 1990.1 | 97.7 | 1.93 | - | 91571 | 0 | 91571
P01012 | 70 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 2.43 | -2.57 | 23.4 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1646 | 63.1 | 2.01 | - | 78325 | 0 | 78325
P01013 | 70 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.95 | -1.05 | 19.6 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1275.1 | 35.8 | 2.15 | - | 62605 | 0 | 62605
P01014 | 70 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 8.13 | 0.83 | 15.8 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 844.7 | 15.3 | 2.41 | - | 42780 | 0 | 42780
P01015 | 70 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.54 | 2.74 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 1 | 413.3 | 3.9 | 3.06 | - | 21547 | 0 | 21547
P01016 | 70 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -1.67 | -5.16 | 32.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2355.2 | 145.1 | 1.89 | - | 103867 | 0 | 103867
P01017 | 56 | -20 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.54 | -7.07 | 40.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2191.9 | 130.3 | 2.16 | - | 121817 | 0 | 121817
P01018 | 56 | -15 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -2.9 | -5.97 | 35.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 1951.2 | 97.4 | 2.2 | - | 111585 | 0 | 111585
P01019 | 56 | -10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -0.87 | -4.64 | 30 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1682 | 67.8 | 2.27 | - | 98865 | 0 | 98865
P01020 | 56 | -5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.72 | -3.01 | 24.6 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1371.1 | 42.4 | 2.38 | - | 82742 | 0 | 82742
P01021 | 56 | 0 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.61 | -1.24 | 20.1 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 1045.8 | 23.2 | 2.59 | - | 64700 | 0 | 64700
P01022 | 56 | 5 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.92 | 0.7 | 16 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 695.7 | 10 | 2.95 | - | 44116 | 0 | 44116
P01023 | 56 | 10 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.56 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 1 | 330.1 | 2.2 | 3.8 | - | 21421 | 0 | 21421
P01024 | 56 | -16 | 15 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.26 | -6.2 | 36.7 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2001.1 | 103.9 | 2.18 | - | 113795 | 0 | 113795
P01025 | 25 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -5.09 | -7.45 | 42.8 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 1911.1 | 88.9 | 2.83 | - | 153881 | 0 | 153881
P01026 | 25 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.13 | -6.13 | 36.3 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1689.9 | 65.2 | 2.88 | - | 138792 | 0 | 138792
P01027 | 25 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.71 | -4.54 | 29.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1436.9 | 43.6 | 3.03 | - | 120302 | 0 | 120302
P01028 | 25 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.03 | -2.82 | 24.1 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 1164.4 | 26.4 | 3.28 | - | 99310 | 0 | 99310
P01029 | 25 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.95 | -1.05 | 19.6 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 886.4 | 14.5 | 3.63 | - | 76946 | 0 | 76946
P01030 | 25 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.27 | 0.91 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 582.8 | 6.2 | 4.22 | - | 51491 | 0 | 51491
P01031 | 25 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.8 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 25 | 1 | 272.9 | 1.1 | 5.6 | - | 24517 | 0 | 24517
P01032 | 25 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.6 | -6.43 | 37.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1740.5 | 69.5 | 2.89 | - | 142389 | 0 | 142389
P01033 | 32.5 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.65 | -7.15 | 41.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 2011.9 | 100.2 | 2.66 | - | 150482 | 0 | 150482
P01034 | 32.5 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.72 | -5.84 | 35 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1775.6 | 73.7 | 2.7 | - | 135661 | 0 | 135661
P01035 | 32.5 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.55 | -4.43 | 29.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1526 | 50.4 | 2.83 | - | 119020 | 0 | 119020
P01036 | 32.5 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.14 | -2.75 | 23.9 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1237.6 | 30.8 | 3.02 | - | 98473 | 0 | 98473
P01037 | 32.5 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.03 | -0.97 | 19.5 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 941.3 | 16.8 | 3.32 | - | 76325 | 0 | 76325
P01038 | 32.5 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.29 | 0.92 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 621.5 | 7.2 | 3.81 | - | 51358 | 0 | 51358
P01039 | 32.5 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.78 | 2.87 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 1 | 293 | 1.4 | 5 | - | 24644 | 0 | 24644
P01040 | 32.5 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.22 | -6.22 | 36.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1834 | 79 | 2.71 | - | 139536 | 0 | 139536
P01041 | 40 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4 | -6.7 | 39 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2111.8 | 113.3 | 2.49 | - | 145491 | 0 | 145491
P01042 | 40 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.34 | -5.59 | 33.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1882.8 | 84.5 | 2.54 | - | 132742 | 0 | 132742
P01043 | 40 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.28 | -4.28 | 28.6 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1622.7 | 58.5 | 2.63 | - | 116986 | 0 | 116986
P01044 | 40 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.28 | -2.66 | 23.7 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1322.1 | 36.1 | 2.8 | - | 97394 | 0 | 97394
P01045 | 40 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.06 | -0.94 | 19.5 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 1011.8 | 19.9 | 3.05 | - | 76068 | 0 | 76068
P01046 | 40 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.32 | 0.93 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 666.2 | 8.5 | 3.47 | - | 51119 | 0 | 51119
P01047 | 40 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.75 | 2.86 | 12.4 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 1 | 318 | 1.8 | 4.49 | - | 24870 | 0 | 24870
P01048 | 40 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.74 | -5.86 | 35.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 1935.7 | 90.6 | 2.52 | - | 135853 | 0 | 135853
P01049 | 47.5 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.39 | -6.29 | 37.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2243.2 | 129.2 | 2.34 | - | 140838 | 0 | 140838
P01050 | 47.5 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.91 | -5.31 | 32.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 2010.1 | 97.9 | 2.37 | - | 129443 | 0 | 129443
P01051 | 47.5 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 0.08 | -4.04 | 27.7 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1731.4 | 68 | 2.46 | - | 114250 | 0 | 114250
P01052 | 47.5 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.47 | -2.53 | 23.4 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1419.9 | 42.7 | 2.59 | - | 95923 | 0 | 95923
P01053 | 47.5 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.26 | -0.85 | 19.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 1079.5 | 23.5 | 2.79 | - | 74567 | 0 | 74567
P01054 | 47.5 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.36 | 0.96 | 15.5 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 719.3 | 10.2 | 3.16 | - | 50798 | 0 | 50798
P01055 | 47.5 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.74 | 2.85 | 12.4 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 1 | 345.9 | 2.4 | 4.06 | - | 24946 | 0 | 24946
P01056 | 47.5 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.21 | -5.51 | 33.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 2056.2 | 103.7 | 2.37 | - | 131749 | 0 | 131749
P01057 | 55 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.68 | -5.82 | 34.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2398.5 | 148.8 | 2.19 | - | 135374 | 0 | 135374
P01058 | 55 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.29 | -4.91 | 31.1 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 2148.3 | 113.1 | 2.23 | - | 124712 | 0 | 124712
P01059 | 55 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 0.49 | -3.78 | 26.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1861.9 | 80.1 | 2.28 | - | 111050 | 0 | 111050
P01060 | 55 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.77 | -2.36 | 22.9 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1529.8 | 51.1 | 2.37 | - | 93643 | 0 | 93643
P01061 | 55 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.37 | -0.78 | 19 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 1174.4 | 28.4 | 2.56 | - | 73669 | 0 | 73669
P01062 | 55 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.41 | 0.99 | 15.5 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 784.6 | 12.3 | 2.88 | - | 50431 | 0 | 50431
P01063 | 55 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.79 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 1 | 374 | 3.1 | 3.64 | - | 24598 | 0 | 24598
P01064 | 55 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.58 | -5.1 | 31.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2199.4 | 120.3 | 2.21 | - | 126970 | 0 | 126970
P01065 | 62.5 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.73 | -5.2 | 32.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2572.2 | 171.7 | 2.06 | - | 128117 | 0 | 128117
P01066 | 62.5 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -0.57 | -4.45 | 29.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2318.6 | 132.9 | 2.07 | - | 119216 | 0 | 119216
P01067 | 62.5 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 0.97 | -3.48 | 26 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 2026.5 | 96.3 | 2.11 | - | 107425 | 0 | 107425
P01068 | 62.5 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 3.11 | -2.15 | 22.3 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1667.5 | 61.8 | 2.19 | - | 91016 | 0 | 91016
P01069 | 62.5 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.55 | -0.68 | 18.8 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 1288.8 | 35 | 2.33 | - | 72299 | 0 | 72299
P01070 | 62.5 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.56 | 1.07 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 855.2 | 15 | 2.6 | - | 49296 | 0 | 49296
P01071 | 62.5 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.78 | 2.87 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 1 | 417 | 3.9 | 3.27 | - | 24660 | 0 | 24660
P01072 | 62.5 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -0.85 | -4.63 | 30 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2374.6 | 141 | 2.06 | - | 121336 | 0 | 121336
P01073 | 70 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -0.61 | -4.47 | 29.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2791.3 | 201.9 | 1.9 | - | 119500 | 0 | 119500
P01074 | 70 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | 0.41 | -3.83 | 27.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2513.8 | 157.7 | 1.9 | - | 111663 | 0 | 111663
P01075 | 70 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.76 | -2.98 | 24.6 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 2203 | 115.6 | 1.93 | - | 101367 | 0 | 101367
P01076 | 70 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 3.53 | -1.9 | 21.7 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1845.2 | 76.7 | 2 | - | 87801 | 0 | 87801
P01077 | 70 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.77 | -0.55 | 18.5 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1439.2 | 44.4 | 2.12 | - | 70665 | 0 | 70665
P01078 | 70 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.65 | 1.12 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 958.9 | 19.2 | 2.34 | - | 48567 | 0 | 48567
P01079 | 70 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.81 | 2.89 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 1 | 467.6 | 4.9 | 2.88 | - | 24377 | 0 | 24377
P01080 | 70 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | 0.11 | -4.02 | 27.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2585.4 | 167.2 | 1.92 | - | 114015 | 0 | 114015
P01081 | 56 | -20 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.51 | -5.71 | 34.4 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2413 | 150.9 | 2.18 | - | 134104 | 0 | 134104
P01082 | 56 | -15 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.21 | -4.86 | 30.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 2169.7 | 115.5 | 2.21 | - | 124075 | 0 | 124075
P01083 | 56 | -10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 0.55 | -3.74 | 26.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1881.7 | 82 | 2.26 | - | 110602 | 0 | 110602
P01084 | 56 | -5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.8 | -2.34 | 22.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1547.9 | 52.4 | 2.34 | - | 93412 | 0 | 93412
P01085 | 56 | 0 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.39 | -0.77 | 19 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 1188.5 | 29.2 | 2.53 | - | 73527 | 0 | 73527
P01086 | 56 | 5 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.42 | 0.99 | 15.4 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 794.4 | 12.7 | 2.85 | - | 50373 | 0 | 50373
P01087 | 56 | 10 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.79 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 1 | 378.8 | 3.2 | 3.59 | - | 24586 | 0 | 24586
P01088 | 56 | -16 | 15 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.49 | -5.04 | 31.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2220.2 | 122.5 | 2.2 | - | 126257 | 0 | 126257
P01089 | 25 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.46 | -6.34 | 37.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 2092.1 | 102.6 | 2.84 | - | 168453 | 0 | 168453
P01090 | 25 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.71 | -5.19 | 32.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1856.8 | 76.4 | 2.87 | - | 152501 | 0 | 152501
P01091 | 25 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.43 | -3.82 | 27 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1588.4 | 52 | 3.01 | - | 132982 | 0 | 132982
P01092 | 25 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.86 | -2.31 | 22.7 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 1298.9 | 32.2 | 3.21 | - | 110785 | 0 | 110785
P01093 | 25 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.65 | -0.62 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 982.2 | 17.4 | 3.55 | - | 85266 | 0 | 85266
P01094 | 25 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.65 | 1.12 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 655.1 | 7.5 | 4.11 | - | 57885 | 0 | 57885
P01095 | 25 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.97 | 2.97 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 25 | 1 | 307.8 | 1.5 | 5.3 | - | 27654 | 0 | 27654
P01096 | 25 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.03 | -5.4 | 33.1 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1900.1 | 81.1 | 2.86 | - | 155445 | 0 | 155445
P01097 | 32.5 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.99 | -5.99 | 35.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 2195 | 115.3 | 2.67 | - | 164178 | 0 | 164178
P01098 | 32.5 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.32 | -4.93 | 31.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1949 | 85.9 | 2.71 | - | 148914 | 0 | 148914
P01099 | 32.5 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.66 | -3.67 | 26.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1677.3 | 59.4 | 2.81 | - | 130827 | 0 | 130827
P01100 | 32.5 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.97 | -2.23 | 22.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1379 | 37.4 | 2.97 | - | 109723 | 0 | 109723
P01101 | 32.5 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.64 | -0.63 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 1052.8 | 20.5 | 3.25 | - | 85364 | 0 | 85364
P01102 | 32.5 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.74 | 1.17 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 690.8 | 8.7 | 3.68 | - | 57082 | 0 | 57082
P01103 | 32.5 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.95 | 2.95 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 1 | 330.2 | 2 | 4.75 | - | 27778 | 0 | 27778
P01104 | 32.5 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.65 | -5.14 | 32 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1996.5 | 91.6 | 2.68 | - | 151899 | 0 | 151899
P01105 | 40 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.34 | -5.6 | 33.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2297.3 | 129.1 | 2.5 | - | 158266 | 0 | 158266
P01106 | 40 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.91 | -4.67 | 30.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 2058.6 | 97.9 | 2.54 | - | 145136 | 0 | 145136
P01107 | 40 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.9 | -3.52 | 26.1 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1783.9 | 68.7 | 2.62 | - | 128613 | 0 | 128613
P01108 | 40 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.19 | -2.1 | 22.2 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1462.4 | 43.2 | 2.76 | - | 107728 | 0 | 107728
P01109 | 40 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.79 | -0.54 | 18.5 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 1117.6 | 24 | 2.96 | - | 84023 | 0 | 84023
P01110 | 40 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.77 | 1.19 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 740.8 | 10.3 | 3.36 | - | 56844 | 0 | 56844
P01111 | 40 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 12 | 3 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 1 | 349.8 | 2.5 | 4.26 | - | 27358 | 0 | 27358
P01112 | 40 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.26 | -4.9 | 31 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 2114.4 | 104.5 | 2.52 | - | 148393 | 0 | 148393
P01113 | 47.5 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.75 | -5.21 | 32.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2434 | 146.3 | 2.36 | - | 152817 | 0 | 152817
P01114 | 47.5 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.47 | -4.39 | 29 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 2192.2 | 112.6 | 2.38 | - | 141164 | 0 | 141164
P01115 | 47.5 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 1.21 | -3.33 | 25.6 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1906.2 | 80.1 | 2.44 | - | 125788 | 0 | 125788
P01116 | 47.5 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.39 | -1.98 | 21.9 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1567.6 | 50.8 | 2.56 | - | 105905 | 0 | 105905
P01117 | 47.5 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.93 | -0.46 | 18.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 1197.6 | 28.3 | 2.74 | - | 82725 | 0 | 82725
P01118 | 47.5 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.79 | 1.2 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 802.3 | 12.3 | 3.08 | - | 56663 | 0 | 56663
P01119 | 47.5 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.99 | 2.99 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 1 | 380.9 | 3.1 | 3.85 | - | 27464 | 0 | 27464
P01120 | 47.5 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.71 | -4.54 | 29.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 2236.9 | 118.8 | 2.37 | - | 143327 | 0 | 143327
P01121 | 55 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.03 | -4.74 | 30.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2590.9 | 167.1 | 2.21 | - | 146234 | 0 | 146234
P01122 | 55 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 0.1 | -4.02 | 27.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 2341.4 | 129.6 | 2.24 | - | 135919 | 0 | 135919
P01123 | 55 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 1.67 | -3.04 | 24.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 2038.5 | 93.1 | 2.28 | - | 121580 | 0 | 121580
P01124 | 55 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.71 | -1.79 | 21.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1683 | 60.3 | 2.35 | - | 103018 | 0 | 103018
P01125 | 55 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 6.06 | -0.38 | 18.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 1300 | 34 | 2.52 | - | 81548 | 0 | 81548
P01126 | 55 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.91 | 1.27 | 14.9 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 864.6 | 14.8 | 2.78 | - | 55572 | 0 | 55572
P01127 | 55 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.96 | 2.96 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 1 | 421.5 | 3.8 | 3.47 | - | 27717 | 0 | 27717
P01128 | 55 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.1 | -4.1 | 28.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2387.3 | 136.5 | 2.23 | - | 137818 | 0 | 137818
P01129 | 62.5 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.17 | -4.17 | 28.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2779.8 | 192.5 | 2.07 | - | 138458 | 0 | 138458
P01130 | 62.5 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 0.85 | -3.55 | 26.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2511 | 150.4 | 2.09 | - | 129112 | 0 | 129112
P01131 | 62.5 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.25 | -2.68 | 23.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 2195.2 | 110.3 | 2.09 | - | 116366 | 0 | 116366
P01132 | 62.5 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 4.06 | -1.57 | 20.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1828 | 72.4 | 2.17 | - | 99775 | 0 | 99775
P01133 | 62.5 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 6.24 | -0.27 | 17.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 1423.8 | 41.8 | 2.3 | - | 79870 | 0 | 79870
P01134 | 62.5 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 9.01 | 1.33 | 14.8 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 947.6 | 18.1 | 2.54 | - | 54626 | 0 | 54626
P01135 | 62.5 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 12.01 | 3.01 | 12.1 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 1 | 461.1 | 4.6 | 3.1 | - | 27264 | 0 | 27264
P01136 | 62.5 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 0.61 | -3.7 | 26.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2569.1 | 159.1 | 2.08 | - | 131274 | 0 | 131274
P01137 | 70 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 0.92 | -3.51 | 26.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 3001.3 | 223.6 | 1.93 | - | 128488 | 0 | 128488
P01138 | 70 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 1.72 | -3.01 | 24.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2727.1 | 178 | 1.93 | - | 121141 | 0 | 121141
P01139 | 70 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.96 | -2.24 | 22.6 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 2387.1 | 131.4 | 1.94 | - | 109840 | 0 | 109840
P01140 | 70 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 4.51 | -1.3 | 20.2 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 2011 | 88.8 | 1.99 | - | 95690 | 0 | 95690
P01141 | 70 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 6.54 | -0.1 | 17.6 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1571.9 | 52.1 | 2.08 | - | 77178 | 0 | 77178
P01142 | 70 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 9.08 | 1.37 | 14.8 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 1065.4 | 23.2 | 2.29 | - | 53961 | 0 | 53961
P01143 | 70 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 12 | 3 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 1 | 525.1 | 6 | 2.76 | - | 27378 | 0 | 27378
P01144 | 70 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 1.57 | -3.1 | 24.9 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2778.4 | 187 | 1.92 | - | 122527 | 0 | 122527
P01145 | 56 | -20 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.9 | -4.66 | 30.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2610.9 | 170 | 2.19 | - | 145103 | 0 | 145103
P01146 | 56 | -15 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | 0.21 | -3.96 | 27.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 2360.3 | 132.1 | 2.21 | - | 134979 | 0 | 134979
P01147 | 56 | -10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 1.75 | -2.99 | 24.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 2056.4 | 95.1 | 2.26 | - | 120871 | 0 | 120871
P01148 | 56 | -5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.75 | -1.76 | 21.3 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1701.3 | 61.8 | 2.33 | - | 102670 | 0 | 102670
P01149 | 56 | 0 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 6.08 | -0.37 | 18.1 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 1315.2 | 34.9 | 2.49 | - | 81364 | 0 | 81364
P01150 | 56 | 5 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.92 | 1.27 | 14.9 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 875.1 | 15.2 | 2.75 | - | 55494 | 0 | 55494
P01151 | 56 | 10 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.96 | 2.96 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 1 | 427.3 | 3.9 | 3.42 | - | 27729 | 0 | 27729
P01152 | 56 | -16 | 15 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.02 | -4.1 | 28 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2409.5 | 139.2 | 2.21 | - | 137021 | 0 | 137021
P01153 | 25 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -2.15 | -5.47 | 33.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 2256 | 115.9 | 2.83 | - | 181654 | 0 | 181654
P01154 | 25 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.5 | -4.41 | 29.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1999.7 | 86.5 | 2.87 | - | 164232 | 0 | 164232
P01155 | 25 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.39 | -3.21 | 25.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1721.8 | 59.7 | 2.99 | - | 144149 | 0 | 144149
P01156 | 25 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.62 | -1.84 | 21.5 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 1413.7 | 37.5 | 3.18 | - | 120575 | 0 | 120575
P01157 | 25 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.15 | -0.33 | 18 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 1079.3 | 20.5 | 3.49 | - | 93689 | 0 | 93689
P01158 | 25 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.08 | 1.37 | 14.8 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 709.7 | 8.8 | 3.97 | - | 62710 | 0 | 62710
P01159 | 25 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.13 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 25 | 1 | 337.8 | 2 | 5.11 | - | 30347 | 0 | 30347
P01160 | 25 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.86 | -4.63 | 30 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 2053.3 | 92.3 | 2.86 | - | 167981 | 0 | 167981
P01161 | 32.5 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.62 | -5.13 | 32 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 2354.4 | 128.1 | 2.69 | - | 176096 | 0 | 176096
P01162 | 32.5 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.18 | -4.18 | 28.3 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 2104.5 | 97.6 | 2.7 | - | 160794 | 0 | 160794
P01163 | 32.5 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.64 | -3.06 | 24.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1814.2 | 68 | 2.79 | - | 141499 | 0 | 141499
P01164 | 32.5 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.76 | -1.75 | 21.3 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1495.9 | 43.2 | 2.94 | - | 119023 | 0 | 119023
P01165 | 32.5 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.22 | -0.29 | 17.9 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 1146.4 | 23.9 | 3.2 | - | 92957 | 0 | 92957
P01166 | 32.5 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.1 | 1.38 | 14.7 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 755.5 | 10.2 | 3.6 | - | 62425 | 0 | 62425
P01167 | 32.5 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.16 | 3.08 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 1 | 357.5 | 2.5 | 4.52 | - | 30069 | 0 | 30069
P01168 | 32.5 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.44 | -4.37 | 29 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 2149.6 | 103.1 | 2.7 | - | 163554 | 0 | 163554
P01169 | 40 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.04 | -4.75 | 30.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2466.6 | 143.9 | 2.52 | - | 169931 | 0 | 169931
P01170 | 40 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.26 | -3.93 | 27.4 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 2214.8 | 110.2 | 2.54 | - | 156153 | 0 | 156153
P01171 | 40 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.91 | -2.89 | 24.3 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1923.9 | 78.1 | 2.62 | - | 138703 | 0 | 138703
P01172 | 40 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.92 | -1.66 | 21.1 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1593.3 | 50.3 | 2.73 | - | 117369 | 0 | 117369
P01173 | 40 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.35 | -0.21 | 17.8 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 1217.8 | 28 | 2.92 | - | 91558 | 0 | 91558
P01174 | 40 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.14 | 1.4 | 14.7 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 808.9 | 12 | 3.29 | - | 62064 | 0 | 62064
P01175 | 40 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.14 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 1 | 386.6 | 3.1 | 4.08 | - | 30237 | 0 | 30237
P01176 | 40 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.05 | -4.12 | 28.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 2271.9 | 117.2 | 2.53 | - | 159448 | 0 | 159448
P01177 | 47.5 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.44 | -4.37 | 29 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2605.1 | 162 | 2.38 | - | 163560 | 0 | 163560
P01178 | 47.5 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.7 | -3.65 | 26.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 2351.9 | 125.9 | 2.39 | - | 151453 | 0 | 151453
P01179 | 47.5 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 2.23 | -2.69 | 23.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 2049.8 | 90.5 | 2.44 | - | 135264 | 0 | 135264
P01180 | 47.5 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 4.17 | -1.51 | 20.7 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1697.8 | 58.4 | 2.55 | - | 114700 | 0 | 114700
P01181 | 47.5 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.47 | -0.14 | 17.6 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 1307.3 | 33.1 | 2.69 | - | 90302 | 0 | 90302
P01182 | 47.5 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.19 | 1.43 | 14.7 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 871.4 | 14.3 | 3.01 | - | 61537 | 0 | 61537
P01183 | 47.5 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.13 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 1 | 420.8 | 3.7 | 3.7 | - | 30347 | 0 | 30347
P01184 | 47.5 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.5 | -3.78 | 26.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 2397.8 | 132.1 | 2.39 | - | 153636 | 0 | 153636
P01185 | 55 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.32 | -3.89 | 27.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2755.9 | 183 | 2.23 | - | 155547 | 0 | 155547
P01186 | 55 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 1.32 | -3.26 | 25.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 2496.7 | 143.2 | 2.26 | - | 144932 | 0 | 144932
P01187 | 55 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 2.68 | -2.41 | 23 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 2187.7 | 104.7 | 2.29 | - | 130482 | 0 | 130482
P01188 | 55 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 4.52 | -1.29 | 20.2 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1812.6 | 68.5 | 2.34 | - | 110956 | 0 | 110956
P01189 | 55 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.65 | -0.03 | 17.4 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 1408.9 | 39.3 | 2.49 | - | 88377 | 0 | 88377
P01190 | 55 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.28 | 1.48 | 14.6 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 941.7 | 17.2 | 2.73 | - | 60530 | 0 | 60530
P01191 | 55 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.17 | 3.09 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 1 | 456.2 | 4.4 | 3.31 | - | 29999 | 0 | 29999
P01192 | 55 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 1.06 | -3.42 | 25.8 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2557.6 | 151.7 | 2.25 | - | 147652 | 0 | 147652
P01193 | 62.5 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 1.17 | -3.35 | 25.6 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2941.9 | 209.1 | 2.09 | - | 146533 | 0 | 146533
P01194 | 62.5 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 2 | -2.84 | 24.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2679 | 166.3 | 2.1 | - | 137750 | 0 | 137750
P01195 | 62.5 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.21 | -2.09 | 22.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 2355.1 | 122.8 | 2.13 | - | 124843 | 0 | 124843
P01196 | 62.5 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 4.84 | -1.11 | 19.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1972.1 | 82.5 | 2.16 | - | 107639 | 0 | 107639
P01197 | 62.5 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.82 | 0.07 | 17.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 1543.5 | 48.1 | 2.28 | - | 86586 | 0 | 86586
P01198 | 62.5 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.34 | 1.51 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 1039.8 | 21.3 | 2.49 | - | 59939 | 0 | 59939
P01199 | 62.5 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.16 | 3.08 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 1 | 508.2 | 5.5 | 2.99 | - | 30049 | 0 | 30049
P01200 | 62.5 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 1.83 | -2.94 | 24.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2730.5 | 174.3 | 2.1 | - | 139523 | 0 | 139523
P01201 | 70 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 2.13 | -2.75 | 23.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 3184.2 | 242.8 | 1.96 | - | 136317 | 0 | 136317
P01202 | 70 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 2.86 | -2.3 | 22.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2894.7 | 194.5 | 1.95 | - | 128583 | 0 | 128583
P01203 | 70 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.9 | -1.67 | 21.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 2554.9 | 146.4 | 1.95 | - | 117558 | 0 | 117558
P01204 | 70 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 5.33 | -0.81 | 19.1 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 2152.4 | 99.6 | 1.99 | - | 102419 | 0 | 102419
P01205 | 70 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 7.14 | 0.25 | 16.8 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1694.9 | 59.4 | 2.06 | - | 83218 | 0 | 83218
P01206 | 70 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.48 | 1.6 | 14.4 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 1153.9 | 26.7 | 2.26 | - | 58440 | 0 | 58440
P01207 | 70 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.18 | 3.09 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 1 | 572.2 | 7 | 2.68 | - | 29834 | 0 | 29834
P01208 | 70 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 2.68 | -2.41 | 23 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2959.1 | 204.4 | 1.96 | - | 130496 | 0 | 130496
P01209 | 56 | -20 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.42 | -3.83 | 27.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2779.5 | 186.2 | 2.21 | - | 154474 | 0 | 154474
P01210 | 56 | -15 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 1.42 | -3.19 | 25.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 2514.5 | 146 | 2.22 | - | 143795 | 0 | 143795
P01211 | 56 | -10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 2.74 | -2.38 | 22.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 2208.7 | 106.9 | 2.27 | - | 129828 | 0 | 129828
P01212 | 56 | -5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 4.54 | -1.28 | 20.2 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1835.7 | 70.4 | 2.32 | - | 110780 | 0 | 110780
P01213 | 56 | 0 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.68 | -0.02 | 17.4 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 1424.9 | 40.3 | 2.46 | - | 88153 | 0 | 88153
P01214 | 56 | 5 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.3 | 1.49 | 14.6 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 951.8 | 17.6 | 2.7 | - | 60357 | 0 | 60357
P01215 | 56 | 10 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.17 | 3.08 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 1 | 462.4 | 4.5 | 3.27 | - | 30010 | 0 | 30010
P01216 | 56 | -16 | 15 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 1.16 | -3.36 | 25.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2578.1 | 154.5 | 2.22 | - | 146609 | 0 | 146609
P01217 | 25 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.86 | -4.64 | 30 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 2367 | 126 | 2.82 | - | 190587 | 0 | 190587
P01218 | 25 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.41 | -3.83 | 27.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 2134.7 | 95.2 | 2.92 | - | 175318 | 0 | 175318
P01219 | 25 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.19 | -2.71 | 23.8 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1838.1 | 66.9 | 2.98 | - | 153889 | 0 | 153889
P01220 | 25 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.29 | -1.44 | 20.5 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 1509.2 | 42.1 | 3.16 | - | 128722 | 0 | 128722
P01221 | 25 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.59 | -0.07 | 17.5 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 1163.2 | 23.6 | 3.43 | - | 100976 | 0 | 100976
P01222 | 25 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.37 | 1.53 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 765.2 | 10.1 | 3.88 | - | 67610 | 0 | 67610
P01223 | 25 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.27 | 3.14 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 25 | 1 | 364.6 | 2.5 | 4.96 | - | 32757 | 0 | 32757
P01224 | 25 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.16 | -3.99 | 27.6 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 2180 | 101.7 | 2.86 | - | 178343 | 0 | 178343
P01225 | 32.5 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.41 | -4.35 | 28.9 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 2475.8 | 139.6 | 2.68 | - | 185177 | 0 | 185177
P01226 | 32.5 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.8 | -3.58 | 26.3 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 2232.7 | 107.4 | 2.71 | - | 170590 | 0 | 170590
P01227 | 32.5 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.41 | -2.59 | 23.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1939.2 | 76.2 | 2.78 | - | 151249 | 0 | 151249
P01228 | 32.5 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.44 | -1.35 | 20.3 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1594.9 | 48.4 | 2.92 | - | 126903 | 0 | 126903
P01229 | 32.5 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.71 | 0 | 17.4 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 1228.1 | 27 | 3.16 | - | 99581 | 0 | 99581
P01230 | 32.5 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.4 | 1.55 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 814 | 11.7 | 3.52 | - | 67259 | 0 | 67259
P01231 | 32.5 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.24 | 3.13 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 1 | 393.6 | 3 | 4.43 | - | 33109 | 0 | 33109
P01232 | 32.5 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.58 | -3.72 | 26.7 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 2277.9 | 113.1 | 2.71 | - | 173312 | 0 | 173312
P01233 | 40 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.14 | -4 | 27.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2592.7 | 155.1 | 2.54 | - | 178616 | 0 | 178616
P01234 | 40 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.28 | -3.29 | 25.4 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 2339 | 120.1 | 2.55 | - | 164905 | 0 | 164905
P01235 | 40 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.74 | -2.38 | 22.9 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 2042.8 | 86.3 | 2.62 | - | 147275 | 0 | 147275
P01236 | 40 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.59 | -1.25 | 20.1 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1698 | 56.1 | 2.73 | - | 125084 | 0 | 125084
P01237 | 40 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.8 | 0.05 | 17.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 1310.5 | 31.6 | 2.92 | - | 98524 | 0 | 98524
P01238 | 40 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.44 | 1.57 | 14.4 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 870.7 | 13.7 | 3.23 | - | 66811 | 0 | 66811
P01239 | 40 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.29 | 3.15 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 1 | 416.3 | 3.5 | 3.98 | - | 32563 | 0 | 32563
P01240 | 40 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.01 | -3.45 | 25.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 2395.3 | 127.3 | 2.55 | - | 168112 | 0 | 168112
P01241 | 47.5 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.7 | -3.65 | 26.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2736.3 | 174.4 | 2.39 | - | 171797 | 0 | 171797
P01242 | 47.5 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.72 | -3.01 | 24.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 2478.7 | 136.8 | 2.4 | - | 159616 | 0 | 159616
P01243 | 47.5 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 3.1 | -2.16 | 22.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 2166.3 | 99 | 2.45 | - | 142952 | 0 | 142952
P01244 | 47.5 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.8 | -1.13 | 19.8 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1813.4 | 65.5 | 2.53 | - | 122510 | 0 | 122510
P01245 | 47.5 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.98 | 0.16 | 17 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 1394.7 | 37.2 | 2.67 | - | 96335 | 0 | 96335
P01246 | 47.5 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.52 | 1.62 | 14.3 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 932.4 | 16.1 | 2.98 | - | 65846 | 0 | 65846
P01247 | 47.5 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.28 | 3.15 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 1 | 452.9 | 4.2 | 3.61 | - | 32661 | 0 | 32661
P01248 | 47.5 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.52 | -3.13 | 25 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 2528 | 143.5 | 2.4 | - | 161978 | 0 | 161978
P01249 | 55 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.35 | -3.24 | 25.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2905.2 | 197.2 | 2.26 | - | 163971 | 0 | 163971
P01250 | 55 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.3 | -2.65 | 23.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 2628.5 | 155.1 | 2.27 | - | 152588 | 0 | 152588
P01251 | 55 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 3.48 | -1.93 | 21.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 2321.2 | 115.4 | 2.28 | - | 138443 | 0 | 138443
P01252 | 55 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 5.11 | -0.94 | 19.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1941.2 | 76.6 | 2.36 | - | 118825 | 0 | 118825
P01253 | 55 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 7.1 | 0.23 | 16.9 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 1512.2 | 44.6 | 2.46 | - | 94859 | 0 | 94859
P01254 | 55 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.63 | 1.68 | 14.2 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 1003.2 | 19.2 | 2.7 | - | 64485 | 0 | 64485
P01255 | 55 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.25 | 3.13 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 1 | 501.5 | 5.2 | 3.26 | - | 32979 | 0 | 32979
P01256 | 55 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.1 | -2.77 | 24 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2685.4 | 163.4 | 2.26 | - | 155028 | 0 | 155028
P01257 | 62.5 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.21 | -2.7 | 23.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 3085.7 | 223.6 | 2.12 | - | 153693 | 0 | 153693
P01258 | 62.5 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.96 | -2.24 | 22.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2813.4 | 179 | 2.11 | - | 144659 | 0 | 144659
P01259 | 62.5 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.08 | -1.56 | 20.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 2475.4 | 133.9 | 2.11 | - | 131220 | 0 | 131220
P01260 | 62.5 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 5.52 | -0.7 | 18.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 2087 | 90.7 | 2.17 | - | 113908 | 0 | 113908
P01261 | 62.5 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 7.31 | 0.35 | 16.7 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 1647.2 | 54 | 2.27 | - | 92400 | 0 | 92400
P01262 | 62.5 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.68 | 1.68 | 14.2 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 1108.6 | 23.9 | 2.46 | - | 63904 | 0 | 63904
P01263 | 62.5 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.32 | 3.17 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 1 | 544.4 | 6.2 | 2.93 | - | 32191 | 0 | 32191
P01264 | 62.5 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.79 | -2.35 | 22.8 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2871.9 | 188.1 | 2.11 | - | 146745 | 0 | 146745
P01265 | 70 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 3.14 | -2.14 | 22.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 3330 | 258.2 | 1.99 | - | 142560 | 0 | 142560
P01266 | 70 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 3.77 | -1.75 | 21.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 3038.3 | 208.9 | 1.97 | - | 134965 | 0 | 134965
P01267 | 70 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.74 | -1.16 | 19.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 2679.2 | 157.6 | 1.97 | - | 123278 | 0 | 123278
P01268 | 70 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 5.95 | -0.45 | 18.3 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 2285.3 | 110.1 | 1.99 | - | 108742 | 0 | 108742
P01269 | 70 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 7.6 | 0.52 | 16.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1811.2 | 66.3 | 2.08 | - | 88928 | 0 | 88928
P01270 | 70 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.83 | 1.83 | 14 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 1225.8 | 29.9 | 2.21 | - | 62083 | 0 | 62083
P01271 | 70 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.38 | 3.2 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 1 | 603.2 | 7.7 | 2.6 | - | 31448 | 0 | 31448
P01272 | 70 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 3.6 | -1.85 | 21.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 3105.4 | 219.5 | 1.97 | - | 136950 | 0 | 136950
P01273 | 56 | -20 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.46 | -3.17 | 25.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2926.8 | 200.6 | 2.23 | - | 162663 | 0 | 162663
P01274 | 56 | -15 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.39 | -2.61 | 23.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 2649.1 | 157.8 | 2.24 | - | 151492 | 0 | 151492
P01275 | 56 | -10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 3.57 | -1.87 | 21.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 2335.6 | 116.9 | 2.28 | - | 137283 | 0 | 137283
P01276 | 56 | -5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 5.15 | -0.92 | 19.3 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1960.7 | 78.3 | 2.34 | - | 118327 | 0 | 118327
P01277 | 56 | 0 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 7.13 | 0.25 | 16.9 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 1527.9 | 45.7 | 2.43 | - | 94524 | 0 | 94524
P01278 | 56 | 5 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.61 | 1.67 | 14.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 1021.3 | 19.9 | 2.67 | - | 64761 | 0 | 64761
P01279 | 56 | 10 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.25 | 3.13 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 1 | 508.2 | 5.3 | 3.21 | - | 32980 | 0 | 32980
P01280 | 56 | -16 | 15 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 2.18 | -2.72 | 23.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2708.6 | 166.3 | 2.24 | - | 154030 | 0 | 154030
P01281 | 25 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -4.16 | -6.81 | 39.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 2012.8 | 96.8 | 2.82 | - | 162073 | 0 | 162073
P01282 | 25 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.3 | -5.57 | 33.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 1781.9 | 71.1 | 2.89 | - | 146344 | 0 | 146344
P01283 | 25 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.12 | -4.12 | 28.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 1527.6 | 48.6 | 3.01 | - | 127890 | 0 | 127890
P01284 | 25 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.51 | -2.49 | 23.3 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 1 | 1238.6 | 29.6 | 3.24 | - | 105644 | 0 | 105644
P01285 | 25 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.37 | -0.79 | 19 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 1 | 937.7 | 16 | 3.58 | - | 81402 | 0 | 81402
P01286 | 25 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.53 | 1.05 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 1 | 618.9 | 6.9 | 4.14 | - | 54685 | 0 | 54685
P01287 | 25 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.93 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 25 | 1 | 292.9 | 1.3 | 5.42 | - | 26315 | 0 | 26315
P01288 | 25 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.7 | -5.83 | 35 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 1829.8 | 76.4 | 2.85 | - | 149693 | 0 | 149693
P01289 | 32.5 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.7 | -6.5 | 38.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 2115.3 | 108.5 | 2.67 | - | 158213 | 0 | 158213
P01290 | 32.5 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.96 | -5.35 | 32.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 1877.9 | 81 | 2.7 | - | 143477 | 0 | 143477
P01291 | 32.5 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.17 | -3.98 | 27.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 1608.3 | 55.3 | 2.81 | - | 125446 | 0 | 125446
P01292 | 32.5 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.6 | -2.46 | 23.1 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 1 | 1317.4 | 34.4 | 3 | - | 104821 | 0 | 104821
P01293 | 32.5 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.44 | -0.74 | 18.9 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 1 | 996.3 | 18.6 | 3.28 | - | 80785 | 0 | 80785
P01294 | 32.5 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.55 | 1.07 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 1 | 659.4 | 8 | 3.75 | - | 54490 | 0 | 54490
P01295 | 32.5 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.93 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 1 | 312.8 | 1.7 | 4.85 | - | 26315 | 0 | 26315
P01296 | 32.5 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.36 | -5.61 | 34 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 1929.6 | 86.6 | 2.68 | - | 146812 | 0 | 146812
P01297 | 40 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.05 | -6.05 | 36 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 2216.5 | 122.5 | 2.48 | - | 152702 | 0 | 152702
P01298 | 40 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.53 | -5.07 | 31.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 1982.8 | 91.9 | 2.54 | - | 139792 | 0 | 139792
P01299 | 40 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.42 | -3.82 | 27.1 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 1709.9 | 63.9 | 2.62 | - | 123275 | 0 | 123275
P01300 | 40 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.76 | -2.36 | 22.9 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 1 | 1404.5 | 40.2 | 2.77 | - | 103466 | 0 | 103466
P01301 | 40 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.46 | -0.74 | 18.9 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 1 | 1073 | 22.1 | 3.02 | - | 80667 | 0 | 80667
P01302 | 40 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.58 | 1.08 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 1 | 706.9 | 9.5 | 3.42 | - | 54242 | 0 | 54242
P01303 | 40 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.9 | 2.94 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 1 | 335 | 2.2 | 4.33 | - | 26204 | 0 | 26204
P01304 | 40 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.88 | -5.3 | 32.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 2034.2 | 98 | 2.53 | - | 142766 | 0 | 142766
P01305 | 47.5 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.49 | -5.7 | 34.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 2356.4 | 139.4 | 2.35 | - | 147946 | 0 | 147946
P01306 | 47.5 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.04 | -4.76 | 30.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 2107.2 | 105.6 | 2.38 | - | 135691 | 0 | 135691
P01307 | 47.5 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.73 | -3.63 | 26.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 1829.3 | 74.6 | 2.45 | - | 120714 | 0 | 120714
P01308 | 47.5 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.95 | -2.25 | 22.6 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 1 | 1508.7 | 47.6 | 2.57 | - | 101926 | 0 | 101926
P01309 | 47.5 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.6 | -0.65 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 1 | 1150.2 | 26.3 | 2.75 | - | 79451 | 0 | 79451
P01310 | 47.5 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.62 | 1.11 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 1 | 763.5 | 11.3 | 3.11 | - | 53919 | 0 | 53919
P01311 | 47.5 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.94 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 1 | 364.1 | 2.9 | 3.92 | - | 26257 | 0 | 26257
P01312 | 47.5 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.41 | -4.99 | 31.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 2166.1 | 112.6 | 2.38 | - | 138791 | 0 | 138791
P01313 | 55 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.7 | -5.18 | 32.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 2503.1 | 158.6 | 2.21 | - | 141277 | 0 | 141277
P01314 | 55 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -0.47 | -4.39 | 29 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 2254.1 | 122.1 | 2.23 | - | 130848 | 0 | 130848
P01315 | 55 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 1.12 | -3.38 | 25.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 1968 | 88 | 2.28 | - | 117377 | 0 | 117377
P01316 | 55 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 3.26 | -2.06 | 22.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 1 | 1622.2 | 56.2 | 2.38 | - | 99299 | 0 | 99299
P01317 | 55 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.74 | -0.57 | 18.6 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 1 | 1248.1 | 31.7 | 2.53 | - | 78292 | 0 | 78292
P01318 | 55 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.68 | 1.14 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 1 | 831.4 | 13.7 | 2.84 | - | 53443 | 0 | 53443
P01319 | 55 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.93 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 1 | 400.1 | 3.5 | 3.54 | - | 26315 | 0 | 26315
P01320 | 55 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -0.75 | -4.56 | 29.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 2307.2 | 129.6 | 2.22 | - | 133194 | 0 | 133194
P01321 | 62.5 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -0.83 | -4.62 | 29.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 2688.1 | 183.5 | 2.06 | - | 133889 | 0 | 133889
P01322 | 62.5 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | 0.21 | -3.95 | 27.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 2432.1 | 143.3 | 2.08 | - | 125052 | 0 | 125052
P01323 | 62.5 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 1.68 | -3.03 | 24.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 2124.5 | 103.8 | 2.12 | - | 112621 | 0 | 112621
P01324 | 62.5 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 3.62 | -1.84 | 21.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 1 | 1762.4 | 68 | 2.18 | - | 96192 | 0 | 96192
P01325 | 62.5 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.9 | -0.47 | 18.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 1 | 1371 | 39.1 | 2.31 | - | 76910 | 0 | 76910
P01326 | 62.5 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.79 | 1.2 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 1 | 911.3 | 16.8 | 2.56 | - | 52532 | 0 | 52532
P01327 | 62.5 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.91 | 2.91 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 1 | 441 | 4.3 | 3.15 | - | 26077 | 0 | 26077
P01328 | 62.5 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | 0 | -4.09 | 27.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 2482.3 | 150.8 | 2.08 | - | 126843 | 0 | 126843
P01329 | 70 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | 0.22 | -3.95 | 27.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 2920.5 | 215.2 | 1.92 | - | 125028 | 0 | 125028
P01330 | 70 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | 1.13 | -3.38 | 25.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 2641.3 | 169.6 | 1.92 | - | 117327 | 0 | 117327
P01331 | 70 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.44 | -2.56 | 23.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 2308.8 | 124.5 | 1.94 | - | 106233 | 0 | 106233
P01332 | 70 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 4.1 | -1.55 | 20.8 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 1 | 1937.2 | 83.4 | 1.99 | - | 92176 | 0 | 92176
P01333 | 70 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 6.19 | -0.3 | 18 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 1 | 1516.7 | 48.7 | 2.1 | - | 74469 | 0 | 74469
P01334 | 70 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.88 | 1.25 | 15 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 1 | 1021.2 | 21.5 | 2.31 | - | 51722 | 0 | 51722
P01335 | 70 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.91 | 2.91 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 1 | 500.8 | 5.5 | 2.81 | - | 26110 | 0 | 26110
P01336 | 70 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | 0.88 | -3.53 | 26.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 2707.8 | 179.5 | 1.92 | - | 119415 | 0 | 119415
P01337 | 56 | -20 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.6 | -5.11 | 31.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 2526 | 161.6 | 2.19 | - | 140389 | 0 | 140389
P01338 | 56 | -15 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -0.39 | -4.33 | 28.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 2275.8 | 124.6 | 2.21 | - | 130142 | 0 | 130142
P01339 | 56 | -10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 1.18 | -3.35 | 25.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 1988.6 | 90 | 2.25 | - | 116887 | 0 | 116887
P01340 | 56 | -5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 3.29 | -2.04 | 22 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 1 | 1640.2 | 57.6 | 2.35 | - | 98984 | 0 | 98984
P01341 | 56 | 0 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.76 | -0.56 | 18.5 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 1 | 1262.8 | 32.6 | 2.5 | - | 78125 | 0 | 78125
P01342 | 56 | 5 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.69 | 1.14 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 1 | 841.7 | 14 | 2.81 | - | 53374 | 0 | 53374
P01343 | 56 | 10 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.93 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 1 | 405.5 | 3.6 | 3.49 | - | 26315 | 0 | 26315
P01344 | 56 | -16 | 15 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -0.65 | -4.5 | 29.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 2327.8 | 132.2 | 2.2 | - | 132376 | 0 | 132376
P01345 | 25 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.31 | -17.04 | 21.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 697 | 17.7 | 2.76 | - | 56119 | 0 | 56119
P01346 | 25 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.21 | -13.92 | 15.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 428.4 | 6.2 | 3.06 | - | 35187 | 0 | 35187
P01347 | 25 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.72 | -11.83 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 138.4 | 1 | 4.46 | - | 11586 | 0 | 11586
P01348 | 25 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.92 | -14.62 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 488.7 | 8.8 | 2.99 | - | 39982 | 0 | 39982
P01349 | 32.5 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.1 | -16.83 | 20.6 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 731.4 | 20.2 | 2.53 | - | 54707 | 0 | 54707
P01350 | 32.5 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.2 | -13.9 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 459 | 7.9 | 2.82 | - | 35073 | 0 | 35073
P01351 | 32.5 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.69 | -11.8 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 146.5 | 1.1 | 4.03 | - | 11423 | 0 | 11423
P01352 | 32.5 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.8 | -14.5 | 16.7 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 514.7 | 10 | 2.73 | - | 39160 | 0 | 39160
P01353 | 40 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.98 | -16.7 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 782.1 | 23.5 | 2.35 | - | 53884 | 0 | 53884
P01354 | 40 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.13 | -13.84 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 491.3 | 9.4 | 2.61 | - | 34641 | 0 | 34641
P01355 | 40 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.66 | -11.78 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 155.6 | 1.2 | 3.65 | - | 11215 | 0 | 11215
P01356 | 40 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.73 | -14.43 | 16.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 551.2 | 11.7 | 2.52 | - | 38684 | 0 | 38684
P01357 | 47.5 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.81 | -16.53 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 840 | 27.5 | 2.18 | - | 52740 | 0 | 52740
P01358 | 47.5 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.07 | -13.78 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 531.6 | 11.1 | 2.4 | - | 34232 | 0 | 34232
P01359 | 47.5 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.69 | -11.8 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 173 | 1.4 | 3.29 | - | 11418 | 0 | 11418
P01360 | 47.5 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.6 | -14.31 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 590.1 | 13.6 | 2.32 | - | 37834 | 0 | 37834
P01361 | 55 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.56 | -16.27 | 19.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 903.9 | 32.2 | 2.02 | - | 51016 | 0 | 51016
P01362 | 55 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -11.93 | -15.4 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 573.6 | 13.2 | 2.16 | - | 33297 | 0 | 33297
P01363 | 55 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.66 | -11.78 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 187.9 | 1.6 | 2.95 | - | 11207 | 0 | 11207
P01364 | 55 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.49 | -14.19 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 641.7 | 16.4 | 2.1 | - | 37048 | 0 | 37048
P01365 | 62.5 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.22 | -15.93 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 978.6 | 38.5 | 1.82 | - | 48743 | 0 | 48743
P01366 | 62.5 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -11.83 | -15.23 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 634 | 16.2 | 1.96 | - | 32600 | 0 | 32600
P01367 | 62.5 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.63 | -11.75 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 208.1 | 1.9 | 2.62 | - | 11032 | 0 | 11032
P01368 | 62.5 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.33 | -14.04 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 704.7 | 19.9 | 1.91 | - | 36010 | 0 | 36010
P01369 | 70 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13.82 | -15.53 | 18.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1076.1 | 46.8 | 1.65 | - | 46069 | 0 | 46069
P01370 | 70 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -11.65 | -14.96 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 706.6 | 20.1 | 1.76 | - | 31386 | 0 | 31386
P01371 | 70 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.66 | -11.77 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 243.3 | 2.4 | 2.29 | - | 11196 | 0 | 11196
P01372 | 70 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.08 | -13.79 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 778.3 | 24.6 | 1.7 | - | 34324 | 0 | 34324
P01373 | 56 | -20 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.46 | -16.17 | 19.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 905.8 | 32.7 | 1.97 | - | 50341 | 0 | 50341
P01374 | 56 | -15 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -11.92 | -15.38 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 580.8 | 13.5 | 2.13 | - | 33213 | 0 | 33213
P01375 | 56 | -10 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.66 | -11.78 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 190.9 | 1.7 | 2.91 | - | 11223 | 0 | 11223
P01376 | 56 | -16 | -7 | 18194.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.47 | -14.18 | 16.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 649.6 | 16.8 | 2.08 | - | 36940 | 0 | 36940
P01377 | 25 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.51 | -16.23 | 19.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 774 | 21.5 | 2.66 | - | 62321 | 0 | 62321
P01378 | 25 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.82 | -15.22 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 487.1 | 8.7 | 2.94 | - | 40006 | 0 | 40006
P01379 | 25 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.59 | -11.71 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 157.2 | 1.2 | 4.18 | - | 13161 | 0 | 13161
P01380 | 25 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.37 | -14.08 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 544.8 | 10.7 | 2.86 | - | 44572 | 0 | 44572
P01381 | 32.5 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.4 | -16.12 | 19.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 821.2 | 24.6 | 2.49 | - | 61422 | 0 | 61422
P01382 | 32.5 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.76 | -15.13 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 516.7 | 9.9 | 2.73 | - | 39478 | 0 | 39478
P01383 | 32.5 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.57 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 166.9 | 1.3 | 3.77 | - | 13014 | 0 | 13014
P01384 | 32.5 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.32 | -14.02 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 579.8 | 12.4 | 2.65 | - | 44114 | 0 | 44114
P01385 | 40 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.25 | -15.96 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 873.4 | 28.4 | 2.31 | - | 60173 | 0 | 60173
P01386 | 40 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.71 | -15.06 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 554.6 | 11.5 | 2.52 | - | 39103 | 0 | 39103
P01387 | 40 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.58 | -11.71 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 182.2 | 1.5 | 3.43 | - | 13135 | 0 | 13135
P01388 | 40 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.25 | -13.96 | 15.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 620.4 | 14.4 | 2.45 | - | 43542 | 0 | 43542
P01389 | 47.5 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.04 | -15.75 | 18.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 930.4 | 32.6 | 2.16 | - | 58416 | 0 | 58416
P01390 | 47.5 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.59 | -14.87 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 590.9 | 13.4 | 2.29 | - | 38050 | 0 | 38050
P01391 | 47.5 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.57 | -11.69 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 196.6 | 1.7 | 3.08 | - | 12976 | 0 | 12976
P01392 | 47.5 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.1 | -13.81 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 660.5 | 16.7 | 2.23 | - | 42319 | 0 | 42319
P01393 | 55 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -13.75 | -15.45 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 991.7 | 38 | 1.96 | - | 55974 | 0 | 55974
P01394 | 55 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.5 | -14.75 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 642.9 | 16 | 2.1 | - | 37321 | 0 | 37321
P01395 | 55 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.54 | -11.67 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 214.5 | 2 | 2.76 | - | 12794 | 0 | 12794
P01396 | 55 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.99 | -15.5 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 717.1 | 19.9 | 2.05 | - | 41400 | 0 | 41400
P01397 | 62.5 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -13.46 | -15.16 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1075.6 | 45 | 1.81 | - | 53575 | 0 | 53575
P01398 | 62.5 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.39 | -14.6 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 708.1 | 19.6 | 1.91 | - | 36407 | 0 | 36407
P01399 | 62.5 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.51 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 235.6 | 2.3 | 2.46 | - | 12489 | 0 | 12489
P01400 | 62.5 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.88 | -15.31 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 792 | 24.2 | 1.9 | - | 40471 | 0 | 40471
P01401 | 70 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -13.09 | -14.79 | 17.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1180.4 | 54.5 | 1.65 | - | 50535 | 0 | 50535
P01402 | 70 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.16 | -14.3 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 776.8 | 23.9 | 1.7 | - | 34508 | 0 | 34508
P01403 | 70 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.48 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 266.6 | 2.8 | 2.16 | - | 12269 | 0 | 12269
P01404 | 70 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.63 | -14.93 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 870 | 29.6 | 1.69 | - | 38368 | 0 | 38368
P01405 | 56 | -20 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -13.72 | -15.42 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1002.5 | 38.9 | 1.94 | - | 55716 | 0 | 55716
P01406 | 56 | -15 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.49 | -14.73 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 650.7 | 16.4 | 2.08 | - | 37209 | 0 | 37209
P01407 | 56 | -10 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.55 | -11.68 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 218 | 2 | 2.72 | - | 12811 | 0 | 12811
P01408 | 56 | -16 | -7 | 22353.12 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.98 | -15.48 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 726.2 | 20.4 | 2.03 | - | 41297 | 0 | 41297
P01409 | 25 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.89 | -15.6 | 18.5 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 846.5 | 25.1 | 2.62 | - | 68161 | 0 | 68161
P01410 | 25 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.47 | -14.71 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 538.3 | 10.3 | 2.86 | - | 44211 | 0 | 44211
P01411 | 25 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.48 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 175.2 | 1.3 | 3.96 | - | 14667 | 0 | 14667
P01412 | 25 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.97 | -15.45 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 600 | 12.7 | 2.79 | - | 49083 | 0 | 49083
P01413 | 32.5 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.78 | -15.49 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 896.3 | 28.6 | 2.46 | - | 67041 | 0 | 67041
P01414 | 32.5 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.43 | -14.65 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 572.5 | 11.8 | 2.65 | - | 43744 | 0 | 43744
P01415 | 32.5 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.5 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 190.3 | 1.5 | 3.61 | - | 14839 | 0 | 14839
P01416 | 32.5 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.9 | -15.35 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 636.9 | 14.6 | 2.59 | - | 48455 | 0 | 48455
P01417 | 40 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.63 | -15.33 | 18 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 951 | 32.8 | 2.29 | - | 65514 | 0 | 65514
P01418 | 40 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.35 | -14.55 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 610.2 | 13.6 | 2.46 | - | 43019 | 0 | 43019
P01419 | 40 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.48 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 202.7 | 1.7 | 3.26 | - | 14617 | 0 | 14617
P01420 | 40 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.84 | -15.25 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 681.4 | 16.9 | 2.4 | - | 47820 | 0 | 47820
P01421 | 47.5 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.45 | -15.16 | 17.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1016.2 | 37.9 | 2.14 | - | 63801 | 0 | 63801
P01422 | 47.5 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.28 | -14.45 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 656.6 | 16 | 2.28 | - | 42281 | 0 | 42281
P01423 | 47.5 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.45 | -11.6 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 217.6 | 1.9 | 2.94 | - | 14356 | 0 | 14356
P01424 | 47.5 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.69 | -15.01 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 723 | 19.6 | 2.19 | - | 46326 | 0 | 46326
P01425 | 55 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.15 | -14.85 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1076.9 | 43.6 | 1.96 | - | 60782 | 0 | 60782
P01426 | 55 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.13 | -14.26 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 703 | 18.7 | 2.06 | - | 40809 | 0 | 40809
P01427 | 55 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.47 | -11.61 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 243.9 | 2.3 | 2.65 | - | 14545 | 0 | 14545
P01428 | 55 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.57 | -14.84 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 781.8 | 23.1 | 2.02 | - | 45134 | 0 | 45134
P01429 | 62.5 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.87 | -14.57 | 16.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1165.1 | 51.5 | 1.8 | - | 58030 | 0 | 58030
P01430 | 62.5 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.01 | -14.12 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 771.3 | 22.7 | 1.88 | - | 39660 | 0 | 39660
P01431 | 62.5 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.44 | -11.59 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 269.2 | 2.7 | 2.35 | - | 14272 | 0 | 14272
P01432 | 62.5 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.4 | -14.61 | 14.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 851 | 27.6 | 1.85 | - | 43486 | 0 | 43486
P01433 | 70 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.49 | -14.19 | 16.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1266.7 | 61.3 | 1.64 | - | 54229 | 0 | 54229
P01434 | 70 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -10.78 | -13.78 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 840.8 | 27.4 | 1.68 | - | 37350 | 0 | 37350
P01435 | 70 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.42 | -11.57 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 305.3 | 3.4 | 2.06 | - | 14048 | 0 | 14048
P01436 | 70 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.19 | -14.34 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 940 | 33.8 | 1.67 | - | 41456 | 0 | 41456
P01437 | 56 | -20 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.11 | -14.81 | 17.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1085.4 | 44.4 | 1.93 | - | 60379 | 0 | 60379
P01438 | 56 | -15 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.11 | -14.24 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 711.2 | 19.2 | 2.04 | - | 40669 | 0 | 40669
P01439 | 56 | -10 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.43 | -11.58 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 240.3 | 2.3 | 2.6 | - | 14123 | 0 | 14123
P01440 | 56 | -16 | -7 | 26641.8 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.55 | -14.82 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 791.5 | 23.7 | 1.99 | - | 45008 | 0 | 45008
P01441 | 25 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.38 | -15.08 | 17.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 909 | 28.4 | 2.6 | - | 73196 | 0 | 73196
P01442 | 25 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.17 | -14.31 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 582.5 | 11.8 | 2.8 | - | 47841 | 0 | 47841
P01443 | 25 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.4 | -11.56 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 192.5 | 1.5 | 3.78 | - | 16119 | 0 | 16119
P01444 | 25 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.64 | -14.95 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 651 | 14.7 | 2.73 | - | 53257 | 0 | 53257
P01445 | 32.5 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.24 | -14.94 | 17.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 957.4 | 32 | 2.44 | - | 71606 | 0 | 71606
P01446 | 32.5 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.12 | -14.25 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 618.2 | 13.5 | 2.6 | - | 47232 | 0 | 47232
P01447 | 32.5 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.42 | -11.57 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 209.1 | 1.7 | 3.45 | - | 16313 | 0 | 16313
P01448 | 32.5 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.58 | -14.86 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 690.4 | 16.8 | 2.54 | - | 52525 | 0 | 52525
P01449 | 40 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.11 | -14.82 | 17.2 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1018.8 | 36.7 | 2.29 | - | 70187 | 0 | 70187
P01450 | 40 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.98 | -14.08 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 647.7 | 15.3 | 2.39 | - | 45663 | 0 | 45663
P01451 | 40 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.4 | -11.55 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 222.6 | 1.9 | 3.11 | - | 16051 | 0 | 16051
P01452 | 40 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.5 | -14.75 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 736.6 | 19.4 | 2.36 | - | 51699 | 0 | 51699
P01453 | 47.5 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -12.94 | -14.64 | 16.9 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1085.4 | 42.4 | 2.13 | - | 68149 | 0 | 68149
P01454 | 47.5 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.91 | -13.91 | 14.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 696.2 | 17.9 | 2.21 | - | 44834 | 0 | 44834
P01455 | 47.5 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.41 | -11.56 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 246 | 2.3 | 2.83 | - | 16234 | 0 | 16234
P01456 | 47.5 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.38 | -14.59 | 14.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 785.3 | 22.3 | 2.2 | - | 50320 | 0 | 50320
P01457 | 55 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -12.68 | -14.38 | 16.5 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1155.3 | 48.6 | 1.98 | - | 65203 | 0 | 65203
P01458 | 55 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.77 | -13.77 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 744.4 | 20.9 | 2 | - | 43210 | 0 | 43210
P01459 | 55 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.38 | -11.54 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 266.3 | 2.6 | 2.54 | - | 15880 | 0 | 15880
P01460 | 55 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.21 | -14.36 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 836.4 | 25.9 | 2 | - | 48285 | 0 | 48285
P01461 | 62.5 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -12.35 | -14.06 | 16.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1233.9 | 56.5 | 1.8 | - | 61456 | 0 | 61456
P01462 | 62.5 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.69 | -13.69 | 13.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 823.1 | 25.4 | 1.86 | - | 42321 | 0 | 42321
P01463 | 62.5 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.35 | -11.51 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 292.5 | 3.1 | 2.27 | - | 15506 | 0 | 15506
P01464 | 62.5 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.06 | -14.18 | 14.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 912.1 | 31.1 | 1.83 | - | 46604 | 0 | 46604
P01465 | 70 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.99 | -15.5 | 15.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1338.2 | 67.1 | 1.64 | - | 57290 | 0 | 57290
P01466 | 70 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.5 | -13.5 | 13.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 904 | 30.8 | 1.69 | - | 40191 | 0 | 40191
P01467 | 70 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.32 | -11.49 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 329.5 | 3.8 | 2 | - | 15164 | 0 | 15164
P01468 | 70 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.77 | -13.77 | 13.9 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 981.9 | 36.6 | 1.65 | - | 43303 | 0 | 43303
P01469 | 56 | -20 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -12.65 | -14.35 | 16.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1166.3 | 49.6 | 1.96 | - | 64818 | 0 | 64818
P01470 | 56 | -15 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.75 | -13.75 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 753.2 | 21.4 | 1.98 | - | 43070 | 0 | 43070
P01471 | 56 | -10 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.39 | -11.54 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 270.5 | 2.7 | 2.51 | - | 15899 | 0 | 15899
P01472 | 56 | -16 | -7 | 30930.48 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.19 | -14.34 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 845.5 | 26.5 | 1.97 | - | 48078 | 0 | 48078
P01473 | 25 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.97 | -14.67 | 17 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 965.7 | 31.4 | 2.58 | - | 77756 | 0 | 77756
P01474 | 25 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.91 | -13.91 | 14.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 619.1 | 13.1 | 2.77 | - | 50843 | 0 | 50843
P01475 | 25 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.33 | -11.49 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 206.3 | 1.6 | 3.67 | - | 17273 | 0 | 17273
P01476 | 25 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.35 | -14.54 | 14.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 691.5 | 16.3 | 2.7 | - | 56571 | 0 | 56571
P01477 | 32.5 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.88 | -14.59 | 16.9 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 1024.5 | 35.9 | 2.42 | - | 76624 | 0 | 76624
P01478 | 32.5 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.85 | -13.85 | 14 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 655.9 | 15 | 2.57 | - | 50115 | 0 | 50115
P01479 | 32.5 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.34 | -11.5 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 224 | 1.9 | 3.35 | - | 17471 | 0 | 17471
P01480 | 32.5 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.28 | -14.45 | 14.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 731.7 | 18.6 | 2.51 | - | 55669 | 0 | 55669
P01481 | 40 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.69 | -14.39 | 16.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 1074.6 | 40.2 | 2.28 | - | 74030 | 0 | 74030
P01482 | 40 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.74 | -13.74 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 690.3 | 17.1 | 2.35 | - | 48668 | 0 | 48668
P01483 | 40 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.32 | -11.48 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 238.2 | 2.1 | 3.03 | - | 17170 | 0 | 17170
P01484 | 40 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.2 | -14.35 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 779 | 21.3 | 2.34 | - | 54671 | 0 | 54671
P01485 | 47.5 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.42 | -14.13 | 16.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 1124.6 | 45.2 | 2.1 | - | 70610 | 0 | 70610
P01486 | 47.5 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.64 | -13.64 | 13.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 736.2 | 19.7 | 2.19 | - | 47410 | 0 | 47410
P01487 | 47.5 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.33 | -11.49 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 262.9 | 2.5 | 2.75 | - | 17349 | 0 | 17349
P01488 | 47.5 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.08 | -14.2 | 14.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 828 | 24.4 | 2.18 | - | 53054 | 0 | 53054
P01489 | 55 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.21 | -13.92 | 15.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1202.4 | 52.4 | 1.95 | - | 67866 | 0 | 67866
P01490 | 55 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.56 | -13.56 | 13.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 797.4 | 23.3 | 2.02 | - | 46289 | 0 | 46289
P01491 | 55 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.31 | -11.47 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 285.4 | 2.9 | 2.47 | - | 17020 | 0 | 17020
P01492 | 55 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.96 | -14.06 | 14.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 894 | 28.8 | 2.01 | - | 51609 | 0 | 51609
P01493 | 62.5 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.94 | -15.42 | 15.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1292.5 | 61.1 | 1.8 | - | 64375 | 0 | 64375
P01494 | 62.5 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.38 | -13.38 | 13.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 856.8 | 27.4 | 1.81 | - | 44053 | 0 | 44053
P01495 | 62.5 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.28 | -11.45 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 313.7 | 3.4 | 2.2 | - | 16631 | 0 | 16631
P01496 | 62.5 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.71 | -13.71 | 13.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 944.6 | 33.2 | 1.8 | - | 48267 | 0 | 48267
P01497 | 70 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.59 | -14.87 | 15 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1394.7 | 71.6 | 1.65 | - | 59710 | 0 | 59710
P01498 | 70 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.2 | -13.2 | 13.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 938.4 | 33.1 | 1.66 | - | 41684 | 0 | 41684
P01499 | 70 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.24 | -11.42 | 11.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 351 | 4.3 | 1.94 | - | 16152 | 0 | 16152
P01500 | 70 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.51 | -13.51 | 13.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 1034.8 | 40.1 | 1.64 | - | 45676 | 0 | 45676
P01501 | 56 | -20 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.19 | -13.9 | 15.8 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1216.6 | 53.5 | 1.93 | - | 67612 | 0 | 67612
P01502 | 56 | -15 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.54 | -13.54 | 13.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 805.7 | 23.8 | 1.99 | - | 46077 | 0 | 46077
P01503 | 56 | -10 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.31 | -11.47 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 289.9 | 3 | 2.44 | - | 17039 | 0 | 17039
P01504 | 56 | -16 | -7 | 35089.2 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.95 | -13.95 | 14.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 903.2 | 29.5 | 1.99 | - | 51361 | 0 | 51361
P01505 | 25 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.19 | -15.9 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 1 | 818.7 | 23.7 | 2.63 | - | 65921 | 0 | 65921
P01506 | 25 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.61 | -14.9 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 1 | 514.2 | 9.5 | 2.89 | - | 42228 | 0 | 42228
P01507 | 25 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.54 | -11.67 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 1 | 168.3 | 1.3 | 4.03 | - | 14089 | 0 | 14089
P01508 | 25 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.16 | -13.87 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 1 | 578.1 | 11.9 | 2.81 | - | 47296 | 0 | 47296
P01509 | 32.5 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.04 | -15.74 | 18.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 1 | 862.1 | 26.8 | 2.47 | - | 64477 | 0 | 64477
P01510 | 32.5 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.58 | -14.86 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 1 | 548.9 | 11 | 2.68 | - | 41937 | 0 | 41937
P01511 | 32.5 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.5 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 1 | 176.5 | 1.4 | 3.67 | - | 13766 | 0 | 13766
P01512 | 32.5 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.1 | -13.81 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 1 | 614 | 13.7 | 2.6 | - | 46713 | 0 | 46713
P01513 | 40 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.81 | -15.52 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 1 | 905.8 | 30.4 | 2.28 | - | 62404 | 0 | 62404
P01514 | 40 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.44 | -14.66 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 1 | 576.5 | 12.5 | 2.46 | - | 40648 | 0 | 40648
P01515 | 40 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.53 | -11.66 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 1 | 194.1 | 1.6 | 3.32 | - | 13992 | 0 | 13992
P01516 | 40 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.03 | -13.73 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 1 | 656.1 | 15.8 | 2.42 | - | 46046 | 0 | 46046
P01517 | 47.5 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.7 | -15.4 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 1 | 977.3 | 35.5 | 2.14 | - | 61360 | 0 | 61360
P01518 | 47.5 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.37 | -14.57 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 1 | 621.5 | 14.6 | 2.27 | - | 40020 | 0 | 40020
P01519 | 47.5 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.5 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 1 | 207.9 | 1.8 | 3 | - | 13722 | 0 | 13722
P01520 | 47.5 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.94 | -15.41 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 1 | 706.4 | 18.6 | 2.23 | - | 45261 | 0 | 45261
P01521 | 55 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.46 | -15.16 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 1 | 1048.9 | 41.4 | 1.99 | - | 59199 | 0 | 59199
P01522 | 55 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.28 | -14.46 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 1 | 676.2 | 17.5 | 2.08 | - | 39251 | 0 | 39251
P01523 | 55 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.47 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 1 | 226.4 | 2.1 | 2.69 | - | 13505 | 0 | 13505
P01524 | 55 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.79 | -15.17 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 1 | 760.3 | 21.8 | 2.06 | - | 43890 | 0 | 43890
P01525 | 62.5 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.12 | -14.82 | 17.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 1 | 1125 | 48.6 | 1.8 | - | 56035 | 0 | 56035
P01526 | 62.5 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.11 | -14.24 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 1 | 732.4 | 20.9 | 1.87 | - | 37659 | 0 | 37659
P01527 | 62.5 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.49 | -11.63 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 1 | 257.5 | 2.6 | 2.4 | - | 13649 | 0 | 13649
P01528 | 62.5 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.59 | -14.88 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 1 | 823.1 | 26 | 1.86 | - | 42059 | 0 | 42059
P01529 | 70 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.73 | -14.44 | 16.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 1 | 1227 | 58 | 1.65 | - | 52527 | 0 | 52527
P01530 | 70 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11 | -14.11 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 1 | 825.3 | 26.4 | 1.71 | - | 36658 | 0 | 36658
P01531 | 70 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.42 | -11.57 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 1 | 282.9 | 3.1 | 2.1 | - | 13019 | 0 | 13019
P01532 | 70 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.37 | -14.57 | 14.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 1 | 908.5 | 31.9 | 1.69 | - | 40064 | 0 | 40064
P01533 | 56 | -20 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.43 | -15.13 | 17.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 1 | 1059.5 | 42.3 | 1.97 | - | 58885 | 0 | 58885
P01534 | 56 | -15 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.27 | -14.44 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 1 | 684.1 | 17.9 | 2.06 | - | 39121 | 0 | 39121
P01535 | 56 | -10 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.48 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 1 | 230.1 | 2.2 | 2.65 | - | 13526 | 0 | 13526
P01536 | 56 | -16 | -7 | 24692.4 | 1 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.71 | -15.06 | 15.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 1 | 759.6 | 22 | 2.01 | - | 43194 | 0 | 43194
P00001 | 25 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.48 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 328.2 | 3.7 | 3.48 | - | 30952 | 0 | 30952
P00002 | 25 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.97 | -15.8 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 69.8 | 0.5 | 6.31 | - | 6693 | 0 | 6693
P00003 | 25 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.63 | -16.46 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 117.6 | 0.9 | 4.93 | - | 11246 | 0 | 11246
P00004 | 32.5 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.48 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 348.1 | 4.1 | 3.21 | - | 30963 | 0 | 30963
P00005 | 32.5 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.96 | -15.78 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 72.9 | 0.6 | 5.73 | - | 6604 | 0 | 6604
P00006 | 32.5 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.65 | -16.48 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 126.3 | 1.1 | 4.48 | - | 11401 | 0 | 11401
P00007 | 40 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.47 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 370.5 | 4.7 | 2.96 | - | 30930 | 0 | 30930
P00008 | 40 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.98 | -15.81 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 80.4 | 0.6 | 5.18 | - | 6785 | 0 | 6785
P00009 | 40 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.62 | -16.45 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 132.2 | 1.2 | 4.06 | - | 11204 | 0 | 11204
P00010 | 47.5 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.45 | -19.33 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 395.1 | 5.6 | 2.75 | - | 30769 | 0 | 30769
P00011 | 47.5 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.96 | -15.79 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 83.6 | 0.7 | 4.74 | - | 6648 | 0 | 6648
P00012 | 47.5 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.64 | -16.47 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 143.1 | 1.3 | 3.7 | - | 11331 | 0 | 11331
P00013 | 55 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.36 | -19.24 | 15 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 417.7 | 6.9 | 2.51 | - | 30129 | 0 | 30129
P00014 | 55 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.77 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 88.7 | 0.7 | 4.31 | - | 6538 | 0 | 6538
P00015 | 55 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.61 | -16.45 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 152 | 1.4 | 3.36 | - | 11160 | 0 | 11160
P00016 | 62.5 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.29 | -19.17 | 14.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 447.8 | 8.7 | 2.32 | - | 29653 | 0 | 29653
P00017 | 62.5 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.98 | -15.81 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 100.5 | 0.9 | 3.86 | - | 6760 | 0 | 6760
P00018 | 62.5 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.63 | -16.47 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 167.2 | 1.7 | 3.05 | - | 11283 | 0 | 11283
P00019 | 70 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.21 | -19.08 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 483.8 | 11.1 | 2.14 | - | 29088 | 0 | 29088
P00020 | 70 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.96 | -15.79 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 107.4 | 1 | 3.5 | - | 6628 | 0 | 6628
P00021 | 70 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.61 | -16.44 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 180.8 | 1.9 | 2.74 | - | 11104 | 0 | 11104
P00022 | 56 | -20 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.35 | -19.23 | 14.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 421.4 | 7.1 | 2.48 | - | 30069 | 0 | 30069
P00023 | 56 | -15 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.78 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 90.1 | 0.8 | 4.26 | - | 6570 | 0 | 6570
P00024 | 56 | -16 | -13 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.62 | -16.45 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 153.9 | 1.5 | 3.31 | - | 11177 | 0 | 11177
P00025 | 25 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.15 | -19.03 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 374.2 | 4.4 | 3.34 | - | 35285 | 0 | 35285
P00026 | 25 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.9 | -15.73 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 79.7 | 0.6 | 5.88 | - | 7642 | 0 | 7642
P00027 | 25 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.56 | -16.39 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 138.7 | 1.1 | 4.64 | - | 13259 | 0 | 13259
P00028 | 32.5 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.14 | -19.01 | 14.6 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 395 | 5.3 | 3.09 | - | 35141 | 0 | 35141
P00029 | 32.5 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.71 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 83.2 | 0.6 | 5.33 | - | 7532 | 0 | 7532
P00030 | 32.5 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.54 | -16.37 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 144.6 | 1.2 | 4.17 | - | 13049 | 0 | 13049
P00031 | 40 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.12 | -18.99 | 14.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 418.8 | 6.4 | 2.86 | - | 34968 | 0 | 34968
P00032 | 40 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.9 | -15.73 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 90.2 | 0.7 | 4.86 | - | 7678 | 0 | 7678
P00033 | 40 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.55 | -16.38 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 155.4 | 1.4 | 3.81 | - | 13175 | 0 | 13175
P00034 | 47.5 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.01 | -18.88 | 14.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 437.5 | 7.7 | 2.62 | - | 34074 | 0 | 34074
P00035 | 47.5 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.72 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 95.3 | 0.8 | 4.41 | - | 7575 | 0 | 7575
P00036 | 47.5 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.52 | -16.35 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 162.5 | 1.5 | 3.47 | - | 12869 | 0 | 12869
P00037 | 55 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.97 | -18.84 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 467.4 | 9.5 | 2.44 | - | 33711 | 0 | 33711
P00038 | 55 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.91 | -15.74 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 104.8 | 0.9 | 4 | - | 7726 | 0 | 7726
P00039 | 55 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.54 | -16.38 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 178.6 | 1.8 | 3.16 | - | 13109 | 0 | 13109
P00040 | 62.5 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.89 | -18.76 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 499.4 | 11.6 | 2.26 | - | 33065 | 0 | 33065
P00041 | 62.5 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.9 | -15.73 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 112.5 | 1 | 3.62 | - | 7629 | 0 | 7629
P00042 | 62.5 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.51 | -16.34 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 189.4 | 2 | 2.87 | - | 12787 | 0 | 12787
P00043 | 70 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 537.8 | 13.6 | 2.09 | - | 32335 | 0 | 32335
P00044 | 70 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.71 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 122 | 1.1 | 3.26 | - | 7533 | 0 | 7533
P00045 | 70 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.48 | -16.31 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 204.5 | 2.2 | 2.58 | - | 12559 | 0 | 12559
P00046 | 56 | -20 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.95 | -18.83 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 470.7 | 9.8 | 2.41 | - | 33582 | 0 | 33582
P00047 | 56 | -15 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.91 | -15.74 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 106.2 | 0.9 | 3.95 | - | 7746 | 0 | 7746
P00048 | 56 | -16 | -13 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.55 | -16.38 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 180.7 | 1.8 | 3.12 | - | 13125 | 0 | 13125
P00049 | 25 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.85 | -18.72 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 413.4 | 5.8 | 3.24 | - | 38990 | 0 | 38990
P00050 | 25 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.84 | -15.67 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 88.7 | 0.7 | 5.55 | - | 8507 | 0 | 8507
P00051 | 25 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.45 | -16.28 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 153.6 | 1.3 | 4.41 | - | 14684 | 0 | 14684
P00052 | 32.5 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.82 | -18.69 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 435.1 | 7 | 3.01 | - | 38710 | 0 | 38710
P00053 | 32.5 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 95.5 | 0.7 | 5.05 | - | 8647 | 0 | 8647
P00054 | 32.5 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.43 | -16.26 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 159.9 | 1.4 | 3.98 | - | 14428 | 0 | 14428
P00055 | 40 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 462.3 | 8.6 | 2.79 | - | 38601 | 0 | 38601
P00056 | 40 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.84 | -15.67 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 100.1 | 0.8 | 4.58 | - | 8519 | 0 | 8519
P00057 | 40 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.44 | -16.27 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 172.2 | 1.6 | 3.63 | - | 14598 | 0 | 14598
P00058 | 47.5 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.74 | -18.6 | 14.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 485.7 | 10.2 | 2.61 | - | 37823 | 0 | 37823
P00059 | 47.5 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.83 | -15.65 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 105.3 | 0.9 | 4.17 | - | 8368 | 0 | 8368
P00060 | 47.5 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.42 | -16.25 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 181.6 | 1.8 | 3.29 | - | 14380 | 0 | 14380
P00061 | 55 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.64 | -18.5 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 510.7 | 11.8 | 2.38 | - | 36835 | 0 | 36835
P00062 | 55 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 116.4 | 1 | 3.77 | - | 8583 | 0 | 8583
P00063 | 55 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.43 | -16.26 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 197.5 | 2 | 3.01 | - | 14499 | 0 | 14499
P00064 | 62.5 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.57 | -18.44 | 13.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 546.2 | 13.6 | 2.21 | - | 36165 | 0 | 36165
P00065 | 62.5 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.83 | -15.66 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 125.2 | 1.1 | 3.41 | - | 8449 | 0 | 8449
P00066 | 62.5 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.41 | -16.24 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 211.1 | 2.3 | 2.72 | - | 14251 | 0 | 14251
P00067 | 70 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.5 | -18.36 | 13.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 588.9 | 15.9 | 2.04 | - | 35408 | 0 | 35408
P00068 | 70 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.82 | -15.65 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 135 | 1.3 | 3.07 | - | 8333 | 0 | 8333
P00069 | 70 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.42 | -16.25 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 234.1 | 2.6 | 2.47 | - | 14380 | 0 | 14380
P00070 | 56 | -20 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.63 | -18.5 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 515.4 | 12 | 2.36 | - | 36770 | 0 | 36770
P00071 | 56 | -15 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 117.6 | 1 | 3.73 | - | 8583 | 0 | 8583
P00072 | 56 | -16 | -13 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.43 | -16.27 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 199.8 | 2 | 2.98 | - | 14516 | 0 | 14516
P00073 | 25 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.61 | -18.47 | 13.9 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 449.5 | 7.4 | 3.16 | - | 42391 | 0 | 42391
P00074 | 25 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.79 | -15.62 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 96.9 | 0.7 | 5.3 | - | 9294 | 0 | 9294
P00075 | 25 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.37 | -16.2 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 167.8 | 1.4 | 4.24 | - | 16040 | 0 | 16040
P00076 | 32.5 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.5 | -18.36 | 13.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 462.3 | 8.5 | 2.9 | - | 41128 | 0 | 41128
P00077 | 32.5 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 104.3 | 0.8 | 4.82 | - | 9442 | 0 | 9442
P00078 | 32.5 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.39 | -16.22 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 181.2 | 1.6 | 3.83 | - | 16352 | 0 | 16352
P00079 | 40 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.46 | -18.32 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 487 | 10.1 | 2.71 | - | 40657 | 0 | 40657
P00080 | 40 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.62 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 109.8 | 0.9 | 4.36 | - | 9347 | 0 | 9347
P00081 | 40 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.35 | -16.19 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 187.7 | 1.8 | 3.49 | - | 15915 | 0 | 15915
P00082 | 47.5 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.42 | -18.28 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 515.7 | 11.6 | 2.53 | - | 40167 | 0 | 40167
P00083 | 47.5 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.81 | -15.64 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 119.8 | 1 | 3.97 | - | 9524 | 0 | 9524
P00084 | 47.5 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.37 | -16.2 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 203 | 2 | 3.2 | - | 16074 | 0 | 16074
P00085 | 55 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.37 | -18.23 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 548.4 | 13.3 | 2.35 | - | 39551 | 0 | 39551
P00086 | 55 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 127.3 | 1.1 | 3.6 | - | 9385 | 0 | 9385
P00087 | 55 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.34 | -16.17 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 214.8 | 2.2 | 2.9 | - | 15772 | 0 | 15772
P00088 | 62.5 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.25 | -18.11 | 13.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 576.5 | 15 | 2.14 | - | 38174 | 0 | 38174
P00089 | 62.5 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.78 | -15.61 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 135.8 | 1.3 | 3.26 | - | 9208 | 0 | 9208
P00090 | 62.5 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.35 | -16.18 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 235.5 | 2.6 | 2.65 | - | 15899 | 0 | 15899
P00091 | 70 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.15 | -18.01 | 13.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 616.2 | 17.3 | 2 | - | 37050 | 0 | 37050
P00092 | 70 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 152 | 1.5 | 2.94 | - | 9385 | 0 | 9385
P00093 | 70 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.33 | -16.16 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 253.5 | 3 | 2.39 | - | 15569 | 0 | 15569
P00094 | 56 | -20 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.35 | -18.21 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 552.3 | 13.5 | 2.32 | - | 39408 | 0 | 39408
P00095 | 56 | -15 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 128.6 | 1.1 | 3.56 | - | 9385 | 0 | 9385
P00096 | 56 | -16 | -13 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.34 | -16.17 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 217.4 | 2.3 | 2.87 | - | 15792 | 0 | 15792
P00097 | 25 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.38 | -18.24 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 477.7 | 8.8 | 3.13 | - | 45052 | 0 | 45052
P00098 | 25 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.75 | -15.58 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 104.4 | 0.8 | 5.1 | - | 10009 | 0 | 10009
P00099 | 25 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.3 | -16.13 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 180.8 | 1.6 | 4.09 | - | 17280 | 0 | 17280
P00100 | 32.5 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.34 | -18.2 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 501 | 10.3 | 2.9 | - | 44567 | 0 | 44567
P00101 | 32.5 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.73 | -15.56 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 107.9 | 0.9 | 4.63 | - | 9772 | 0 | 9772
P00102 | 32.5 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.31 | -16.14 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 193.8 | 1.8 | 3.73 | - | 17490 | 0 | 17490
P00103 | 40 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.25 | -18.11 | 13.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 519.6 | 11.4 | 2.66 | - | 43381 | 0 | 43381
P00104 | 40 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.75 | -15.58 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 117.9 | 1 | 4.2 | - | 10036 | 0 | 10036
P00105 | 40 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.29 | -16.12 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 202.2 | 1.9 | 3.38 | - | 17139 | 0 | 17139
P00106 | 47.5 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.19 | -18.05 | 13.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 546 | 12.8 | 2.49 | - | 42520 | 0 | 42520
P00107 | 47.5 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.74 | -15.56 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 123.4 | 1.1 | 3.83 | - | 9807 | 0 | 9807
P00108 | 47.5 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.3 | -16.13 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 218.4 | 2.2 | 3.1 | - | 17288 | 0 | 17288
P00109 | 55 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.14 | -17.99 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 579.8 | 14.6 | 2.32 | - | 41820 | 0 | 41820
P00110 | 55 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 144.4 | 1.3 | 3.52 | - | 10647 | 0 | 10647
P00111 | 55 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.27 | -16.1 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 231 | 2.5 | 2.81 | - | 16962 | 0 | 16962
P00112 | 62.5 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.07 | -17.93 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 618.4 | 16.8 | 2.15 | - | 40944 | 0 | 40944
P00113 | 62.5 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.74 | -15.57 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 145.2 | 1.4 | 3.15 | - | 9848 | 0 | 9848
P00114 | 62.5 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.28 | -16.11 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 252.6 | 2.9 | 2.57 | - | 17054 | 0 | 17054
P00115 | 70 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -15.99 | -17.84 | 13.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 662.3 | 19.4 | 2 | - | 39823 | 0 | 39823
P00116 | 70 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 172.5 | 1.7 | 2.86 | - | 10647 | 0 | 10647
P00117 | 70 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.25 | -16.08 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 271.4 | 3.3 | 2.32 | - | 16671 | 0 | 16671
P00118 | 56 | -20 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.13 | -17.98 | 13.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 584.7 | 14.9 | 2.3 | - | 41714 | 0 | 41714
P00119 | 56 | -15 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 145.9 | 1.3 | 3.47 | - | 10647 | 0 | 10647
P00120 | 56 | -16 | -13 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.27 | -16.1 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 233.5 | 2.5 | 2.78 | - | 16962 | 0 | 16962
P00121 | 25 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.94 | -18.81 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 392.1 | 5.1 | 3.21 | - | 36973 | 0 | 36973
P00122 | 25 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 84.4 | 0.6 | 5.7 | - | 8096 | 0 | 8096
P00123 | 25 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.5 | -16.33 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 146.7 | 1.2 | 4.52 | - | 14023 | 0 | 14023
P00124 | 32.5 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.92 | -18.79 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 413.2 | 6.1 | 2.98 | - | 36759 | 0 | 36759
P00125 | 32.5 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.88 | -15.71 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 91.4 | 0.7 | 5.18 | - | 8278 | 0 | 8278
P00126 | 32.5 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.47 | -16.3 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 152.8 | 1.3 | 4.07 | - | 13789 | 0 | 13789
P00127 | 40 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.87 | -18.74 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 434.4 | 7.3 | 2.78 | - | 36269 | 0 | 36269
P00128 | 40 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.87 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 95.6 | 0.8 | 4.7 | - | 8132 | 0 | 8132
P00129 | 40 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.49 | -16.32 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 164.4 | 1.5 | 3.72 | - | 13940 | 0 | 13940
P00130 | 47.5 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.82 | -18.69 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 460 | 8.8 | 2.59 | - | 35829 | 0 | 35829
P00131 | 47.5 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 100.6 | 0.8 | 4.28 | - | 7999 | 0 | 7999
P00132 | 47.5 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.46 | -16.29 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 173.1 | 1.6 | 3.37 | - | 13703 | 0 | 13703
P00133 | 55 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.77 | -18.64 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 490.2 | 10.9 | 2.41 | - | 35356 | 0 | 35356
P00134 | 55 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 111.2 | 1 | 3.88 | - | 8203 | 0 | 8203
P00135 | 55 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.48 | -16.31 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 188.6 | 1.9 | 3.08 | - | 13846 | 0 | 13846
P00136 | 62.5 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.66 | -18.52 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 518.1 | 12.5 | 2.2 | - | 34305 | 0 | 34305
P00137 | 62.5 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 119 | 1.1 | 3.5 | - | 8069 | 0 | 8069
P00138 | 62.5 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.45 | -16.28 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 201.1 | 2.1 | 2.79 | - | 13576 | 0 | 13576
P00139 | 70 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.58 | -18.44 | 13.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 558 | 14.6 | 2.03 | - | 33548 | 0 | 33548
P00140 | 70 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 128.8 | 1.2 | 3.15 | - | 7954 | 0 | 7954
P00141 | 70 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.42 | -16.25 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 217 | 2.4 | 2.5 | - | 13326 | 0 | 13326
P00142 | 56 | -20 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.76 | -18.63 | 14.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 494.4 | 11.1 | 2.39 | - | 35272 | 0 | 35272
P00143 | 56 | -15 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.88 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 112.8 | 1 | 3.82 | - | 8227 | 0 | 8227
P00144 | 56 | -16 | -13 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.48 | -16.31 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 190.9 | 1.9 | 3.05 | - | 13864 | 0 | 13864
P00145 | 25 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.2 | -16.91 | 22.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 656.6 | 14.5 | 3.28 | - | 61920 | 0 | 61920
P00146 | 25 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.04 | -13.72 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 423.5 | 5.3 | 3.75 | - | 40616 | 0 | 40616
P00147 | 25 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.39 | -11.5 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 165.1 | 1.1 | 5.11 | - | 16098 | 0 | 16098
P00148 | 25 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.68 | -14.36 | 18 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 470 | 7.4 | 3.62 | - | 44932 | 0 | 44932
P00149 | 32.5 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.12 | -16.82 | 22.6 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 689.8 | 16.4 | 3.05 | - | 61363 | 0 | 61363
P00150 | 32.5 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.01 | -13.69 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 446 | 6.5 | 3.43 | - | 40398 | 0 | 40398
P00151 | 32.5 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.41 | -11.52 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 175.9 | 1.2 | 4.6 | - | 16213 | 0 | 16213
P00152 | 32.5 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.65 | -14.32 | 18 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 495.3 | 8.4 | 3.32 | - | 44703 | 0 | 44703
P00153 | 40 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.99 | -16.69 | 22.3 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 724.3 | 18.4 | 2.85 | - | 60468 | 0 | 60468
P00154 | 40 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.96 | -15.37 | 16.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 471.2 | 7.8 | 3.17 | - | 40098 | 0 | 40098
P00155 | 40 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.44 | -11.54 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 189 | 1.4 | 4.17 | - | 16382 | 0 | 16382
P00156 | 40 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.61 | -14.28 | 17.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 524.1 | 9.7 | 3.07 | - | 44430 | 0 | 44430
P00157 | 47.5 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.85 | -16.55 | 22 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 764.8 | 21 | 2.65 | - | 59565 | 0 | 59565
P00158 | 47.5 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.84 | -15.18 | 16.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 494.3 | 8.9 | 2.9 | - | 39293 | 0 | 39293
P00159 | 47.5 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.46 | -11.56 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 204.1 | 1.6 | 3.8 | - | 16548 | 0 | 16548
P00160 | 47.5 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.55 | -14.23 | 17.8 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 556.6 | 11.1 | 2.84 | - | 44063 | 0 | 44063
P00161 | 55 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.66 | -16.35 | 21.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 807.7 | 24.2 | 2.45 | - | 58258 | 0 | 58258
P00162 | 55 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.8 | -15.11 | 16.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 529.2 | 10.4 | 2.68 | - | 39022 | 0 | 39022
P00163 | 55 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.42 | -11.53 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 216.4 | 1.8 | 3.43 | - | 16298 | 0 | 16298
P00164 | 55 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.49 | -14.17 | 17.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 594.4 | 12.9 | 2.63 | - | 43635 | 0 | 43635
P00165 | 62.5 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.49 | -16.18 | 21.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 862.4 | 28 | 2.27 | - | 57101 | 0 | 57101
P00166 | 62.5 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.73 | -15 | 16.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 568 | 12.1 | 2.47 | - | 38526 | 0 | 38526
P00167 | 62.5 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.44 | -11.54 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 236.2 | 2.1 | 3.13 | - | 16398 | 0 | 16398
P00168 | 62.5 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.38 | -14.06 | 17.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 635.5 | 14.9 | 2.44 | - | 42897 | 0 | 42897
P00169 | 70 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.24 | -15.93 | 20.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 922.2 | 32.5 | 2.12 | - | 55452 | 0 | 55452
P00170 | 70 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.6 | -14.81 | 16.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 609.6 | 14.3 | 2.25 | - | 37635 | 0 | 37635
P00171 | 70 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.4 | -11.51 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 254.7 | 2.4 | 2.82 | - | 16128 | 0 | 16128
P00172 | 70 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.21 | -13.89 | 17.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 680 | 17.6 | 2.22 | - | 41765 | 0 | 41765
P00173 | 56 | -20 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -14.63 | -16.32 | 21.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 813.7 | 24.6 | 2.42 | - | 58054 | 0 | 58054
P00174 | 56 | -15 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.79 | -15.1 | 16.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 534.1 | 10.6 | 2.65 | - | 38967 | 0 | 38967
P00175 | 56 | -10 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.43 | -11.53 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 218.8 | 1.8 | 3.39 | - | 16312 | 0 | 16312
P00176 | 56 | -16 | -6 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.45 | -14.13 | 17.7 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 597.6 | 13 | 2.61 | - | 43409 | 0 | 43409
P00177 | 25 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.45 | -16.14 | 21.2 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 740.7 | 17.9 | 3.2 | - | 69852 | 0 | 69852
P00178 | 25 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.58 | -14.79 | 16.3 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 480.7 | 7.6 | 3.61 | - | 46103 | 0 | 46103
P00179 | 25 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.29 | -11.42 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 194.2 | 1.3 | 4.83 | - | 18932 | 0 | 18932
P00180 | 25 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.18 | -13.86 | 17.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 534.6 | 9.3 | 3.48 | - | 51103 | 0 | 51103
P00181 | 32.5 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.33 | -16.01 | 21 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 773.7 | 20 | 2.99 | - | 68829 | 0 | 68829
P00182 | 32.5 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.56 | -14.76 | 16.3 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 507.2 | 8.6 | 3.31 | - | 45934 | 0 | 45934
P00183 | 32.5 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.26 | -11.39 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 202.5 | 1.5 | 4.29 | - | 18667 | 0 | 18667
P00184 | 32.5 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.14 | -13.82 | 17.2 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 561.7 | 10.5 | 3.2 | - | 50695 | 0 | 50695
P00185 | 40 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.21 | -15.89 | 20.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 812.2 | 22.5 | 2.79 | - | 67810 | 0 | 67810
P00186 | 40 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.45 | -14.61 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 529.3 | 9.7 | 3.01 | - | 45045 | 0 | 45045
P00187 | 40 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.27 | -11.4 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 216.7 | 1.7 | 3.91 | - | 18784 | 0 | 18784
P00188 | 40 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.08 | -13.77 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 593 | 12 | 2.97 | - | 50277 | 0 | 50277
P00189 | 47.5 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.03 | -15.71 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 852.1 | 25.6 | 2.57 | - | 66363 | 0 | 66363
P00190 | 47.5 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.38 | -14.51 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 559 | 11 | 2.8 | - | 44432 | 0 | 44432
P00191 | 47.5 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.24 | -11.37 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 228 | 1.9 | 3.54 | - | 18483 | 0 | 18483
P00192 | 47.5 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.02 | -13.7 | 17 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 628.7 | 13.7 | 2.76 | - | 49771 | 0 | 49771
P00193 | 55 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.87 | -15.55 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 901.7 | 29.2 | 2.4 | - | 65035 | 0 | 65035
P00194 | 55 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.32 | -14.44 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 596.2 | 12.7 | 2.6 | - | 43960 | 0 | 43960
P00195 | 55 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.26 | -11.39 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 247.8 | 2.1 | 3.23 | - | 18667 | 0 | 18667
P00196 | 55 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.93 | -15.32 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 667.3 | 15.7 | 2.57 | - | 48990 | 0 | 48990
P00197 | 62.5 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.66 | -15.34 | 19.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 956.4 | 33.4 | 2.25 | - | 63329 | 0 | 63329
P00198 | 62.5 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.25 | -14.25 | 15.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 639.9 | 14.9 | 2.4 | - | 43399 | 0 | 43399
P00199 | 62.5 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.21 | -11.35 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 263.1 | 2.4 | 2.93 | - | 18260 | 0 | 18260
P00200 | 62.5 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.83 | -15.16 | 16.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 714.1 | 18.3 | 2.38 | - | 48202 | 0 | 48202
P00201 | 70 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.45 | -15.13 | 19.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1024.6 | 38.8 | 2.09 | - | 61605 | 0 | 61605
P00202 | 70 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.1 | -14.1 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 682.6 | 17.4 | 2.18 | - | 42145 | 0 | 42145
P00203 | 70 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.23 | -11.37 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 291.1 | 2.9 | 2.66 | - | 18436 | 0 | 18436
P00204 | 70 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.65 | -14.9 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 760.7 | 21.3 | 2.17 | - | 46722 | 0 | 46722
P00205 | 56 | -20 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -13.85 | -15.53 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 909.1 | 29.8 | 2.38 | - | 64860 | 0 | 64860
P00206 | 56 | -15 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.31 | -14.43 | 15.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 601.5 | 13 | 2.57 | - | 43888 | 0 | 43888
P00207 | 56 | -10 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.26 | -11.39 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 250.6 | 2.2 | 3.19 | - | 18681 | 0 | 18681
P00208 | 56 | -16 | -6 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.92 | -15.3 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 673.1 | 16.1 | 2.54 | - | 48895 | 0 | 48895
P00209 | 25 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.79 | -15.47 | 20 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 814 | 21.1 | 3.15 | - | 76760 | 0 | 76760
P00210 | 25 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.13 | -14.13 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 526.8 | 9 | 3.44 | - | 50524 | 0 | 50524
P00211 | 25 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.14 | -11.29 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 216.4 | 1.5 | 4.6 | - | 21100 | 0 | 21100
P00212 | 25 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.74 | -15.02 | 16.6 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 590.9 | 11.1 | 3.39 | - | 56491 | 0 | 56491
P00213 | 32.5 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.7 | -15.38 | 19.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 852.5 | 23.6 | 2.93 | - | 75834 | 0 | 75834
P00214 | 32.5 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.09 | -14.09 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 553.4 | 10.2 | 3.17 | - | 50119 | 0 | 50119
P00215 | 32.5 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.11 | -11.26 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 224.9 | 1.7 | 4.1 | - | 20727 | 0 | 20727
P00216 | 32.5 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.69 | -14.95 | 16.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 621 | 12.6 | 3.12 | - | 56042 | 0 | 56042
P00217 | 40 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.55 | -15.23 | 19.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 890.9 | 26.4 | 2.76 | - | 74379 | 0 | 74379
P00218 | 40 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.05 | -14.05 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 584 | 11.6 | 2.93 | - | 49699 | 0 | 49699
P00219 | 40 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.12 | -11.28 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 241.2 | 1.9 | 3.73 | - | 20907 | 0 | 20907
P00220 | 40 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.63 | -14.86 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 653.8 | 14.2 | 2.9 | - | 55428 | 0 | 55428
P00221 | 47.5 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.33 | -15.01 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 927.5 | 29.6 | 2.54 | - | 72237 | 0 | 72237
P00222 | 47.5 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.97 | -13.97 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 615.6 | 13.1 | 2.73 | - | 48937 | 0 | 48937
P00223 | 47.5 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.14 | -11.29 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 260 | 2.2 | 3.42 | - | 21080 | 0 | 21080
P00224 | 47.5 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.56 | -14.76 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 691.9 | 16.2 | 2.7 | - | 54775 | 0 | 54775
P00225 | 55 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.19 | -14.87 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 982.2 | 33.8 | 2.38 | - | 70839 | 0 | 70839
P00226 | 55 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.9 | -13.9 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 655 | 15 | 2.54 | - | 48298 | 0 | 48298
P00227 | 55 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.1 | -11.26 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 274.8 | 2.5 | 3.09 | - | 20703 | 0 | 20703
P00228 | 55 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.39 | -14.54 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 723.6 | 18.3 | 2.48 | - | 53125 | 0 | 53125
P00229 | 62.5 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.04 | -14.71 | 18.6 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1046.6 | 38.9 | 2.23 | - | 69299 | 0 | 69299
P00230 | 62.5 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.84 | -13.84 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 702.5 | 17.5 | 2.35 | - | 47647 | 0 | 47647
P00231 | 62.5 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.07 | -11.24 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 294.3 | 2.8 | 2.79 | - | 20427 | 0 | 20427
P00232 | 62.5 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.29 | -14.41 | 15.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 772.3 | 21.2 | 2.31 | - | 52131 | 0 | 52131
P00233 | 70 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -12.79 | -14.47 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1112.3 | 44.6 | 2.08 | - | 66877 | 0 | 66877
P00234 | 70 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.69 | -13.69 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 747.5 | 20.4 | 2.14 | - | 46148 | 0 | 46148
P00235 | 70 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.09 | -11.25 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 324.4 | 3.4 | 2.54 | - | 20547 | 0 | 20547
P00236 | 70 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.19 | -14.19 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 831.9 | 24.9 | 2.14 | - | 51091 | 0 | 51091
P00237 | 56 | -20 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.17 | -14.85 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 990 | 34.4 | 2.36 | - | 70637 | 0 | 70637
P00238 | 56 | -15 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -10.91 | -13.91 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 662.4 | 15.4 | 2.51 | - | 48326 | 0 | 48326
P00239 | 56 | -10 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.1 | -11.26 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 277.9 | 2.5 | 3.05 | - | 20715 | 0 | 20715
P00240 | 56 | -16 | -6 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.38 | -14.52 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 729.8 | 18.7 | 2.46 | - | 53012 | 0 | 53012
P00241 | 25 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.15 | -14.82 | 18.8 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 866.7 | 23.8 | 3.07 | - | 81734 | 0 | 81734
P00242 | 25 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.85 | -13.85 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 578 | 10.5 | 3.42 | - | 55439 | 0 | 55439
P00243 | 25 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8.02 | -11.19 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 236.7 | 1.7 | 4.42 | - | 23081 | 0 | 23081
P00244 | 25 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.34 | -14.47 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 639.1 | 12.8 | 3.32 | - | 61096 | 0 | 61096
P00245 | 32.5 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.06 | -14.73 | 18.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 907 | 26.7 | 2.87 | - | 80688 | 0 | 80688
P00246 | 32.5 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.81 | -13.81 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 607.1 | 11.8 | 3.15 | - | 54981 | 0 | 54981
P00247 | 32.5 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8.05 | -11.21 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 253.7 | 2 | 3.98 | - | 23380 | 0 | 23380
P00248 | 32.5 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 663.7 | 14.3 | 3.02 | - | 59899 | 0 | 59899
P00249 | 40 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.91 | -14.59 | 18.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 946.8 | 29.6 | 2.69 | - | 79049 | 0 | 79049
P00250 | 40 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.71 | -13.71 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 632.2 | 13.3 | 2.88 | - | 53801 | 0 | 53801
P00251 | 40 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8 | -11.18 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 263.9 | 2.2 | 3.6 | - | 22877 | 0 | 22877
P00252 | 40 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.17 | -14.17 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 697.5 | 16.1 | 2.81 | - | 59136 | 0 | 59136
P00253 | 47.5 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.76 | -14.44 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 992.9 | 33.3 | 2.53 | - | 77327 | 0 | 77327
P00254 | 47.5 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.65 | -13.65 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 668.2 | 15.1 | 2.68 | - | 53113 | 0 | 53113
P00255 | 47.5 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8.01 | -11.19 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 284 | 2.5 | 3.29 | - | 23024 | 0 | 23024
P00256 | 47.5 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.1 | -14.1 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 737.1 | 18.3 | 2.62 | - | 58358 | 0 | 58358
P00257 | 55 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.64 | -14.31 | 18 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1052.3 | 37.9 | 2.37 | - | 75898 | 0 | 75898
P00258 | 55 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.58 | -13.58 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 710.2 | 17.3 | 2.49 | - | 52369 | 0 | 52369
P00259 | 55 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.98 | -11.16 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 300.5 | 2.8 | 2.98 | - | 22639 | 0 | 22639
P00260 | 55 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11 | -14 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 777.9 | 20.8 | 2.46 | - | 57113 | 0 | 57113
P00261 | 62.5 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.48 | -14.15 | 17.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1118.2 | 43.5 | 2.21 | - | 74041 | 0 | 74041
P00262 | 62.5 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.51 | -13.51 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 759.7 | 20.1 | 2.31 | - | 51523 | 0 | 51523
P00263 | 62.5 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.99 | -11.17 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 327.7 | 3.3 | 2.73 | - | 22748 | 0 | 22748
P00264 | 62.5 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.91 | -13.91 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 831.1 | 24 | 2.28 | - | 56098 | 0 | 56098
P00265 | 70 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.24 | -13.92 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1186.4 | 49.7 | 2.07 | - | 71335 | 0 | 71335
P00266 | 70 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.38 | -13.38 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 811.8 | 23.3 | 2.15 | - | 50119 | 0 | 50119
P00267 | 70 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.95 | -11.13 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 351.8 | 3.9 | 2.47 | - | 22277 | 0 | 22277
P00268 | 70 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.73 | -13.73 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 880.7 | 27.7 | 2.09 | - | 54087 | 0 | 54087
P00269 | 56 | -20 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -12.64 | -14.31 | 18 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1063.8 | 38.8 | 2.36 | - | 75898 | 0 | 75898
P00270 | 56 | -15 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.57 | -13.57 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 716.3 | 17.7 | 2.47 | - | 52258 | 0 | 52258
P00271 | 56 | -10 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -7.98 | -11.16 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 303.9 | 2.9 | 2.95 | - | 22656 | 0 | 22656
P00272 | 56 | -16 | -6 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.98 | -13.98 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 784.4 | 21.1 | 2.43 | - | 56978 | 0 | 56978
P00273 | 25 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.74 | -14.41 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 926.4 | 26.3 | 3.1 | - | 87368 | 0 | 87368
P00274 | 25 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.58 | -13.58 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 618.9 | 11.8 | 3.36 | - | 59362 | 0 | 59362
P00275 | 25 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.92 | -11.11 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 255.7 | 1.9 | 4.27 | - | 24935 | 0 | 24935
P00276 | 25 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.01 | -14.01 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 680.1 | 14.2 | 3.28 | - | 65014 | 0 | 65014
P00277 | 32.5 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.58 | -14.26 | 17.9 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 959.2 | 29.3 | 2.86 | - | 85328 | 0 | 85328
P00278 | 32.5 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.53 | -13.53 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 649.3 | 13.3 | 3.1 | - | 58812 | 0 | 58812
P00279 | 32.5 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.94 | -11.12 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 272.2 | 2.2 | 3.87 | - | 25089 | 0 | 25089
P00280 | 32.5 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.96 | -13.96 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 713.2 | 16 | 3.04 | - | 64364 | 0 | 64364
P00281 | 40 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.49 | -14.17 | 17.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1008.9 | 33.1 | 2.67 | - | 84234 | 0 | 84234
P00282 | 40 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.41 | -13.41 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 671.4 | 14.7 | 2.85 | - | 57140 | 0 | 57140
P00283 | 40 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.9 | -11.09 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 284.6 | 2.4 | 3.48 | - | 24672 | 0 | 24672
P00284 | 40 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.91 | -13.91 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 751.2 | 18.1 | 2.82 | - | 63684 | 0 | 63684
P00285 | 47.5 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.37 | -14.05 | 17.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1060.7 | 37.2 | 2.51 | - | 82605 | 0 | 82605
P00286 | 47.5 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.35 | -13.35 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 709.9 | 16.8 | 2.65 | - | 56431 | 0 | 56431
P00287 | 47.5 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.92 | -11.11 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 306.4 | 2.8 | 3.19 | - | 24844 | 0 | 24844
P00288 | 47.5 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.84 | -13.84 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 792.3 | 20.5 | 2.64 | - | 62730 | 0 | 62730
P00289 | 55 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.19 | -13.87 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1113.2 | 41.7 | 2.36 | - | 80294 | 0 | 80294
P00290 | 55 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.28 | -13.28 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 752.6 | 19.2 | 2.46 | - | 55497 | 0 | 55497
P00291 | 55 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.89 | -11.08 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 325 | 3.1 | 2.89 | - | 24484 | 0 | 24484
P00292 | 55 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.7 | -13.7 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 829.5 | 23.2 | 2.42 | - | 60899 | 0 | 60899
P00293 | 62.5 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.94 | -15.33 | 16.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1163.8 | 46.9 | 2.18 | - | 77058 | 0 | 77058
P00294 | 62.5 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.2 | -13.2 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 803.5 | 22.2 | 2.29 | - | 54496 | 0 | 54496
P00295 | 62.5 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.89 | -11.08 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 353.2 | 3.8 | 2.65 | - | 24519 | 0 | 24519
P00296 | 62.5 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.59 | -13.59 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 881.6 | 26.6 | 2.26 | - | 59511 | 0 | 59511
P00297 | 70 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.71 | -14.97 | 16.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1230.8 | 53.2 | 2.04 | - | 74006 | 0 | 74006
P00298 | 70 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.11 | -13.11 | 14.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 862.4 | 25.9 | 2.13 | - | 53242 | 0 | 53242
P00299 | 70 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.83 | -11.03 | 11.7 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 374.3 | 4.7 | 2.42 | - | 23703 | 0 | 23703
P00300 | 70 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.45 | -13.45 | 14.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 939.9 | 30.7 | 2.1 | - | 57726 | 0 | 57726
P00301 | 56 | -20 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.17 | -13.85 | 17.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1121.3 | 42.4 | 2.34 | - | 80006 | 0 | 80006
P00302 | 56 | -15 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.27 | -13.27 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 758.6 | 19.5 | 2.44 | - | 55347 | 0 | 55347
P00303 | 56 | -10 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.89 | -11.08 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 328.6 | 3.2 | 2.86 | - | 24494 | 0 | 24494
P00304 | 56 | -16 | -6 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.68 | -13.68 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 835 | 23.6 | 2.4 | - | 60652 | 0 | 60652
P00305 | 25 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.99 | -15.67 | 20.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 773.2 | 19.5 | 3.13 | - | 72918 | 0 | 72918
P00306 | 25 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.35 | -14.47 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 508.7 | 8.3 | 3.56 | - | 48788 | 0 | 48788
P00307 | 25 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.2 | -11.34 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 205.9 | 1.4 | 4.7 | - | 20074 | 0 | 20074
P00308 | 25 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.91 | -15.29 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 564.5 | 10.2 | 3.44 | - | 53961 | 0 | 53961
P00309 | 32.5 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.89 | -15.57 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 809.4 | 21.9 | 2.91 | - | 72008 | 0 | 72008
P00310 | 32.5 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.32 | -14.44 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 536.2 | 9.5 | 3.26 | - | 48562 | 0 | 48562
P00311 | 32.5 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.17 | -11.32 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 214.8 | 1.6 | 4.19 | - | 19792 | 0 | 19792
P00312 | 32.5 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.87 | -15.22 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 593.9 | 11.6 | 3.16 | - | 53600 | 0 | 53600
P00313 | 40 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.79 | -15.46 | 19.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 851.2 | 24.7 | 2.72 | - | 71070 | 0 | 71070
P00314 | 40 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.28 | -14.38 | 15.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 565.9 | 10.8 | 3.02 | - | 48161 | 0 | 48161
P00315 | 40 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.18 | -11.33 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 229.9 | 1.8 | 3.82 | - | 19934 | 0 | 19934
P00316 | 40 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.81 | -15.13 | 16.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 625.4 | 13.1 | 2.93 | - | 53021 | 0 | 53021
P00317 | 47.5 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.63 | -15.31 | 19.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 894.3 | 27.8 | 2.56 | - | 69650 | 0 | 69650
P00318 | 47.5 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.16 | -14.16 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 592.7 | 12.2 | 2.76 | - | 47115 | 0 | 47115
P00319 | 47.5 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.15 | -11.3 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 242.3 | 2 | 3.45 | - | 19643 | 0 | 19643
P00320 | 47.5 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.69 | -14.95 | 16.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 656.4 | 15 | 2.68 | - | 51968 | 0 | 51968
P00321 | 55 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.47 | -15.14 | 19.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 944.9 | 31.6 | 2.39 | - | 68150 | 0 | 68150
P00322 | 55 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.1 | -14.1 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 631.4 | 14.1 | 2.56 | - | 46556 | 0 | 46556
P00323 | 55 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.17 | -11.31 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 262.5 | 2.3 | 3.16 | - | 19772 | 0 | 19772
P00324 | 55 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.61 | -14.83 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 697.5 | 17.2 | 2.5 | - | 51205 | 0 | 51205
P00325 | 62.5 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.32 | -14.99 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1008.5 | 36.5 | 2.24 | - | 66778 | 0 | 66778
P00326 | 62.5 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.03 | -14.03 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 676.4 | 16.4 | 2.37 | - | 45876 | 0 | 45876
P00327 | 62.5 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.19 | -11.33 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 288.1 | 2.7 | 2.87 | - | 19996 | 0 | 19996
P00328 | 62.5 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.52 | -14.71 | 16.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 746.6 | 20 | 2.32 | - | 50399 | 0 | 50399
P00329 | 70 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.1 | -14.77 | 18.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1077.3 | 42.3 | 2.08 | - | 64778 | 0 | 64778
P00330 | 70 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -10.94 | -13.94 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 730.1 | 19.4 | 2.19 | - | 45072 | 0 | 45072
P00331 | 70 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.14 | -11.29 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 308.9 | 3.1 | 2.6 | - | 19562 | 0 | 19562
P00332 | 70 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.38 | -14.52 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 799.4 | 23.2 | 2.15 | - | 49096 | 0 | 49096
P00333 | 56 | -20 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.43 | -15.11 | 19.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 951.2 | 32.2 | 2.37 | - | 67866 | 0 | 67866
P00334 | 56 | -15 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.09 | -14.09 | 15.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 637 | 14.4 | 2.53 | - | 46475 | 0 | 46475
P00335 | 56 | -10 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.17 | -11.31 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 265.4 | 2.4 | 3.12 | - | 19788 | 0 | 19788
P00336 | 56 | -16 | -6 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.6 | -14.82 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 703.5 | 17.5 | 2.47 | - | 51101 | 0 | 51101
P00337 | 25 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.62 | -14.04 | 32 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 946.3 | 26.1 | 3.25 | - | 89243 | 0 | 89243
P00338 | 25 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.8 | -12.36 | 24.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 737.6 | 14.8 | 3.55 | - | 70746 | 0 | 70746
P00339 | 25 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.64 | -9.74 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 513 | 6.9 | 4.12 | - | 50024 | 0 | 50024
P00340 | 25 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3 | -7.13 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 264.6 | 1.6 | 5.2 | - | 26211 | 0 | 26211
P00341 | 25 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 25.2 | 0.1 | 12.38 | - | 2530 | 0 | 2530
P00342 | 25 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.44 | -12.98 | 26.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 784.3 | 16.9 | 3.47 | - | 74971 | 0 | 74971
P00343 | 32.5 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.44 | -13.87 | 31.5 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 990.2 | 29.3 | 3.02 | - | 88086 | 0 | 88086
P00344 | 32.5 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.75 | -12.31 | 24.8 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 777.4 | 16.9 | 3.26 | - | 70406 | 0 | 70406
P00345 | 32.5 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.61 | -9.71 | 18.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 540.5 | 7.9 | 3.72 | - | 49812 | 0 | 49812
P00346 | 32.5 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3.02 | -7.14 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 280.9 | 1.8 | 4.61 | - | 26332 | 0 | 26332
P00347 | 32.5 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.56 | -4.76 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 30.2 | 0.1 | 11.55 | - | 2879 | 0 | 2879
P00348 | 32.5 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.34 | -12.87 | 26.1 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 823.2 | 19.2 | 3.2 | - | 74295 | 0 | 74295
P00349 | 40 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.32 | -13.75 | 31.2 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1045.5 | 33.5 | 2.83 | - | 87287 | 0 | 87287
P00350 | 40 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.64 | -12.21 | 24.5 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 818.8 | 19.3 | 3.02 | - | 69677 | 0 | 69677
P00351 | 40 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.57 | -9.68 | 18.7 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 571.6 | 9.1 | 3.41 | - | 49555 | 0 | 49555
P00352 | 40 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3.03 | -7.15 | 13.9 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 299.3 | 2 | 4.16 | - | 26420 | 0 | 26420
P00353 | 40 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 28.6 | 0.1 | 10.85 | - | 2549 | 0 | 2549
P00354 | 40 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.22 | -12.75 | 25.8 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 866.8 | 21.9 | 2.97 | - | 73485 | 0 | 73485
P00355 | 47.5 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.12 | -13.55 | 30.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1103.6 | 38.2 | 2.64 | - | 85953 | 0 | 85953
P00356 | 47.5 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.53 | -12.11 | 24.3 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 867.4 | 22.2 | 2.81 | - | 68950 | 0 | 68950
P00357 | 47.5 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.45 | -9.59 | 18.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 601.6 | 10.4 | 3.1 | - | 48777 | 0 | 48777
P00358 | 47.5 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3.03 | -7.15 | 13.9 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 319.6 | 2.3 | 3.79 | - | 26420 | 0 | 26420
P00359 | 47.5 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.6 | -4.74 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 30.9 | 0.1 | 10.18 | - | 2604 | 0 | 2604
P00360 | 47.5 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.09 | -12.63 | 25.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 917.4 | 25.1 | 2.77 | - | 72628 | 0 | 72628
P00361 | 55 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -11.9 | -14.61 | 30 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1171.8 | 43.9 | 2.47 | - | 84519 | 0 | 84519
P00362 | 55 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.35 | -11.95 | 23.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 919.6 | 25.5 | 2.62 | - | 67811 | 0 | 67811
P00363 | 55 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.4 | -9.56 | 18.5 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 643.7 | 12.2 | 2.86 | - | 48489 | 0 | 48489
P00364 | 55 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 340.5 | 2.8 | 3.42 | - | 26183 | 0 | 26183
P00365 | 55 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.6 | -4.74 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 33.1 | 0.2 | 9.48 | - | 2596 | 0 | 2596
P00366 | 55 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.88 | -12.44 | 25.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 971.1 | 28.7 | 2.59 | - | 71291 | 0 | 71291
P00367 | 62.5 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -11.62 | -14.26 | 29.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1248.8 | 50.7 | 2.31 | - | 82688 | 0 | 82688
P00368 | 62.5 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.16 | -11.78 | 23.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 981.2 | 29.6 | 2.44 | - | 66545 | 0 | 66545
P00369 | 62.5 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.32 | -9.5 | 18.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 690.8 | 14.3 | 2.63 | - | 47950 | 0 | 47950
P00370 | 62.5 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.99 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 368.5 | 3.7 | 3.12 | - | 26156 | 0 | 26156
P00371 | 62.5 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.6 | -4.74 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 35.8 | 0.2 | 8.78 | - | 2592 | 0 | 2592
P00372 | 62.5 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.7 | -12.27 | 24.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1038.6 | 33.5 | 2.41 | - | 70107 | 0 | 70107
P00373 | 70 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -11.22 | -13.79 | 28.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1331.2 | 58.4 | 2.17 | - | 80043 | 0 | 80043
P00374 | 70 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -8.92 | -11.57 | 23 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1052.5 | 35 | 2.24 | - | 64981 | 0 | 64981
P00375 | 70 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.23 | -9.43 | 18.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 747.6 | 17 | 2.43 | - | 47344 | 0 | 47344
P00376 | 70 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.97 | -7.11 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 400.9 | 4.9 | 2.85 | - | 26020 | 0 | 26020
P00377 | 70 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.6 | -4.74 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 39.1 | 0.2 | 8.07 | - | 2595 | 0 | 2595
P00378 | 70 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.42 | -12.01 | 24 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1111 | 39.4 | 2.2 | - | 68233 | 0 | 68233
P00379 | 56 | -20 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -11.86 | -14.57 | 29.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1181.4 | 44.7 | 2.45 | - | 84289 | 0 | 84289
P00380 | 56 | -15 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.33 | -11.93 | 23.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 927.5 | 26 | 2.6 | - | 67670 | 0 | 67670
P00381 | 56 | -10 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.39 | -9.55 | 18.5 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 649.5 | 12.4 | 2.83 | - | 48420 | 0 | 48420
P00382 | 56 | -5 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 344 | 2.9 | 3.38 | - | 26182 | 0 | 26182
P00383 | 56 | 0 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.6 | -4.74 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 33.7 | 0.2 | 9.37 | - | 2614 | 0 | 2614
P00384 | 56 | -16 | 1 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.86 | -12.41 | 25 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 979.2 | 29.3 | 2.56 | - | 71128 | 0 | 71128
P00385 | 25 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.52 | -14.14 | 29 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1068.3 | 32.1 | 3.2 | - | 100750 | 0 | 100750
P00386 | 25 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.98 | -11.62 | 23.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 837.1 | 18.5 | 3.46 | - | 80288 | 0 | 80288
P00387 | 25 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.09 | -9.33 | 18 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 585.1 | 8.8 | 3.94 | - | 57048 | 0 | 57048
P00388 | 25 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.74 | -6.95 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 303.6 | 1.9 | 4.89 | - | 30076 | 0 | 30076
P00389 | 25 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 26.6 | 0.1 | 11.94 | - | 2676 | 0 | 2676
P00390 | 25 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.51 | -12.09 | 24.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 884.9 | 21 | 3.39 | - | 84589 | 0 | 84589
P00391 | 32.5 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.35 | -13.94 | 28.6 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1117.2 | 36.1 | 2.98 | - | 99388 | 0 | 99388
P00392 | 32.5 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.88 | -11.54 | 22.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 878.2 | 21 | 3.19 | - | 79535 | 0 | 79535
P00393 | 32.5 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.05 | -9.3 | 17.9 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 615.7 | 10 | 3.58 | - | 56741 | 0 | 56741
P00394 | 32.5 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.75 | -6.96 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 321.9 | 2.2 | 4.35 | - | 30172 | 0 | 30172
P00395 | 32.5 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 29.9 | 0.1 | 11.06 | - | 2807 | 0 | 2807
P00396 | 32.5 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.39 | -11.99 | 24 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 927 | 23.7 | 3.13 | - | 83661 | 0 | 83661
P00397 | 40 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.16 | -13.73 | 28.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1172.6 | 40.8 | 2.79 | - | 97898 | 0 | 97898
P00398 | 40 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.77 | -11.44 | 22.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 923.6 | 23.9 | 2.96 | - | 78595 | 0 | 78595
P00399 | 40 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.93 | -9.21 | 17.7 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 643.3 | 11.4 | 3.24 | - | 55765 | 0 | 55765
P00400 | 40 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.75 | -6.96 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 342.2 | 2.7 | 3.94 | - | 30202 | 0 | 30202
P00401 | 40 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 31.3 | 0.1 | 10.41 | - | 2806 | 0 | 2806
P00402 | 40 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.27 | -11.88 | 23.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 975.2 | 26.9 | 2.92 | - | 82676 | 0 | 82676
P00403 | 47.5 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.98 | -13.53 | 27.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1238.3 | 46.4 | 2.62 | - | 96438 | 0 | 96438
P00404 | 47.5 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.64 | -11.34 | 22.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 976.1 | 27.3 | 2.76 | - | 77590 | 0 | 77590
P00405 | 47.5 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.88 | -9.17 | 17.7 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 682.4 | 13.1 | 2.99 | - | 55330 | 0 | 55330
P00406 | 47.5 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.72 | -6.93 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 361.7 | 3.3 | 3.55 | - | 29893 | 0 | 29893
P00407 | 47.5 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 32.7 | 0.2 | 9.78 | - | 2754 | 0 | 2754
P00408 | 47.5 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.14 | -11.76 | 23.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1030.6 | 30.7 | 2.73 | - | 81590 | 0 | 81590
P00409 | 55 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.73 | -13.27 | 27 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1309.1 | 52.9 | 2.45 | - | 94421 | 0 | 94421
P00410 | 55 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.49 | -11.21 | 22.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1035.4 | 31.3 | 2.58 | - | 76345 | 0 | 76345
P00411 | 55 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.82 | -9.13 | 17.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 728.9 | 15.2 | 2.77 | - | 54911 | 0 | 54911
P00412 | 55 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.71 | -6.93 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 388.3 | 4.2 | 3.25 | - | 29859 | 0 | 29859
P00413 | 55 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.63 | -4.72 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 37.1 | 0.2 | 8.96 | - | 2939 | 0 | 2939
P00414 | 55 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.97 | -11.62 | 23.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1093.3 | 35.3 | 2.55 | - | 80268 | 0 | 80268
P00415 | 62.5 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.39 | -12.92 | 26.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1384.7 | 60.2 | 2.3 | - | 91682 | 0 | 91682
P00416 | 62.5 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.3 | -11.05 | 21.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1103.3 | 36.3 | 2.4 | - | 74828 | 0 | 74828
P00417 | 62.5 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.74 | -9.07 | 17.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 781 | 17.8 | 2.56 | - | 54212 | 0 | 54212
P00418 | 62.5 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.7 | -6.92 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 419.3 | 5.4 | 2.98 | - | 29764 | 0 | 29764
P00419 | 62.5 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.64 | -4.72 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 40 | 0.2 | 8.27 | - | 2934 | 0 | 2934
P00420 | 62.5 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.71 | -11.39 | 22.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1157.1 | 40.7 | 2.35 | - | 78108 | 0 | 78108
P00421 | 70 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.96 | -12.51 | 25.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1466.8 | 69.1 | 2.13 | - | 88197 | 0 | 88197
P00422 | 70 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.02 | -10.82 | 21.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1176.1 | 42.3 | 2.2 | - | 72611 | 0 | 72611
P00423 | 70 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.64 | -8.99 | 17.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 843.2 | 21.1 | 2.36 | - | 53400 | 0 | 53400
P00424 | 70 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.68 | -6.91 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 456.7 | 6.5 | 2.73 | - | 29639 | 0 | 29639
P00425 | 70 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.61 | -4.73 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 47.1 | 0.2 | 7.36 | - | 3126 | 0 | 3126
P00426 | 70 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.47 | -11.19 | 22.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1240.3 | 47.6 | 2.18 | - | 76178 | 0 | 76178
P00427 | 56 | -20 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -10.7 | -13.23 | 26.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1319.4 | 53.9 | 2.43 | - | 94136 | 0 | 94136
P00428 | 56 | -15 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.47 | -11.19 | 22.1 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1044.1 | 31.9 | 2.56 | - | 76177 | 0 | 76177
P00429 | 56 | -10 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.82 | -9.12 | 17.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 735.6 | 15.5 | 2.74 | - | 54842 | 0 | 54842
P00430 | 56 | -5 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.71 | -6.93 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 392.1 | 4.3 | 3.21 | - | 29850 | 0 | 29850
P00431 | 56 | 0 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.63 | -4.72 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 37.6 | 0.2 | 8.85 | - | 2958 | 0 | 2958
P00432 | 56 | -16 | 1 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.94 | -11.59 | 23 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1100.8 | 35.9 | 2.52 | - | 79957 | 0 | 79957
P00433 | 25 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.59 | -13.12 | 26.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1178.8 | 38.2 | 3.16 | - | 111165 | 0 | 111165
P00434 | 25 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.2 | -10.97 | 21.6 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 919.6 | 21.9 | 3.4 | - | 88202 | 0 | 88202
P00435 | 25 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.53 | -8.92 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 642.3 | 10.5 | 3.78 | - | 62627 | 0 | 62627
P00436 | 25 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 340.3 | 2.4 | 4.69 | - | 33712 | 0 | 33712
P00437 | 25 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 29 | 0.1 | 11.55 | - | 2951 | 0 | 2951
P00438 | 25 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.68 | -11.37 | 22.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 971.4 | 24.6 | 3.35 | - | 92864 | 0 | 92864
P00439 | 32.5 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.37 | -12.9 | 26.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1225.6 | 42.4 | 2.95 | - | 109027 | 0 | 109027
P00440 | 32.5 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.11 | -10.9 | 21.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 964.9 | 24.7 | 3.15 | - | 87392 | 0 | 87392
P00441 | 32.5 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.49 | -8.89 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 675.4 | 11.9 | 3.44 | - | 62246 | 0 | 62246
P00442 | 32.5 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 359.5 | 3 | 4.18 | - | 33702 | 0 | 33702
P00443 | 32.5 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.7 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 30.4 | 0.1 | 10.83 | - | 2891 | 0 | 2891
P00444 | 32.5 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.64 | -11.33 | 22.4 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1024.2 | 28.1 | 3.1 | - | 92434 | 0 | 92434
P00445 | 40 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.19 | -12.72 | 25.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1285.3 | 47.7 | 2.77 | - | 107306 | 0 | 107306
P00446 | 40 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.02 | -10.82 | 21.3 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1016.5 | 28.2 | 2.92 | - | 86500 | 0 | 86500
P00447 | 40 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.44 | -8.85 | 17 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 712.8 | 13.6 | 3.16 | - | 61791 | 0 | 61791
P00448 | 40 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 381.9 | 3.7 | 3.78 | - | 33706 | 0 | 33706
P00449 | 40 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.68 | -4.69 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 34.5 | 0.2 | 9.94 | - | 3101 | 0 | 3101
P00450 | 40 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.51 | -11.23 | 22.2 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1076.4 | 31.9 | 2.88 | - | 91256 | 0 | 91256
P00451 | 47.5 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10 | -12.55 | 25.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1355.3 | 53.9 | 2.61 | - | 105552 | 0 | 105552
P00452 | 47.5 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.92 | -10.74 | 21.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1075.8 | 32.2 | 2.73 | - | 85517 | 0 | 85517
P00453 | 47.5 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.38 | -8.8 | 16.9 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 754.4 | 15.6 | 2.92 | - | 61172 | 0 | 61172
P00454 | 47.5 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.51 | -6.79 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 407.2 | 4.6 | 3.46 | - | 33657 | 0 | 33657
P00455 | 47.5 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 38.2 | 0.2 | 9.09 | - | 3200 | 0 | 3200
P00456 | 47.5 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.39 | -11.12 | 22 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1137.1 | 36.4 | 2.69 | - | 90028 | 0 | 90028
P00457 | 55 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -9.73 | -12.29 | 24.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1427.1 | 61.1 | 2.44 | - | 102928 | 0 | 102928
P00458 | 55 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.74 | -10.6 | 20.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1137.2 | 36.8 | 2.55 | - | 83850 | 0 | 83850
P00459 | 55 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.31 | -8.76 | 16.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 803.5 | 18 | 2.72 | - | 60527 | 0 | 60527
P00460 | 55 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.5 | -6.79 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 436.9 | 5.6 | 3.18 | - | 33594 | 0 | 33594
P00461 | 55 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 42.5 | 0.2 | 8.34 | - | 3280 | 0 | 3280
P00462 | 55 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.18 | -10.95 | 21.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1198.9 | 41.3 | 2.52 | - | 88020 | 0 | 88020
P00463 | 62.5 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -9.39 | -11.99 | 24 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1505.5 | 69.1 | 2.3 | - | 99681 | 0 | 99681
P00464 | 62.5 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.56 | -10.45 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1210.2 | 42.5 | 2.38 | - | 82077 | 0 | 82077
P00465 | 62.5 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.16 | -8.65 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 851.6 | 20.9 | 2.48 | - | 59111 | 0 | 59111
P00466 | 62.5 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.45 | -6.75 | 13.2 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 465.8 | 6.6 | 2.88 | - | 33064 | 0 | 33064
P00467 | 62.5 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 44.5 | 0.2 | 7.8 | - | 3224 | 0 | 3224
P00468 | 62.5 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.91 | -10.73 | 21.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1265.8 | 47.4 | 2.33 | - | 85441 | 0 | 85441
P00469 | 70 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.96 | -11.61 | 23.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1588.6 | 78.7 | 2.13 | - | 95515 | 0 | 95515
P00470 | 70 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.26 | -10.26 | 19.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1283.4 | 49.1 | 2.19 | - | 79235 | 0 | 79235
P00471 | 70 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.02 | -8.55 | 16.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 912.3 | 24.3 | 2.31 | - | 57773 | 0 | 57773
P00472 | 70 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.39 | -6.71 | 13.1 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 500.5 | 7.7 | 2.6 | - | 32485 | 0 | 32485
P00473 | 70 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 49.4 | 0.3 | 7.07 | - | 3253 | 0 | 3253
P00474 | 70 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.65 | -10.53 | 20.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1351.5 | 55 | 2.17 | - | 83005 | 0 | 83005
P00475 | 56 | -20 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -9.69 | -12.26 | 24.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1437.8 | 62.2 | 2.42 | - | 102585 | 0 | 102585
P00476 | 56 | -15 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -7.72 | -10.58 | 20.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1146.3 | 37.5 | 2.53 | - | 83635 | 0 | 83635
P00477 | 56 | -10 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.31 | -8.76 | 16.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 811.9 | 18.4 | 2.69 | - | 60527 | 0 | 60527
P00478 | 56 | -5 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.45 | -6.75 | 13.2 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 434.8 | 5.7 | 3.1 | - | 33094 | 0 | 33094
P00479 | 56 | 0 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.66 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 43.1 | 0.2 | 8.24 | - | 3297 | 0 | 3297
P00480 | 56 | -16 | 1 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.15 | -10.93 | 21.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1208.3 | 42.1 | 2.5 | - | 87768 | 0 | 87768
P00481 | 25 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.75 | -12.31 | 24.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1268.9 | 43.3 | 3.15 | - | 119666 | 0 | 119666
P00482 | 25 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.53 | -10.43 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 990.6 | 24.9 | 3.37 | - | 95014 | 0 | 95014
P00483 | 25 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.14 | -8.63 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 701 | 12.3 | 3.68 | - | 68350 | 0 | 68350
P00484 | 25 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.31 | -6.66 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 372 | 3.2 | 4.52 | - | 36856 | 0 | 36856
P00485 | 25 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 32 | 0.1 | 11.11 | - | 3219 | 0 | 3219
P00486 | 25 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.06 | -10.86 | 21.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1055.8 | 28.5 | 3.31 | - | 100932 | 0 | 100932
P00487 | 32.5 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.6 | -12.17 | 24.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1326.7 | 48.5 | 2.93 | - | 118028 | 0 | 118028
P00488 | 32.5 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.51 | -10.41 | 20.3 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1046 | 28.4 | 3.11 | - | 94735 | 0 | 94735
P00489 | 32.5 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.06 | -8.58 | 16.5 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 732.5 | 13.8 | 3.37 | - | 67510 | 0 | 67510
P00490 | 32.5 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.31 | -6.66 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 393.3 | 3.9 | 4.04 | - | 36868 | 0 | 36868
P00491 | 32.5 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 32.9 | 0.2 | 10.47 | - | 3130 | 0 | 3130
P00492 | 32.5 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.95 | -10.76 | 21.1 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1104 | 32.1 | 3.06 | - | 99633 | 0 | 99633
P00493 | 40 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.37 | -11.96 | 23.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1382.7 | 53.8 | 2.76 | - | 115438 | 0 | 115438
P00494 | 40 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.34 | -10.28 | 20 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1091.2 | 32.2 | 2.86 | - | 92864 | 0 | 92864
P00495 | 40 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.01 | -8.54 | 16.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 772.2 | 15.7 | 3.11 | - | 66944 | 0 | 66944
P00496 | 40 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.3 | -6.65 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 416.7 | 4.8 | 3.68 | - | 36777 | 0 | 36777
P00497 | 40 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 37.1 | 0.2 | 9.62 | - | 3328 | 0 | 3328
P00498 | 40 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.85 | -10.69 | 21 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1162.9 | 36.4 | 2.86 | - | 98588 | 0 | 98588
P00499 | 47.5 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.13 | -11.76 | 23.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1448.7 | 60.4 | 2.6 | - | 112830 | 0 | 112830
P00500 | 47.5 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.21 | -10.21 | 19.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1149.8 | 36.6 | 2.67 | - | 91395 | 0 | 91395
P00501 | 47.5 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.96 | -8.5 | 16.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 818.3 | 18 | 2.88 | - | 66347 | 0 | 66347
P00502 | 47.5 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.25 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 438.3 | 5.6 | 3.32 | - | 36224 | 0 | 36224
P00503 | 47.5 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 39.8 | 0.2 | 8.88 | - | 3316 | 0 | 3316
P00504 | 47.5 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.7 | -10.56 | 20.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1223.5 | 41.3 | 2.67 | - | 96867 | 0 | 96867
P00505 | 55 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.88 | -11.54 | 22.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1526.1 | 68.3 | 2.44 | - | 110073 | 0 | 110073
P00506 | 55 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.07 | -10.07 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1218.4 | 41.9 | 2.49 | - | 89838 | 0 | 89838
P00507 | 55 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.88 | -8.45 | 16.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 869.3 | 20.7 | 2.68 | - | 65482 | 0 | 65482
P00508 | 55 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.25 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 470.7 | 6.5 | 3.05 | - | 36193 | 0 | 36193
P00509 | 55 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 42.4 | 0.2 | 8.23 | - | 3294 | 0 | 3294
P00510 | 55 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.54 | -10.43 | 20.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1294.9 | 47.2 | 2.5 | - | 95063 | 0 | 95063
P00511 | 62.5 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.6 | -11.3 | 22.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1613.9 | 77.4 | 2.29 | - | 106858 | 0 | 106858
P00512 | 62.5 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.85 | -9.85 | 19.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1288.8 | 47.7 | 2.34 | - | 87412 | 0 | 87412
P00513 | 62.5 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.73 | -8.34 | 16 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 918.9 | 23.9 | 2.45 | - | 63787 | 0 | 63787
P00514 | 62.5 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.24 | -6.61 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 507.6 | 7.6 | 2.81 | - | 36029 | 0 | 36029
P00515 | 62.5 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.71 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 45.7 | 0.2 | 7.59 | - | 3280 | 0 | 3280
P00516 | 62.5 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.29 | -10.29 | 19.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1367.6 | 53.6 | 2.35 | - | 92319 | 0 | 92319
P00517 | 70 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.14 | -10.92 | 21.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1692.6 | 87.3 | 2.12 | - | 101770 | 0 | 101770
P00518 | 70 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.61 | -9.72 | 18.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1373.2 | 55.1 | 2.18 | - | 84777 | 0 | 84777
P00519 | 70 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.61 | -8.25 | 15.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 986.5 | 27.9 | 2.27 | - | 62475 | 0 | 62475
P00520 | 70 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.21 | -6.59 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 551.1 | 9.1 | 2.57 | - | 35769 | 0 | 35769
P00521 | 70 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 52 | 0.3 | 6.86 | - | 3505 | 0 | 3505
P00522 | 70 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -6.97 | -9.97 | 19.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1444.4 | 61.5 | 2.16 | - | 88713 | 0 | 88713
P00523 | 56 | -20 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.85 | -11.51 | 22.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1537.2 | 69.4 | 2.42 | - | 109677 | 0 | 109677
P00524 | 56 | -15 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.05 | -10.05 | 19.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1228.1 | 42.7 | 2.47 | - | 89599 | 0 | 89599
P00525 | 56 | -10 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.86 | -8.43 | 16.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 875.2 | 21 | 2.65 | - | 65250 | 0 | 65250
P00526 | 56 | -5 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.25 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 475.4 | 6.6 | 3.02 | - | 36184 | 0 | 36184
P00527 | 56 | 0 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 43.2 | 0.2 | 8.12 | - | 3321 | 0 | 3321
P00528 | 56 | -16 | 1 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.51 | -10.41 | 20.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1305 | 48 | 2.48 | - | 94789 | 0 | 94789
P00529 | 25 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.04 | -11.68 | 23.2 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1344.9 | 47.8 | 3.13 | - | 126832 | 0 | 126832
P00530 | 25 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.12 | -10.12 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1069 | 28.5 | 3.33 | - | 102537 | 0 | 102537
P00531 | 25 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.77 | -8.36 | 16 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 746.7 | 13.8 | 3.63 | - | 72811 | 0 | 72811
P00532 | 25 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 400.7 | 4 | 4.4 | - | 39702 | 0 | 39702
P00533 | 25 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.75 | -4.64 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 31.3 | 0.1 | 11.02 | - | 3146 | 0 | 3146
P00534 | 25 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.5 | -10.4 | 20.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1122.8 | 31.7 | 3.29 | - | 107331 | 0 | 107331
P00535 | 32.5 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.9 | -11.55 | 23 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1405.5 | 53.3 | 2.94 | - | 125033 | 0 | 125033
P00536 | 32.5 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.98 | -9.98 | 19.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1112.9 | 31.7 | 3.09 | - | 100792 | 0 | 100792
P00537 | 32.5 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.74 | -8.34 | 16 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 785.9 | 15.6 | 3.31 | - | 72435 | 0 | 72435
P00538 | 32.5 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 423.6 | 4.8 | 3.93 | - | 39702 | 0 | 39702
P00539 | 32.5 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.73 | -4.65 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 35.6 | 0.2 | 10.11 | - | 3393 | 0 | 3393
P00540 | 32.5 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.41 | -10.34 | 20.2 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1177.7 | 35.9 | 3.05 | - | 106289 | 0 | 106289
P00541 | 40 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.7 | -11.39 | 22.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1468.4 | 59.6 | 2.75 | - | 122594 | 0 | 122594
P00542 | 40 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.89 | -9.89 | 19.3 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1171 | 36 | 2.88 | - | 99653 | 0 | 99653
P00543 | 40 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.68 | -8.3 | 15.9 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 827 | 17.7 | 3.06 | - | 71695 | 0 | 71695
P00544 | 40 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.1 | -6.52 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 443.8 | 5.5 | 3.52 | - | 39175 | 0 | 39175
P00545 | 40 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 40.3 | 0.2 | 9.25 | - | 3585 | 0 | 3585
P00546 | 40 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.27 | -10.27 | 19.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1232.4 | 40.3 | 2.84 | - | 104480 | 0 | 104480
P00547 | 47.5 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.49 | -11.21 | 22.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1539.7 | 66.8 | 2.59 | - | 119916 | 0 | 119916
P00548 | 47.5 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.75 | -9.82 | 19 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1230.7 | 40.7 | 2.69 | - | 97832 | 0 | 97832
P00549 | 47.5 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.61 | -8.25 | 15.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 874.1 | 20.2 | 2.84 | - | 70874 | 0 | 70874
P00550 | 47.5 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.1 | -6.52 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 473.9 | 6.4 | 3.23 | - | 39169 | 0 | 39169
P00551 | 47.5 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 42 | 0.2 | 8.64 | - | 3532 | 0 | 3532
P00552 | 47.5 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.06 | -10.06 | 19.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1286.3 | 45.4 | 2.64 | - | 101840 | 0 | 101840
P00553 | 55 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.18 | -10.95 | 21.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1608.3 | 74.1 | 2.45 | - | 116000 | 0 | 116000
P00554 | 55 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.53 | -9.66 | 18.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1290.7 | 46.2 | 2.49 | - | 95168 | 0 | 95168
P00555 | 55 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.5 | -8.17 | 15.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 922 | 22.9 | 2.66 | - | 69453 | 0 | 69453
P00556 | 55 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.1 | -6.51 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 508.4 | 7.4 | 2.98 | - | 39094 | 0 | 39094
P00557 | 55 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 44.7 | 0.2 | 8 | - | 3506 | 0 | 3506
P00558 | 55 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.88 | -9.88 | 19.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1356.2 | 51.5 | 2.47 | - | 99568 | 0 | 99568
P00559 | 62.5 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.92 | -10.74 | 21.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1701.9 | 84.3 | 2.29 | - | 112687 | 0 | 112687
P00560 | 62.5 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.35 | -9.52 | 18.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1368.4 | 52.9 | 2.32 | - | 92810 | 0 | 92810
P00561 | 62.5 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.42 | -8.11 | 15.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 985.8 | 26.7 | 2.47 | - | 68432 | 0 | 68432
P00562 | 62.5 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.07 | -6.49 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 545.6 | 8.7 | 2.74 | - | 38729 | 0 | 38729
P00563 | 62.5 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 51.8 | 0.3 | 7.17 | - | 3759 | 0 | 3759
P00564 | 62.5 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.69 | -9.77 | 18.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1438.8 | 58.9 | 2.31 | - | 97121 | 0 | 97121
P00565 | 70 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.53 | -10.42 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1791.3 | 94.4 | 2.17 | - | 107703 | 0 | 107703
P00566 | 70 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.09 | -9.33 | 18 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1451.4 | 60.4 | 2.18 | - | 89604 | 0 | 89604
P00567 | 70 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.31 | -8.04 | 15.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1059.9 | 31.4 | 2.28 | - | 67121 | 0 | 67121
P00568 | 70 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.97 | -6.43 | 12.7 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 578.5 | 10 | 2.5 | - | 37545 | 0 | 37545
P00569 | 70 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 56.6 | 0.3 | 6.53 | - | 3757 | 0 | 3757
P00570 | 70 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.39 | -9.55 | 18.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1520.8 | 66.9 | 2.16 | - | 93406 | 0 | 93406
P00571 | 56 | -20 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.15 | -10.92 | 21.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1619.3 | 75.3 | 2.43 | - | 115534 | 0 | 115534
P00572 | 56 | -15 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.5 | -9.63 | 18.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1298.7 | 46.9 | 2.46 | - | 94748 | 0 | 94748
P00573 | 56 | -10 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.53 | -8.19 | 15.7 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 936.3 | 23.7 | 2.62 | - | 69805 | 0 | 69805
P00574 | 56 | -5 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.09 | -6.51 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 512.2 | 7.5 | 2.94 | - | 38991 | 0 | 38991
P00575 | 56 | 0 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 45.5 | 0.2 | 7.89 | - | 3536 | 0 | 3536
P00576 | 56 | -16 | 1 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.86 | -9.86 | 19.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1366.3 | 52.4 | 2.44 | - | 99249 | 0 | 99249
P00577 | 25 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.99 | -13.54 | 27.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1130.1 | 35.4 | 3.18 | - | 106570 | 0 | 106570
P00578 | 25 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.53 | -11.24 | 22.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 883.1 | 20.4 | 3.42 | - | 84698 | 0 | 84698
P00579 | 25 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.76 | -9.08 | 17.5 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 616.2 | 9.8 | 3.81 | - | 60084 | 0 | 60084
P00580 | 25 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.61 | -6.86 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 323.7 | 2.1 | 4.77 | - | 32069 | 0 | 32069
P00581 | 25 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.68 | -4.69 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 27.5 | 0.1 | 11.78 | - | 2808 | 0 | 2808
P00582 | 25 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.01 | -11.65 | 23.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 931.2 | 22.9 | 3.37 | - | 89016 | 0 | 89016
P00583 | 32.5 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.82 | -13.36 | 27.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1181.6 | 39.8 | 2.96 | - | 105112 | 0 | 105112
P00584 | 32.5 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.42 | -11.15 | 22 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 924.3 | 23 | 3.16 | - | 83718 | 0 | 83718
P00585 | 32.5 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.72 | -9.05 | 17.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 648.2 | 11.1 | 3.46 | - | 59744 | 0 | 59744
P00586 | 32.5 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.63 | -6.88 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 344.5 | 2.6 | 4.24 | - | 32291 | 0 | 32291
P00587 | 32.5 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 31.2 | 0.1 | 10.87 | - | 2973 | 0 | 2973
P00588 | 32.5 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.89 | -11.55 | 23 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 974.4 | 25.8 | 3.11 | - | 87936 | 0 | 87936
P00589 | 40 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.65 | -13.19 | 26.8 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1241.1 | 44.9 | 2.77 | - | 103623 | 0 | 103623
P00590 | 40 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.3 | -11.05 | 21.8 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 971.3 | 26 | 2.94 | - | 82654 | 0 | 82654
P00591 | 40 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.68 | -9.02 | 17.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 684.4 | 12.7 | 3.19 | - | 59332 | 0 | 59332
P00592 | 40 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.64 | -6.88 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 366.1 | 3.2 | 3.84 | - | 32312 | 0 | 32312
P00593 | 40 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 32.9 | 0.2 | 10.17 | - | 2954 | 0 | 2954
P00594 | 40 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.82 | -11.49 | 22.8 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1030.2 | 29.5 | 2.9 | - | 87341 | 0 | 87341
P00595 | 47.5 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.4 | -12.93 | 26.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1301 | 50.4 | 2.61 | - | 101325 | 0 | 101325
P00596 | 47.5 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.16 | -10.93 | 21.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1023.9 | 29.9 | 2.71 | - | 81388 | 0 | 81388
P00597 | 47.5 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.58 | -8.95 | 17.2 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 721.7 | 14.4 | 2.96 | - | 58517 | 0 | 58517
P00598 | 47.5 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.63 | -6.88 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 390.6 | 4.1 | 3.51 | - | 32286 | 0 | 32286
P00599 | 47.5 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.67 | -4.69 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 34.9 | 0.2 | 9.48 | - | 2940 | 0 | 2940
P00600 | 47.5 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.72 | -11.4 | 22.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1091.2 | 33.8 | 2.71 | - | 86388 | 0 | 86388
P00601 | 55 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.12 | -12.66 | 25.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1370.4 | 57.1 | 2.45 | - | 98840 | 0 | 98840
P00602 | 55 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8 | -10.81 | 21.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1085.1 | 34.3 | 2.53 | - | 80013 | 0 | 80013
P00603 | 55 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.53 | -8.91 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 770.3 | 16.7 | 2.74 | - | 58023 | 0 | 58023
P00604 | 55 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.56 | -6.83 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 411.1 | 5 | 3.2 | - | 31614 | 0 | 31614
P00605 | 55 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 39.7 | 0.2 | 8.65 | - | 3112 | 0 | 3112
P00606 | 55 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.47 | -11.19 | 22.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1146.5 | 38.7 | 2.5 | - | 84171 | 0 | 84171
P00607 | 62.5 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.84 | -12.4 | 25 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1455.6 | 65.5 | 2.29 | - | 96380 | 0 | 96380
P00608 | 62.5 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.84 | -10.67 | 20.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1158.2 | 39.8 | 2.36 | - | 78553 | 0 | 78553
P00609 | 62.5 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.44 | -8.85 | 17 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 824.6 | 19.5 | 2.54 | - | 57241 | 0 | 57241
P00610 | 62.5 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.55 | -6.82 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 443.8 | 6 | 2.93 | - | 31502 | 0 | 31502
P00611 | 62.5 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 42.9 | 0.2 | 7.97 | - | 3107 | 0 | 3107
P00612 | 62.5 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.23 | -11 | 21.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1215.9 | 44.3 | 2.34 | - | 82078 | 0 | 82078
P00613 | 70 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.44 | -12.03 | 24.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1544.3 | 74.6 | 2.16 | - | 92853 | 0 | 92853
P00614 | 70 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.57 | -10.46 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1234.3 | 46 | 2.19 | - | 76201 | 0 | 76201
P00615 | 70 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.27 | -8.73 | 16.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 880.4 | 22.9 | 2.31 | - | 55756 | 0 | 55756
P00616 | 70 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.54 | -6.81 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 484.8 | 7.2 | 2.68 | - | 31467 | 0 | 31467
P00617 | 70 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 47 | 0.2 | 7.28 | - | 3123 | 0 | 3123
P00618 | 70 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.98 | -10.79 | 21.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1300.1 | 51.5 | 2.17 | - | 79848 | 0 | 79848
P00619 | 56 | -20 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.08 | -12.63 | 25.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1381.2 | 58.1 | 2.43 | - | 98543 | 0 | 98543
P00620 | 56 | -15 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -7.98 | -10.79 | 21.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1094.1 | 34.9 | 2.51 | - | 79825 | 0 | 79825
P00621 | 56 | -10 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.52 | -8.91 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 777 | 17.1 | 2.71 | - | 57929 | 0 | 57929
P00622 | 56 | -5 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.56 | -6.82 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 415.1 | 5.1 | 3.16 | - | 31600 | 0 | 31600
P00623 | 56 | 0 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.65 | -4.71 | 10.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 40.3 | 0.2 | 8.54 | - | 3131 | 0 | 3131
P00624 | 56 | -16 | 1 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.44 | -11.17 | 22.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1155.9 | 39.4 | 2.48 | - | 83962 | 0 | 83962
P00625 | 25 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.36 | -12.27 | 42.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1243.7 | 40 | 3.29 | - | 117290 | 0 | 117290
P00626 | 25 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.48 | -9.89 | 33.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1031 | 25.5 | 3.52 | - | 98886 | 0 | 98886
P00627 | 25 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.47 | -7.7 | 25.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 816.9 | 14.9 | 3.88 | - | 79651 | 0 | 79651
P00628 | 25 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.23 | -5.51 | 19.5 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 594.5 | 7.5 | 4.53 | - | 58906 | 0 | 58906
P00629 | 25 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.34 | -3.23 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 359 | 2.4 | 5.67 | - | 36114 | 0 | 36114
P00630 | 25 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.21 | -0.87 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 111.9 | 0.4 | 8.54 | - | 11427 | 0 | 11427
P00631 | 25 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.11 | -10.38 | 35 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1076.5 | 28.3 | 3.46 | - | 102904 | 0 | 102904
P00632 | 32.5 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.09 | -12.02 | 41.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1298.8 | 44.8 | 3.08 | - | 115539 | 0 | 115539
P00633 | 32.5 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.39 | -9.82 | 32.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1085.3 | 29.2 | 3.24 | - | 98300 | 0 | 98300
P00634 | 32.5 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.39 | -7.64 | 25.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 858.7 | 17 | 3.53 | - | 79144 | 0 | 79144
P00635 | 32.5 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.19 | -5.49 | 19.4 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 626.2 | 8.6 | 4.02 | - | 58695 | 0 | 58695
P00636 | 32.5 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.34 | -3.23 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 379.3 | 3 | 4.91 | - | 36131 | 0 | 36131
P00637 | 32.5 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.23 | -0.85 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 116.7 | 0.4 | 7.51 | - | 11294 | 0 | 11294
P00638 | 32.5 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.95 | -10.25 | 34.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1128.6 | 32.1 | 3.18 | - | 101856 | 0 | 101856
P00639 | 40 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -9.81 | -11.81 | 40.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1362.8 | 50.7 | 2.87 | - | 113784 | 0 | 113784
P00640 | 40 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.23 | -9.7 | 32.4 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1143.3 | 33.4 | 3 | - | 97293 | 0 | 97293
P00641 | 40 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.3 | -7.58 | 25.2 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 905.9 | 19.5 | 3.24 | - | 78531 | 0 | 78531
P00642 | 40 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.16 | -5.46 | 19.3 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 662.2 | 9.9 | 3.64 | - | 58451 | 0 | 58451
P00643 | 40 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.34 | -3.23 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 402.4 | 3.8 | 4.38 | - | 36128 | 0 | 36128
P00644 | 40 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.21 | -0.87 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 125.4 | 0.5 | 6.74 | - | 11453 | 0 | 11453
P00645 | 40 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.79 | -10.13 | 34 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1189.5 | 36.7 | 2.96 | - | 100842 | 0 | 100842
P00646 | 47.5 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -9.45 | -11.45 | 39.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1431.4 | 57.7 | 2.68 | - | 111478 | 0 | 111478
P00647 | 47.5 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.06 | -9.57 | 31.9 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1209.8 | 38.3 | 2.8 | - | 96172 | 0 | 96172
P00648 | 47.5 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.16 | -7.49 | 24.9 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 958 | 22.4 | 3 | - | 77677 | 0 | 77677
P00649 | 47.5 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.11 | -5.43 | 19.3 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 703.4 | 11.5 | 3.34 | - | 58143 | 0 | 58143
P00650 | 47.5 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.34 | -3.23 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 429.5 | 4.4 | 3.96 | - | 36148 | 0 | 36148
P00651 | 47.5 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.19 | -0.88 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 135 | 0.6 | 6.09 | - | 11575 | 0 | 11575
P00652 | 47.5 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.54 | -9.93 | 33.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1253.4 | 41.7 | 2.77 | - | 99232 | 0 | 99232
P00653 | 55 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -9.1 | -11.17 | 38.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1514.5 | 66.1 | 2.5 | - | 109233 | 0 | 109233
P00654 | 55 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.79 | -9.37 | 31.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1280.8 | 43.9 | 2.62 | - | 94440 | 0 | 94440
P00655 | 55 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.1 | -7.44 | 24.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1025.7 | 26.3 | 2.79 | - | 77263 | 0 | 77263
P00656 | 55 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.02 | -5.37 | 19.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 748.5 | 13.3 | 3.08 | - | 57555 | 0 | 57555
P00657 | 55 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.31 | -3.25 | 14.9 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 463.1 | 5.2 | 3.59 | - | 36313 | 0 | 36313
P00658 | 55 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.2 | -0.87 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 143.7 | 0.6 | 5.47 | - | 11493 | 0 | 11493
P00659 | 55 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.27 | -9.73 | 32.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1328.5 | 48 | 2.59 | - | 97531 | 0 | 97531
P00660 | 62.5 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -8.63 | -10.79 | 36.6 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1604 | 75.2 | 2.36 | - | 106206 | 0 | 106206
P00661 | 62.5 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.49 | -9.14 | 30.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1364 | 51 | 2.43 | - | 92512 | 0 | 92512
P00662 | 62.5 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -3.94 | -7.33 | 24.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1098.5 | 30.9 | 2.58 | - | 76250 | 0 | 76250
P00663 | 62.5 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.94 | -5.32 | 19 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 803.8 | 15.7 | 2.84 | - | 57055 | 0 | 57055
P00664 | 62.5 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.32 | -3.24 | 14.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 500.4 | 6.2 | 3.28 | - | 36280 | 0 | 36280
P00665 | 62.5 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.17 | -0.89 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 156.8 | 0.7 | 4.96 | - | 11652 | 0 | 11652
P00666 | 62.5 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.96 | -9.5 | 31.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1415.6 | 55.6 | 2.42 | - | 95556 | 0 | 95556
P00667 | 70 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -8.14 | -10.4 | 35.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1714.6 | 87.1 | 2.21 | - | 103095 | 0 | 103095
P00668 | 70 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.17 | -8.91 | 29.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1466.2 | 59.9 | 2.26 | - | 90521 | 0 | 90521
P00669 | 70 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -3.76 | -7.21 | 24.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1185.5 | 36.7 | 2.39 | - | 75075 | 0 | 75075
P00670 | 70 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -0.77 | -5.21 | 18.7 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 862.3 | 18.7 | 2.58 | - | 55966 | 0 | 55966
P00671 | 70 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.42 | -3.18 | 14.7 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 536.4 | 7.3 | 2.97 | - | 35627 | 0 | 35627
P00672 | 70 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.15 | -0.9 | 11.4 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 174.1 | 0.9 | 4.45 | - | 11832 | 0 | 11832
P00673 | 70 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.62 | -9.24 | 30.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1520.5 | 65.3 | 2.25 | - | 93387 | 0 | 93387
P00674 | 56 | -20 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -9.05 | -11.13 | 38 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1526.6 | 67.3 | 2.48 | - | 108918 | 0 | 108918
P00675 | 56 | -15 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -6.73 | -9.33 | 31 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1289.9 | 44.8 | 2.59 | - | 94106 | 0 | 94106
P00676 | 56 | -10 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.09 | -7.43 | 24.7 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1035.3 | 26.9 | 2.76 | - | 77181 | 0 | 77181
P00677 | 56 | -5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.01 | -5.36 | 19.1 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 755.3 | 13.6 | 3.05 | - | 57495 | 0 | 57495
P00678 | 56 | 0 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.31 | -3.25 | 14.9 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 467.7 | 5.3 | 3.55 | - | 36311 | 0 | 36311
P00679 | 56 | 5 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.2 | -0.87 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 145.3 | 0.7 | 5.4 | - | 11509 | 0 | 11509
P00680 | 56 | -16 | 8 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.23 | -9.7 | 32.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1339.6 | 49 | 2.56 | - | 97303 | 0 | 97303
P00681 | 25 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.79 | -10.92 | 37.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1397.2 | 48.8 | 3.27 | - | 131765 | 0 | 131765
P00682 | 25 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.32 | -9.02 | 29.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1171.1 | 32 | 3.45 | - | 112328 | 0 | 112328
P00683 | 25 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.5 | -7.03 | 23.5 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 925.6 | 18.6 | 3.78 | - | 90248 | 0 | 90248
P00684 | 25 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.58 | -5.09 | 18.4 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 679.4 | 9.5 | 4.34 | - | 67308 | 0 | 67308
P00685 | 25 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.68 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 414.7 | 3.6 | 5.35 | - | 41715 | 0 | 41715
P00686 | 25 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.33 | -0.79 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 128.1 | 0.5 | 8.05 | - | 13081 | 0 | 13081
P00687 | 25 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.84 | -9.41 | 31.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1218.2 | 35.2 | 3.4 | - | 116457 | 0 | 116457
P00688 | 32.5 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.56 | -10.73 | 36.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1460.6 | 54.8 | 3.05 | - | 129933 | 0 | 129933
P00689 | 32.5 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.16 | -8.9 | 29.5 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1227 | 36.3 | 3.17 | - | 111129 | 0 | 111129
P00690 | 32.5 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.4 | -6.96 | 23.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 970.1 | 21.1 | 3.44 | - | 89404 | 0 | 89404
P00691 | 32.5 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.54 | -5.06 | 18.4 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 714.9 | 10.9 | 3.86 | - | 67006 | 0 | 67006
P00692 | 32.5 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.67 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 438.4 | 4.2 | 4.63 | - | 41762 | 0 | 41762
P00693 | 32.5 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.3 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 137.5 | 0.5 | 7.07 | - | 13311 | 0 | 13311
P00694 | 32.5 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.67 | -9.28 | 30.9 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1275.4 | 39.8 | 3.14 | - | 115103 | 0 | 115103
P00695 | 40 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.27 | -10.5 | 35.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1529.2 | 61.6 | 2.86 | - | 127672 | 0 | 127672
P00696 | 40 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.01 | -8.79 | 29.2 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1291.5 | 41.3 | 2.95 | - | 109908 | 0 | 109908
P00697 | 40 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.38 | -6.95 | 23.3 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1029.9 | 24.4 | 3.18 | - | 89281 | 0 | 89281
P00698 | 40 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.5 | -5.03 | 18.3 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 755 | 12.5 | 3.52 | - | 66641 | 0 | 66641
P00699 | 40 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.67 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 465.5 | 4.9 | 4.14 | - | 41791 | 0 | 41791
P00700 | 40 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.33 | -0.79 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 143.5 | 0.6 | 6.3 | - | 13102 | 0 | 13102
P00701 | 40 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.5 | -9.15 | 30.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1341.7 | 45.2 | 2.92 | - | 113747 | 0 | 113747
P00702 | 47.5 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -7.88 | -10.2 | 34.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1600.5 | 69.7 | 2.65 | - | 124645 | 0 | 124645
P00703 | 47.5 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.81 | -8.65 | 28.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1363.5 | 47.1 | 2.76 | - | 108390 | 0 | 108390
P00704 | 47.5 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.26 | -6.86 | 23.1 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1089.2 | 28.2 | 2.94 | - | 88319 | 0 | 88319
P00705 | 47.5 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.44 | -5 | 18.2 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 801.2 | 14.5 | 3.23 | - | 66223 | 0 | 66223
P00706 | 47.5 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.67 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 496.6 | 5.7 | 3.76 | - | 41796 | 0 | 41796
P00707 | 47.5 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.3 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 155.6 | 0.7 | 5.65 | - | 13339 | 0 | 13339
P00708 | 47.5 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.23 | -8.95 | 29.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1409.8 | 51.1 | 2.74 | - | 111616 | 0 | 111616
P00709 | 55 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -7.54 | -9.93 | 33.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1690.2 | 79.1 | 2.5 | - | 121908 | 0 | 121908
P00710 | 55 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.51 | -8.43 | 27.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1437.2 | 53.6 | 2.58 | - | 105972 | 0 | 105972
P00711 | 55 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.15 | -6.79 | 22.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1161.3 | 32.7 | 2.74 | - | 87482 | 0 | 87482
P00712 | 55 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.34 | -4.93 | 18.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 850.8 | 16.8 | 2.99 | - | 65426 | 0 | 65426
P00713 | 55 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.69 | -3.01 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 531.5 | 6.6 | 3.43 | - | 41673 | 0 | 41673
P00714 | 55 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.31 | -0.8 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 165.4 | 0.8 | 5.08 | - | 13229 | 0 | 13229
P00715 | 55 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.93 | -8.73 | 29 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1488.9 | 58.4 | 2.56 | - | 109309 | 0 | 109309
P00716 | 62.5 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -7.03 | -9.55 | 31.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1781.6 | 89.4 | 2.35 | - | 117966 | 0 | 117966
P00717 | 62.5 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.22 | -8.22 | 27.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1529.2 | 61.9 | 2.42 | - | 103715 | 0 | 103715
P00718 | 62.5 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -2.98 | -6.68 | 22.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1241.1 | 38.3 | 2.54 | - | 86152 | 0 | 86152
P00719 | 62.5 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.18 | -4.83 | 17.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 903.6 | 19.6 | 2.73 | - | 64144 | 0 | 64144
P00720 | 62.5 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.79 | -2.95 | 14.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 563.7 | 7.7 | 3.12 | - | 40872 | 0 | 40872
P00721 | 62.5 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.29 | -0.82 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 181.1 | 0.9 | 4.6 | - | 13407 | 0 | 13407
P00722 | 62.5 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.64 | -8.52 | 28.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1585.7 | 67.4 | 2.4 | - | 107038 | 0 | 107038
P00723 | 70 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -6.55 | -9.19 | 30.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1898.8 | 102.5 | 2.21 | - | 114172 | 0 | 114172
P00724 | 70 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -4.89 | -7.99 | 26.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1637.6 | 72.1 | 2.25 | - | 101100 | 0 | 101100
P00725 | 70 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -2.74 | -6.51 | 22.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1329.8 | 44.9 | 2.36 | - | 84218 | 0 | 84218
P00726 | 70 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.09 | -4.77 | 17.7 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 977.5 | 23.3 | 2.52 | - | 63441 | 0 | 63441
P00727 | 70 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.82 | -2.93 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 611.5 | 9.2 | 2.85 | - | 40612 | 0 | 40612
P00728 | 70 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.31 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 195.3 | 1 | 4.14 | - | 13274 | 0 | 13274
P00729 | 70 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.27 | -8.27 | 27.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1695.6 | 78.2 | 2.24 | - | 104137 | 0 | 104137
P00730 | 56 | -20 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -7.43 | -9.85 | 33 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1696.7 | 79.9 | 2.49 | - | 121058 | 0 | 121058
P00731 | 56 | -15 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.47 | -8.4 | 27.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1448.8 | 54.6 | 2.56 | - | 105699 | 0 | 105699
P00732 | 56 | -10 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.14 | -6.78 | 22.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1171.8 | 33.4 | 2.71 | - | 87359 | 0 | 87359
P00733 | 56 | -5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.26 | -4.88 | 18 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 851.1 | 17 | 2.93 | - | 64788 | 0 | 64788
P00734 | 56 | 0 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.69 | -3.01 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 536.5 | 6.8 | 3.39 | - | 41649 | 0 | 41649
P00735 | 56 | 5 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.31 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 167.3 | 0.8 | 5.01 | - | 13249 | 0 | 13249
P00736 | 56 | -16 | 8 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -5.9 | -8.71 | 28.9 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1501.1 | 59.5 | 2.54 | - | 109037 | 0 | 109037
P00737 | 25 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.54 | -9.94 | 33.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1541.3 | 57.7 | 3.25 | - | 145356 | 0 | 145356
P00738 | 25 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.34 | -8.34 | 27.5 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1300.5 | 38.1 | 3.44 | - | 124742 | 0 | 124742
P00739 | 25 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.73 | -6.51 | 22.1 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1029.3 | 22.5 | 3.73 | - | 100364 | 0 | 100364
P00740 | 25 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -0.02 | -4.72 | 17.6 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 756.5 | 11.6 | 4.22 | - | 74950 | 0 | 74950
P00741 | 25 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 2.99 | -2.83 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 465.8 | 4.5 | 5.13 | - | 46858 | 0 | 46858
P00742 | 25 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.43 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 143.7 | 0.5 | 7.66 | - | 14673 | 0 | 14673
P00743 | 25 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.74 | -8.6 | 28.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1344.1 | 41.8 | 3.36 | - | 128491 | 0 | 128491
P00744 | 32.5 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.24 | -9.71 | 32.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1602.5 | 64 | 3.04 | - | 142559 | 0 | 142559
P00745 | 32.5 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.12 | -8.12 | 27 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1354.4 | 43 | 3.15 | - | 122665 | 0 | 122665
P00746 | 32.5 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.66 | -6.46 | 21.9 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1081.8 | 25.6 | 3.39 | - | 99704 | 0 | 99704
P00747 | 32.5 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.04 | -4.69 | 17.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 794 | 13.2 | 3.76 | - | 74428 | 0 | 74428
P00748 | 32.5 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 2.98 | -2.83 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 492.3 | 5.2 | 4.45 | - | 46893 | 0 | 46893
P00749 | 32.5 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.41 | -0.75 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 153.5 | 0.6 | 6.72 | - | 14861 | 0 | 14861
P00750 | 32.5 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.56 | -8.46 | 28 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1404.6 | 47 | 3.11 | - | 126761 | 0 | 126761
P00751 | 40 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -6.94 | -9.48 | 31.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1674 | 71.6 | 2.85 | - | 139766 | 0 | 139766
P00752 | 40 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.93 | -8.02 | 26.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1420.8 | 48.7 | 2.93 | - | 120913 | 0 | 120913
P00753 | 40 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.57 | -6.4 | 21.8 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1140.1 | 29.3 | 3.12 | - | 98835 | 0 | 98835
P00754 | 40 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.09 | -4.66 | 17.4 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 837.8 | 15.1 | 3.43 | - | 73947 | 0 | 73947
P00755 | 40 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 2.99 | -2.82 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 521.7 | 5.9 | 3.99 | - | 46833 | 0 | 46833
P00756 | 40 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.43 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 160.7 | 0.7 | 5.95 | - | 14673 | 0 | 14673
P00757 | 40 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.37 | -8.37 | 27.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1475.2 | 53.2 | 2.9 | - | 125064 | 0 | 125064
P00758 | 47.5 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -6.55 | -9.19 | 30.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1747.3 | 80.5 | 2.65 | - | 136084 | 0 | 136084
P00759 | 47.5 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.74 | -7.88 | 26.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1498.1 | 55.4 | 2.74 | - | 119087 | 0 | 119087
P00760 | 47.5 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.44 | -6.31 | 21.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1204.3 | 33.6 | 2.9 | - | 97650 | 0 | 97650
P00761 | 47.5 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.25 | -4.55 | 17.2 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 876.1 | 17.1 | 3.14 | - | 72411 | 0 | 72411
P00762 | 47.5 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3 | -2.81 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 554.7 | 6.9 | 3.62 | - | 46686 | 0 | 46686
P00763 | 47.5 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.41 | -0.75 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 173.6 | 0.8 | 5.36 | - | 14884 | 0 | 14884
P00764 | 47.5 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.1 | -8.1 | 27 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1546.9 | 59.8 | 2.73 | - | 122469 | 0 | 122469
P00765 | 55 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -6.2 | -8.93 | 29.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1841.3 | 90.8 | 2.5 | - | 132807 | 0 | 132807
P00766 | 55 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.44 | -7.67 | 25.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1577 | 62.7 | 2.58 | - | 116283 | 0 | 116283
P00767 | 55 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.33 | -6.24 | 21.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1281.9 | 38.9 | 2.7 | - | 96563 | 0 | 96563
P00768 | 55 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.33 | -4.5 | 17.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 932.6 | 19.9 | 2.9 | - | 71714 | 0 | 71714
P00769 | 55 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.09 | -2.76 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 585.6 | 7.9 | 3.28 | - | 45918 | 0 | 45918
P00770 | 55 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.42 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 184.1 | 0.9 | 4.82 | - | 14718 | 0 | 14718
P00771 | 55 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.81 | -7.93 | 26.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1631.2 | 68 | 2.55 | - | 119753 | 0 | 119753
P00772 | 62.5 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -5.74 | -8.59 | 28.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1940.2 | 102.5 | 2.35 | - | 128467 | 0 | 128467
P00773 | 62.5 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.11 | -7.45 | 24.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1669.3 | 71.7 | 2.41 | - | 113213 | 0 | 113213
P00774 | 62.5 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.06 | -6.06 | 20.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1355.2 | 45 | 2.49 | - | 94071 | 0 | 94071
P00775 | 62.5 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.43 | -4.44 | 17 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 997.5 | 23.3 | 2.68 | - | 70806 | 0 | 70806
P00776 | 62.5 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.14 | -2.73 | 14 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 626.5 | 9.3 | 3.02 | - | 45425 | 0 | 45425
P00777 | 62.5 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.4 | -0.75 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 201.5 | 1 | 4.36 | - | 14922 | 0 | 14922
P00778 | 62.5 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.51 | -7.72 | 25.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1732.5 | 77.9 | 2.4 | - | 116948 | 0 | 116948
P00779 | 70 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -5.2 | -8.2 | 27.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2052.2 | 115.7 | 2.22 | - | 123394 | 0 | 123394
P00780 | 70 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -3.78 | -7.22 | 24.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1784.5 | 83.2 | 2.25 | - | 110172 | 0 | 110172
P00781 | 70 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -1.81 | -5.89 | 20.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1448.7 | 52.4 | 2.32 | - | 91744 | 0 | 91744
P00782 | 70 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.51 | -4.39 | 16.9 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1079 | 27.8 | 2.47 | - | 70028 | 0 | 70028
P00783 | 70 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.18 | -2.7 | 14 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 678.2 | 11 | 2.77 | - | 45042 | 0 | 45042
P00784 | 70 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.42 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 217 | 1.2 | 3.92 | - | 14751 | 0 | 14751
P00785 | 70 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.12 | -7.46 | 24.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1845.5 | 89.9 | 2.24 | - | 113346 | 0 | 113346
P00786 | 56 | -20 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -6.15 | -8.9 | 29.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1854.7 | 92.3 | 2.48 | - | 132333 | 0 | 132333
P00787 | 56 | -15 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.38 | -7.64 | 25.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1586.9 | 63.7 | 2.55 | - | 115777 | 0 | 115777
P00788 | 56 | -10 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.27 | -6.2 | 21.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1288.2 | 39.5 | 2.67 | - | 96033 | 0 | 96033
P00789 | 56 | -5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.34 | -4.49 | 17.1 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 940.7 | 20.3 | 2.87 | - | 71609 | 0 | 71609
P00790 | 56 | 0 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.11 | -2.75 | 14 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 588.1 | 8 | 3.25 | - | 45657 | 0 | 45657
P00791 | 56 | 5 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.42 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 186.1 | 0.9 | 4.76 | - | 14736 | 0 | 14736
P00792 | 56 | -16 | 8 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -4.77 | -7.9 | 26.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1643.6 | 69.2 | 2.53 | - | 119388 | 0 | 119388
P00793 | 25 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.32 | -9.02 | 29.9 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1648.6 | 65.4 | 3.21 | - | 155473 | 0 | 155473
P00794 | 25 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.35 | -7.61 | 25.3 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1397.9 | 43.8 | 3.38 | - | 134075 | 0 | 134075
P00795 | 25 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.1 | -6.1 | 20.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1124.7 | 26.4 | 3.66 | - | 109663 | 0 | 109663
P00796 | 25 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.52 | -4.38 | 16.9 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 819.8 | 13.4 | 4.13 | - | 81224 | 0 | 81224
P00797 | 25 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.26 | -2.65 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 510.8 | 5.3 | 4.98 | - | 51381 | 0 | 51381
P00798 | 25 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.52 | -0.68 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 157.7 | 0.6 | 7.39 | - | 16109 | 0 | 16109
P00799 | 25 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.76 | -7.9 | 26.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1448.7 | 47.8 | 3.33 | - | 138487 | 0 | 138487
P00800 | 32.5 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.09 | -8.85 | 29.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1719.2 | 72.8 | 3 | - | 152937 | 0 | 152937
P00801 | 32.5 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.18 | -7.5 | 24.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1460.3 | 49.1 | 3.12 | - | 132258 | 0 | 132258
P00802 | 32.5 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.97 | -5.97 | 20.7 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1174 | 29.6 | 3.35 | - | 108201 | 0 | 108201
P00803 | 32.5 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.56 | -4.35 | 16.8 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 861.7 | 15.3 | 3.69 | - | 80767 | 0 | 80767
P00804 | 32.5 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.28 | -2.64 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 537.2 | 6 | 4.31 | - | 51170 | 0 | 51170
P00805 | 32.5 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.5 | -0.7 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 168.5 | 0.7 | 6.45 | - | 16311 | 0 | 16311
P00806 | 32.5 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.6 | -7.79 | 25.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1515.2 | 53.7 | 3.09 | - | 136749 | 0 | 136749
P00807 | 40 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -5.75 | -8.6 | 28.5 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1788.2 | 80.4 | 2.83 | - | 149294 | 0 | 149294
P00808 | 40 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.03 | -7.39 | 24.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1534.7 | 55.5 | 2.92 | - | 130599 | 0 | 130599
P00809 | 40 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.87 | -5.93 | 20.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1235.6 | 33.7 | 3.09 | - | 107121 | 0 | 107121
P00810 | 40 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.67 | -4.28 | 16.7 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 901.5 | 17.4 | 3.33 | - | 79571 | 0 | 79571
P00811 | 40 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.35 | -2.6 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 561.7 | 6.9 | 3.82 | - | 50430 | 0 | 50430
P00812 | 40 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.51 | -0.69 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 176.4 | 0.8 | 5.7 | - | 16114 | 0 | 16114
P00813 | 40 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.4 | -7.65 | 25.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1588.4 | 60.3 | 2.89 | - | 134662 | 0 | 134662
P00814 | 47.5 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -5.41 | -8.41 | 27.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1868.9 | 89.7 | 2.66 | - | 145549 | 0 | 145549
P00815 | 47.5 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.8 | -7.24 | 24.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1611.6 | 62.6 | 2.73 | - | 128109 | 0 | 128109
P00816 | 47.5 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.76 | -5.86 | 20.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1307 | 38.8 | 2.87 | - | 105977 | 0 | 105977
P00817 | 47.5 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.73 | -4.27 | 16.6 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 953.9 | 20 | 3.08 | - | 78844 | 0 | 78844
P00818 | 47.5 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.36 | -2.59 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 598 | 8 | 3.48 | - | 50334 | 0 | 50334
P00819 | 47.5 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.49 | -0.7 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 190.5 | 0.9 | 5.13 | - | 16328 | 0 | 16328
P00820 | 47.5 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.18 | -7.5 | 24.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1670.4 | 68.2 | 2.71 | - | 132249 | 0 | 132249
P00821 | 55 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -5.05 | -8.05 | 26.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1964.7 | 100.5 | 2.52 | - | 141703 | 0 | 141703
P00822 | 55 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.56 | -7.07 | 23.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1702.5 | 71.4 | 2.56 | - | 125536 | 0 | 125536
P00823 | 55 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.59 | -5.75 | 20.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1382.5 | 44.5 | 2.67 | - | 104138 | 0 | 104138
P00824 | 55 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.77 | -4.23 | 16.6 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1019.9 | 23.3 | 2.85 | - | 78429 | 0 | 78429
P00825 | 55 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.39 | -2.61 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 638.4 | 9.3 | 3.19 | - | 50060 | 0 | 50060
P00826 | 55 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.47 | -0.71 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 207.8 | 1 | 4.62 | - | 16615 | 0 | 16615
P00827 | 55 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.86 | -7.28 | 24.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1754.1 | 76.6 | 2.56 | - | 128776 | 0 | 128776
P00828 | 62.5 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -4.61 | -7.79 | 25.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2067.4 | 113.1 | 2.36 | - | 136884 | 0 | 136884
P00829 | 62.5 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.21 | -6.83 | 23 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1794.5 | 80.7 | 2.41 | - | 121708 | 0 | 121708
P00830 | 62.5 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.35 | -5.59 | 19.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1462.7 | 51.3 | 2.47 | - | 101534 | 0 | 101534
P00831 | 62.5 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.89 | -4.11 | 16.4 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1086.5 | 27 | 2.65 | - | 77124 | 0 | 77124
P00832 | 62.5 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.42 | -2.58 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 685.1 | 10.9 | 2.93 | - | 49671 | 0 | 49671
P00833 | 62.5 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.49 | -0.7 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 221 | 1.2 | 4.17 | - | 16363 | 0 | 16363
P00834 | 62.5 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.51 | -7.04 | 23.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1851.3 | 87 | 2.39 | - | 124967 | 0 | 124967
P00835 | 70 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -4.1 | -7.44 | 24.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2185 | 127.4 | 2.24 | - | 131381 | 0 | 131381
P00836 | 70 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.87 | -6.6 | 22.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1911 | 92.7 | 2.26 | - | 117978 | 0 | 117978
P00837 | 70 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.13 | -5.44 | 19.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1564.3 | 59.8 | 2.3 | - | 99064 | 0 | 99064
P00838 | 70 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 1 | -4.07 | 16.3 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1171.3 | 32.1 | 2.45 | - | 76017 | 0 | 76017
P00839 | 70 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.46 | -2.54 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 741.3 | 12.9 | 2.7 | - | 49231 | 0 | 49231
P00840 | 70 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.51 | -0.69 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 238.1 | 1.3 | 3.75 | - | 16183 | 0 | 16183
P00841 | 70 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.12 | -6.77 | 22.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1966 | 99.3 | 2.26 | - | 120747 | 0 | 120747
P00842 | 56 | -20 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -5 | -8.07 | 26.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1978 | 102.1 | 2.5 | - | 141128 | 0 | 141128
P00843 | 56 | -15 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.53 | -7.05 | 23.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1715.3 | 72.6 | 2.54 | - | 125148 | 0 | 125148
P00844 | 56 | -10 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.57 | -5.74 | 20 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1393.6 | 45.3 | 2.65 | - | 103895 | 0 | 103895
P00845 | 56 | -5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.78 | -4.22 | 16.6 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1028.8 | 23.8 | 2.82 | - | 78314 | 0 | 78314
P00846 | 56 | 0 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.39 | -2.61 | 13.8 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 644.3 | 9.5 | 3.16 | - | 50025 | 0 | 50025
P00847 | 56 | 5 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.46 | -0.72 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 211.1 | 1 | 4.55 | - | 16712 | 0 | 16712
P00848 | 56 | -16 | 8 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -3.82 | -7.25 | 24.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1766.8 | 77.9 | 2.53 | - | 128335 | 0 | 128335
P00849 | 25 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.46 | -8.4 | 27.8 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1758.2 | 71.9 | 3.25 | - | 165807 | 0 | 165807
P00850 | 25 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.58 | -7.09 | 23.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1487 | 48.6 | 3.38 | - | 142626 | 0 | 142626
P00851 | 25 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.51 | -5.7 | 19.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1201.2 | 29.7 | 3.62 | - | 117127 | 0 | 117127
P00852 | 25 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 0.93 | -4.07 | 16.4 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 878.5 | 15.1 | 4.08 | - | 87039 | 0 | 87039
P00853 | 25 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.52 | -2.48 | 13.6 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 548.2 | 6 | 4.86 | - | 55141 | 0 | 55141
P00854 | 25 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.58 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 171.4 | 0.7 | 7.13 | - | 17503 | 0 | 17503
P00855 | 25 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.05 | -7.41 | 24.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1552.2 | 53.7 | 3.32 | - | 148382 | 0 | 148382
P00856 | 32.5 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.13 | -8.13 | 27 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1817.9 | 79.7 | 3 | - | 161720 | 0 | 161720
P00857 | 32.5 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.5 | -7.03 | 23.5 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1563.4 | 55.2 | 3.11 | - | 141601 | 0 | 141601
P00858 | 32.5 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.43 | -5.64 | 19.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1260.3 | 33.6 | 3.31 | - | 116148 | 0 | 116148
P00859 | 32.5 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 0.98 | -4.08 | 16.3 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 921.7 | 17.1 | 3.65 | - | 86398 | 0 | 86398
P00860 | 32.5 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.51 | -2.49 | 13.6 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 580.3 | 6.9 | 4.2 | - | 55274 | 0 | 55274
P00861 | 32.5 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.57 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 182.1 | 0.8 | 6.22 | - | 17622 | 0 | 17622
P00862 | 32.5 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.82 | -7.25 | 24.2 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1612.5 | 59.5 | 3.09 | - | 145527 | 0 | 145527
P00863 | 40 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -4.94 | -8.02 | 26.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1908.6 | 88.4 | 2.86 | - | 159350 | 0 | 159350
P00864 | 40 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.24 | -6.85 | 23 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1626.4 | 61.3 | 2.91 | - | 138410 | 0 | 138410
P00865 | 40 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.34 | -5.58 | 19.6 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1326.3 | 38.3 | 3.06 | - | 114981 | 0 | 114981
P00866 | 40 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.05 | -4.04 | 16.3 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 968.9 | 19.5 | 3.34 | - | 85516 | 0 | 85516
P00867 | 40 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.53 | -2.47 | 13.6 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 613.3 | 7.9 | 3.78 | - | 55064 | 0 | 55064
P00868 | 40 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.55 | -0.67 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 195.7 | 0.9 | 5.53 | - | 17874 | 0 | 17874
P00869 | 40 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.6 | -7.09 | 23.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1684.3 | 66.6 | 2.89 | - | 142797 | 0 | 142797
P00870 | 47.5 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -4.52 | -7.73 | 25.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1979.4 | 98.2 | 2.67 | - | 154159 | 0 | 154159
P00871 | 47.5 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.02 | -6.7 | 22.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1706.5 | 69 | 2.73 | - | 135654 | 0 | 135654
P00872 | 47.5 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.2 | -5.49 | 19.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1396.3 | 43.5 | 2.85 | - | 113219 | 0 | 113219
P00873 | 47.5 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.06 | -4.03 | 16.2 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1033.4 | 22.7 | 3.09 | - | 85415 | 0 | 85415
P00874 | 47.5 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.58 | -2.42 | 13.6 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 647 | 9 | 3.46 | - | 54462 | 0 | 54462
P00875 | 47.5 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.56 | -0.66 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 206.2 | 1 | 4.94 | - | 17675 | 0 | 17675
P00876 | 47.5 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.38 | -6.95 | 23.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1770.1 | 74.9 | 2.72 | - | 140144 | 0 | 140144
P00877 | 55 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -4.18 | -7.49 | 24.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 2078.9 | 110.1 | 2.51 | - | 149941 | 0 | 149941
P00878 | 55 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.77 | -6.54 | 22.1 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1799.4 | 78.2 | 2.56 | - | 132677 | 0 | 132677
P00879 | 55 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.05 | -5.39 | 19.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1479.3 | 50 | 2.66 | - | 111431 | 0 | 111431
P00880 | 55 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.19 | -3.95 | 16.1 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1090.7 | 26.3 | 2.82 | - | 83877 | 0 | 83877
P00881 | 55 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.65 | -2.41 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 682.7 | 10.4 | 3.14 | - | 53536 | 0 | 53536
P00882 | 55 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.55 | -0.67 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 223.7 | 1.1 | 4.47 | - | 17890 | 0 | 17890
P00883 | 55 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.1 | -6.76 | 22.8 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1862 | 84.7 | 2.55 | - | 136697 | 0 | 136697
P00884 | 62.5 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -3.72 | -7.18 | 24 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2179.1 | 122.3 | 2.39 | - | 144284 | 0 | 144284
P00885 | 62.5 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.49 | -6.35 | 21.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1904.9 | 89.1 | 2.41 | - | 129195 | 0 | 129195
P00886 | 62.5 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.82 | -5.24 | 18.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1564.1 | 57.1 | 2.49 | - | 108572 | 0 | 108572
P00887 | 62.5 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.29 | -3.89 | 16 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1164.3 | 30.6 | 2.61 | - | 82648 | 0 | 82648
P00888 | 62.5 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.69 | -2.39 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 731.7 | 12.2 | 2.88 | - | 53048 | 0 | 53048
P00889 | 62.5 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.56 | -0.66 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 239 | 1.3 | 4.02 | - | 17699 | 0 | 17699
P00890 | 62.5 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.72 | -6.5 | 22 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1956 | 95.1 | 2.4 | - | 132033 | 0 | 132033
P00891 | 70 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -3.23 | -6.85 | 23 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2300.1 | 137.6 | 2.25 | - | 138299 | 0 | 138299
P00892 | 70 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.1 | -6.1 | 20.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 2014.7 | 101.3 | 2.26 | - | 124384 | 0 | 124384
P00893 | 70 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -0.52 | -5.05 | 18.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1656.7 | 65.8 | 2.3 | - | 104919 | 0 | 104919
P00894 | 70 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.4 | -3.82 | 15.9 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1251.3 | 36.1 | 2.42 | - | 81209 | 0 | 81209
P00895 | 70 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.77 | -2.34 | 13.4 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 784 | 14.4 | 2.63 | - | 52073 | 0 | 52073
P00896 | 70 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.54 | -0.67 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 264.3 | 1.5 | 3.64 | - | 17962 | 0 | 17962
P00897 | 70 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.38 | -6.27 | 21.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 2080.6 | 109 | 2.25 | - | 127783 | 0 | 127783
P00898 | 56 | -20 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -4.13 | -7.46 | 24.8 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 2093.1 | 111.8 | 2.49 | - | 149336 | 0 | 149336
P00899 | 56 | -15 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -2.74 | -6.52 | 22.1 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1813.4 | 79.7 | 2.54 | - | 132300 | 0 | 132300
P00900 | 56 | -10 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.03 | -5.38 | 19.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1491 | 50.9 | 2.63 | - | 111154 | 0 | 111154
P00901 | 56 | -5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.19 | -3.95 | 16.1 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1101.9 | 26.9 | 2.79 | - | 83877 | 0 | 83877
P00902 | 56 | 0 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.65 | -2.41 | 13.5 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 688.9 | 10.6 | 3.11 | - | 53488 | 0 | 53488
P00903 | 56 | 5 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.54 | -0.67 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 226.3 | 1.1 | 4.41 | - | 17919 | 0 | 17919
P00904 | 56 | -16 | 8 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.06 | -6.73 | 22.7 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1875.4 | 86.1 | 2.53 | - | 136224 | 0 | 136224
P00905 | 25 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.96 | -10.26 | 34.5 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1467.2 | 53.7 | 3.22 | - | 138364 | 0 | 138364
P00906 | 25 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.7 | -8.57 | 28.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1238.2 | 35.4 | 3.42 | - | 118760 | 0 | 118760
P00907 | 25 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.03 | -6.71 | 22.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 980.5 | 20.7 | 3.74 | - | 95604 | 0 | 95604
P00908 | 25 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.24 | -4.87 | 17.9 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 720.7 | 10.6 | 4.27 | - | 71402 | 0 | 71402
P00909 | 25 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.87 | -2.9 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 441.4 | 4.1 | 5.22 | - | 44403 | 0 | 44403
P00910 | 25 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.39 | -0.76 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 136.8 | 0.5 | 7.84 | - | 13974 | 0 | 13974
P00911 | 25 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.17 | -8.91 | 29.6 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1284.7 | 38.7 | 3.37 | - | 122814 | 0 | 122814
P00912 | 32.5 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.74 | -10.09 | 33.9 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1533.8 | 60.2 | 3 | - | 136444 | 0 | 136444
P00913 | 32.5 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.54 | -8.45 | 28 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1295.3 | 39.9 | 3.15 | - | 117318 | 0 | 117318
P00914 | 32.5 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.04 | -6.72 | 22.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1038 | 23.8 | 3.4 | - | 95661 | 0 | 95661
P00915 | 32.5 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.19 | -4.83 | 17.9 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 757 | 12.1 | 3.8 | - | 70960 | 0 | 70960
P00916 | 32.5 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.87 | -2.9 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 466.6 | 4.7 | 4.53 | - | 44442 | 0 | 44442
P00917 | 32.5 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.37 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 146.1 | 0.6 | 6.89 | - | 14144 | 0 | 14144
P00918 | 32.5 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.01 | -8.79 | 29.2 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1345.4 | 43.7 | 3.12 | - | 121424 | 0 | 121424
P00919 | 40 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.42 | -9.85 | 32.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1601.2 | 67.1 | 2.83 | - | 133681 | 0 | 133681
P00920 | 40 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.35 | -8.35 | 27.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1359.9 | 45.2 | 2.94 | - | 115723 | 0 | 115723
P00921 | 40 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.95 | -6.65 | 22.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1094.4 | 27.3 | 3.14 | - | 94872 | 0 | 94872
P00922 | 40 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.09 | -4.77 | 17.7 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 794.4 | 13.9 | 3.43 | - | 70119 | 0 | 70119
P00923 | 40 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.86 | -2.9 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 496 | 5.4 | 4.05 | - | 44534 | 0 | 44534
P00924 | 40 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.38 | -0.76 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 153.2 | 0.6 | 6.1 | - | 13994 | 0 | 13994
P00925 | 40 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.81 | -8.64 | 28.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1411.5 | 49.4 | 2.91 | - | 119668 | 0 | 119668
P00926 | 47.5 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.09 | -9.59 | 32 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1679.2 | 75.4 | 2.66 | - | 130776 | 0 | 130776
P00927 | 47.5 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.2 | -8.2 | 27.2 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1438.7 | 51.6 | 2.75 | - | 114365 | 0 | 114365
P00928 | 47.5 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.85 | -6.58 | 22.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1159.1 | 31.4 | 2.91 | - | 93982 | 0 | 93982
P00929 | 47.5 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.04 | -4.73 | 17.6 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 842.3 | 16 | 3.16 | - | 69617 | 0 | 69617
P00930 | 47.5 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.88 | -2.89 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 527.3 | 6.3 | 3.68 | - | 44380 | 0 | 44380
P00931 | 47.5 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.36 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 165.3 | 0.7 | 5.5 | - | 14172 | 0 | 14172
P00932 | 47.5 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.6 | -8.49 | 28.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1488.9 | 56.1 | 2.72 | - | 117876 | 0 | 117876
P00933 | 55 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -6.74 | -9.33 | 31.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1771.6 | 85.2 | 2.51 | - | 127778 | 0 | 127778
P00934 | 55 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.93 | -8.02 | 26.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1519.9 | 59 | 2.57 | - | 112071 | 0 | 112071
P00935 | 55 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.67 | -6.46 | 21.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1227 | 36.1 | 2.72 | - | 92426 | 0 | 92426
P00936 | 55 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.05 | -4.68 | 17.5 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 896 | 18.6 | 2.92 | - | 68903 | 0 | 68903
P00937 | 55 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.95 | -2.85 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 557.8 | 7.3 | 3.33 | - | 43741 | 0 | 43741
P00938 | 55 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.38 | -0.76 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 175.5 | 0.8 | 4.94 | - | 14030 | 0 | 14030
P00939 | 55 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.35 | -8.35 | 27.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1575.4 | 64.2 | 2.55 | - | 115662 | 0 | 115662
P00940 | 62.5 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -6.27 | -8.98 | 29.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1868.2 | 96.2 | 2.36 | - | 123700 | 0 | 123700
P00941 | 62.5 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.64 | -7.82 | 25.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1615.8 | 67.9 | 2.41 | - | 109586 | 0 | 109586
P00942 | 62.5 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.48 | -6.33 | 21.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1307.7 | 41.9 | 2.52 | - | 90770 | 0 | 90770
P00943 | 62.5 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.18 | -4.6 | 17.3 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 955 | 21.5 | 2.71 | - | 67792 | 0 | 67792
P00944 | 62.5 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.96 | -2.84 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 601.6 | 8.6 | 3.05 | - | 43619 | 0 | 43619
P00945 | 62.5 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.36 | -0.78 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 192 | 1 | 4.47 | - | 14217 | 0 | 14217
P00946 | 62.5 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.98 | -8.05 | 26.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1666.1 | 73.1 | 2.4 | - | 112462 | 0 | 112462
P00947 | 70 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -5.79 | -8.63 | 28.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1987.9 | 110.2 | 2.22 | - | 119524 | 0 | 119524
P00948 | 70 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.23 | -7.53 | 25 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1716.8 | 77.8 | 2.26 | - | 105992 | 0 | 105992
P00949 | 70 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.19 | -6.19 | 21.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1394.5 | 49.1 | 2.32 | - | 88314 | 0 | 88314
P00950 | 70 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.21 | -4.58 | 17.3 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1039.6 | 26 | 2.49 | - | 67468 | 0 | 67468
P00951 | 70 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3 | -2.82 | 14.1 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 651.9 | 10.3 | 2.79 | - | 43296 | 0 | 43296
P00952 | 70 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.37 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 207.2 | 1.1 | 4.02 | - | 14080 | 0 | 14080
P00953 | 70 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.57 | -7.77 | 25.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1774.4 | 84.1 | 2.25 | - | 108977 | 0 | 108977
P00954 | 56 | -20 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -6.71 | -9.31 | 31 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1787.1 | 86.8 | 2.49 | - | 127510 | 0 | 127510
P00955 | 56 | -15 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -4.9 | -7.99 | 26.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1532 | 60.1 | 2.55 | - | 111771 | 0 | 111771
P00956 | 56 | -10 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.64 | -6.45 | 21.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1237.3 | 36.8 | 2.69 | - | 92242 | 0 | 92242
P00957 | 56 | -5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 0.06 | -4.68 | 17.5 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 903.9 | 19 | 2.89 | - | 68809 | 0 | 68809
P00958 | 56 | 0 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.95 | -2.85 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 563.4 | 7.5 | 3.29 | - | 43741 | 0 | 43741
P00959 | 56 | 5 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.38 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 177.5 | 0.8 | 4.88 | - | 14055 | 0 | 14055
P00960 | 56 | -16 | 8 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.31 | -8.31 | 27.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1587.8 | 65.3 | 2.53 | - | 115331 | 0 | 115331
P00961 | 25 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.91 | -9.47 | 54.7 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1514.5 | 54.6 | 3.34 | - | 142823 | 0 | 142823
P00962 | 25 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.36 | -7.63 | 43.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1323.1 | 38 | 3.54 | - | 126909 | 0 | 126909
P00963 | 25 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.52 | -5.71 | 34.5 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1119.8 | 24.7 | 3.88 | - | 109184 | 0 | 109184
P00964 | 25 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.74 | -3.62 | 26.5 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 897.1 | 14.6 | 4.4 | - | 88883 | 0 | 88883
P00965 | 25 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.09 | -1.56 | 20.8 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 675.8 | 7.9 | 5.15 | - | 67980 | 0 | 67980
P00966 | 25 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.83 | 0.65 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 437.3 | 3.2 | 6.95 | - | 44670 | 0 | 44670
P00968 | 25 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.97 | -8.06 | 46.2 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1367.4 | 41.2 | 3.5 | - | 130721 | 0 | 130721
P00969 | 32.5 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.6 | -9.23 | 53.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1583.5 | 61.4 | 3.11 | - | 140869 | 0 | 140869
P00970 | 32.5 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.23 | -7.54 | 43.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1392.4 | 43.3 | 3.28 | - | 126108 | 0 | 126108
P00971 | 32.5 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.36 | -5.61 | 34 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1173.6 | 28.2 | 3.52 | - | 108165 | 0 | 108165
P00972 | 32.5 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.89 | -3.52 | 26.1 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 937.7 | 16.8 | 3.86 | - | 87890 | 0 | 87890
P00973 | 32.5 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.11 | -1.54 | 20.8 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 712.1 | 9.1 | 4.42 | - | 67822 | 0 | 67822
P00974 | 32.5 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.76 | 0.61 | 16.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 465.9 | 3.8 | 5.45 | - | 45100 | 0 | 45100
P00975 | 32.5 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.58 | 2.77 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 20 | 216.6 | 0.7 | 7.41 | - | 21287 | 0 | 21287
P00976 | 32.5 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.75 | -7.9 | 45.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1433 | 46.9 | 3.23 | - | 129331 | 0 | 129331
P00977 | 40 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.3 | -9.02 | 51.8 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1665.1 | 69.6 | 2.91 | - | 139018 | 0 | 139018
P00978 | 40 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.89 | -7.31 | 42.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1456.8 | 49.5 | 3.01 | - | 123975 | 0 | 123975
P00979 | 40 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.2 | -5.5 | 33.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1236.3 | 32.4 | 3.24 | - | 107179 | 0 | 107179
P00980 | 40 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.03 | -3.44 | 25.9 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 986.1 | 19.2 | 3.52 | - | 87031 | 0 | 87031
P00981 | 40 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.16 | -1.51 | 20.7 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 752.3 | 10.5 | 3.95 | - | 67537 | 0 | 67537
P00982 | 40 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.76 | 0.61 | 16.2 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 494 | 4.4 | 4.76 | - | 45119 | 0 | 45119
P00983 | 40 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.56 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 20 | 230.7 | 0.8 | 6.43 | - | 21412 | 0 | 21412
P00984 | 40 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.51 | -7.74 | 44.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1507.8 | 53.3 | 3.01 | - | 127831 | 0 | 127831
P00985 | 47.5 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.84 | -8.68 | 49.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1748.5 | 78.3 | 2.75 | - | 136173 | 0 | 136173
P00986 | 47.5 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.62 | -7.13 | 41.2 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1538.7 | 56.6 | 2.82 | - | 122313 | 0 | 122313
P00987 | 47.5 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.04 | -5.4 | 33.1 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1309.4 | 37.4 | 3.01 | - | 106168 | 0 | 106168
P00988 | 47.5 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1 | -3.46 | 25.9 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1055.3 | 22.6 | 3.23 | - | 87222 | 0 | 87222
P00989 | 47.5 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.22 | -1.48 | 20.6 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 798.1 | 12.2 | 3.59 | - | 67172 | 0 | 67172
P00990 | 47.5 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.8 | 0.63 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 523.5 | 5.2 | 4.22 | - | 44878 | 0 | 44878
P00991 | 47.5 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.52 | 2.73 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 20 | 248.3 | 1 | 5.7 | - | 21649 | 0 | 21649
P00992 | 47.5 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.14 | -7.48 | 43 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1585.5 | 60.4 | 2.83 | - | 125528 | 0 | 125528
P00993 | 55 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.38 | -8.38 | 47.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1848.1 | 89 | 2.59 | - | 133298 | 0 | 133298
P00994 | 55 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.21 | -6.85 | 39.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1624 | 64.5 | 2.64 | - | 119745 | 0 | 119745
P00995 | 55 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.78 | -5.23 | 32.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1388.5 | 43.5 | 2.78 | - | 104593 | 0 | 104593
P00996 | 55 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.17 | -3.35 | 25.6 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1120.5 | 26.3 | 2.98 | - | 86167 | 0 | 86167
P00997 | 55 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.28 | -1.44 | 20.6 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 851.8 | 14.3 | 3.29 | - | 66793 | 0 | 66793
P00998 | 55 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.82 | 0.65 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 559.2 | 6.1 | 3.82 | - | 44718 | 0 | 44718
P00999 | 55 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.56 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 20 | 263 | 1.1 | 5.07 | - | 21425 | 0 | 21425
P01000 | 55 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.77 | -7.22 | 41.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1678.1 | 69.4 | 2.64 | - | 123201 | 0 | 123201
P01001 | 62.5 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.72 | -7.88 | 45.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1950.4 | 101.7 | 2.4 | - | 129140 | 0 | 129140
P01002 | 62.5 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.83 | -6.58 | 38.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1730.1 | 74.7 | 2.47 | - | 117343 | 0 | 117343
P01003 | 62.5 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.51 | -5.06 | 31.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1482.5 | 50.9 | 2.57 | - | 102910 | 0 | 102910
P01004 | 62.5 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.31 | -3.27 | 25.4 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1201.9 | 31.1 | 2.76 | - | 85317 | 0 | 85317
P01005 | 62.5 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.35 | -1.4 | 20.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 914.8 | 17 | 3.02 | - | 66327 | 0 | 66327
P01006 | 62.5 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.84 | 0.66 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 602 | 7.2 | 3.47 | - | 44574 | 0 | 44574
P01007 | 62.5 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.53 | 2.73 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 20 | 286.4 | 1.3 | 4.56 | - | 21637 | 0 | 21637
P01008 | 62.5 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.28 | -6.89 | 40 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1780 | 80.3 | 2.45 | - | 120152 | 0 | 120152
P01009 | 70 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.07 | -7.43 | 42.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2080.3 | 117 | 2.26 | - | 125081 | 0 | 125081
P01010 | 70 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.37 | -6.28 | 37 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 1854.9 | 87.3 | 2.3 | - | 114514 | 0 | 114514
P01011 | 70 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.15 | -4.82 | 30.7 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1589.3 | 59.7 | 2.4 | - | 100651 | 0 | 100651
P01012 | 70 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.51 | -3.14 | 25 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1295.3 | 37 | 2.54 | - | 84066 | 0 | 84066
P01013 | 70 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.49 | -1.32 | 20.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 986 | 20.2 | 2.78 | - | 65489 | 0 | 65489
P01014 | 70 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.89 | 0.69 | 16 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 652 | 8.7 | 3.16 | - | 44311 | 0 | 44311
P01015 | 70 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.51 | 2.73 | 12.6 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 20 | 312.8 | 1.8 | 4.12 | - | 21722 | 0 | 21722
P01016 | 70 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -3.71 | -6.51 | 38.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 1899 | 92.6 | 2.3 | - | 116630 | 0 | 116630
P01017 | 56 | -20 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.32 | -8.32 | 47.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1862.3 | 90.6 | 2.57 | - | 132875 | 0 | 132875
P01018 | 56 | -15 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.17 | -6.81 | 39.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1637.3 | 65.8 | 2.61 | - | 119454 | 0 | 119454
P01019 | 56 | -10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -1.74 | -5.21 | 32.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1399.4 | 44.4 | 2.75 | - | 104323 | 0 | 104323
P01020 | 56 | -5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 1.19 | -3.34 | 25.6 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1130.6 | 26.9 | 2.95 | - | 86066 | 0 | 86066
P01021 | 56 | 0 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.29 | -1.44 | 20.5 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 859.8 | 14.6 | 3.25 | - | 66749 | 0 | 66749
P01022 | 56 | 5 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.82 | 0.65 | 16.1 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 564.5 | 6.2 | 3.77 | - | 44701 | 0 | 44701
P01023 | 56 | 10 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.56 | 2.75 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 20 | 265.8 | 1.1 | 5 | - | 21441 | 0 | 21441
P01024 | 56 | -16 | 15 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -4.64 | -7.14 | 41.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1685.1 | 70.7 | 2.6 | - | 122406 | 0 | 122406
P01025 | 25 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.01 | -8.09 | 46.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1706.2 | 66.8 | 3.32 | - | 160902 | 0 | 160902
P01026 | 25 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.8 | -6.57 | 38.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1501.1 | 47.3 | 3.52 | - | 143980 | 0 | 143980
P01027 | 25 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.26 | -4.89 | 31 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1276.7 | 31.4 | 3.79 | - | 124490 | 0 | 124490
P01028 | 25 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.75 | -2.99 | 24.6 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 1023.7 | 18.8 | 4.22 | - | 101425 | 0 | 101425
P01029 | 25 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.84 | -1.1 | 19.8 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 773.2 | 10.1 | 4.94 | - | 77783 | 0 | 77783
P01030 | 25 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.27 | 0.91 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 504.1 | 4.1 | 6.62 | - | 51491 | 0 | 51491
P01032 | 25 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.31 | -6.91 | 40.1 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1546.9 | 51.3 | 3.45 | - | 147873 | 0 | 147873
P01033 | 32.5 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -5.72 | -7.88 | 45.2 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1783.6 | 74.7 | 3.11 | - | 158667 | 0 | 158667
P01034 | 32.5 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.5 | -6.37 | 37.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1564.3 | 53.7 | 3.21 | - | 141679 | 0 | 141679
P01035 | 32.5 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.08 | -4.78 | 30.5 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1335.7 | 35.5 | 3.46 | - | 123101 | 0 | 123101
P01036 | 32.5 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.84 | -2.93 | 24.4 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 1074.7 | 21.5 | 3.75 | - | 100731 | 0 | 100731
P01037 | 32.5 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.87 | -1.09 | 19.7 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 814.4 | 11.6 | 4.25 | - | 77568 | 0 | 77568
P01038 | 32.5 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.21 | 0.87 | 15.7 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 537.1 | 4.9 | 5.17 | - | 51987 | 0 | 51987
P01039 | 32.5 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.79 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 20 | 250.2 | 0.9 | 6.99 | - | 24593 | 0 | 24593
P01040 | 32.5 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.09 | -6.76 | 39.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1619.7 | 57.9 | 3.2 | - | 146181 | 0 | 146181
P01041 | 40 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -5.37 | -7.64 | 43.9 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1868.4 | 84.1 | 2.9 | - | 155992 | 0 | 155992
P01042 | 40 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.27 | -6.21 | 36.7 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1643.8 | 60.9 | 2.99 | - | 139889 | 0 | 139889
P01043 | 40 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.82 | -4.61 | 29.9 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1397.1 | 40.6 | 3.16 | - | 121116 | 0 | 121116
P01044 | 40 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.98 | -2.85 | 24.2 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 1129.4 | 24.5 | 3.43 | - | 99683 | 0 | 99683
P01045 | 40 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.92 | -1.08 | 19.7 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 859.3 | 13.4 | 3.81 | - | 77148 | 0 | 77148
P01046 | 40 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.27 | 0.91 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 563.8 | 5.7 | 4.48 | - | 51491 | 0 | 51491
P01047 | 40 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.81 | 2.89 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 20 | 263.3 | 1 | 5.98 | - | 24441 | 0 | 24441
P01048 | 40 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.76 | -6.54 | 38.2 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1694.3 | 65 | 2.99 | - | 143642 | 0 | 143642
P01049 | 47.5 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.9 | -7.32 | 42.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 1956.5 | 93.9 | 2.75 | - | 152375 | 0 | 152375
P01050 | 47.5 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.92 | -5.98 | 35.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1726.1 | 68.7 | 2.8 | - | 137209 | 0 | 137209
P01051 | 47.5 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.62 | -4.48 | 29.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1474.8 | 46.6 | 2.93 | - | 119585 | 0 | 119585
P01052 | 47.5 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.01 | -2.83 | 24.1 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1203.1 | 28.7 | 3.15 | - | 99439 | 0 | 99439
P01053 | 47.5 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.99 | -1.01 | 19.6 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 910.2 | 15.5 | 3.47 | - | 76613 | 0 | 76613
P01054 | 47.5 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.27 | 0.91 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 600.7 | 6.6 | 4.02 | - | 51491 | 0 | 51491
P01055 | 47.5 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.79 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 20 | 281.9 | 1.2 | 5.31 | - | 24580 | 0 | 24580
P01056 | 47.5 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.44 | -6.32 | 37.2 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1783.3 | 73.7 | 2.81 | - | 141189 | 0 | 141189
P01057 | 55 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.42 | -6.99 | 40.5 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 2062.1 | 106 | 2.59 | - | 148732 | 0 | 148732
P01058 | 55 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.56 | -5.74 | 34.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1823 | 78.4 | 2.63 | - | 134418 | 0 | 134418
P01059 | 55 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.42 | -4.35 | 28.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1566.7 | 53.8 | 2.73 | - | 118015 | 0 | 118015
P01060 | 55 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.2 | -2.71 | 23.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1274.6 | 33.1 | 2.92 | - | 98014 | 0 | 98014
P01061 | 55 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.06 | -0.94 | 19.5 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 969.8 | 18.1 | 3.19 | - | 76047 | 0 | 76047
P01062 | 55 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.31 | 0.93 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 640.6 | 7.8 | 3.65 | - | 51224 | 0 | 51224
P01063 | 55 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.78 | 2.87 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 20 | 302.9 | 1.5 | 4.77 | - | 24674 | 0 | 24674
P01064 | 55 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.01 | -6.01 | 35.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1877.8 | 84 | 2.62 | - | 137862 | 0 | 137862
P01065 | 62.5 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.74 | -6.53 | 38.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2167.7 | 120 | 2.42 | - | 143525 | 0 | 143525
P01066 | 62.5 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.16 | -5.48 | 33.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 1937.4 | 90.2 | 2.46 | - | 131395 | 0 | 131395
P01067 | 62.5 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.16 | -4.16 | 28.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1671.5 | 62.6 | 2.55 | - | 116028 | 0 | 116028
P01068 | 62.5 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.35 | -2.65 | 23.6 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1364 | 38.9 | 2.7 | - | 96821 | 0 | 96821
P01069 | 62.5 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.1 | -0.95 | 19.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 1045.4 | 21.5 | 2.94 | - | 75792 | 0 | 75792
P01070 | 62.5 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.33 | 0.94 | 15.5 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 689 | 9.2 | 3.33 | - | 51021 | 0 | 51021
P01071 | 62.5 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.74 | 2.85 | 12.4 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 20 | 329.8 | 2.1 | 4.29 | - | 24912 | 0 | 24912
P01072 | 62.5 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.54 | -5.73 | 34.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 1990 | 96.4 | 2.45 | - | 134331 | 0 | 134331
P01073 | 70 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.07 | -6.07 | 36.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2300.7 | 136.9 | 2.27 | - | 138334 | 0 | 138334
P01074 | 70 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.69 | -5.17 | 32.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 2069.8 | 104.4 | 2.3 | - | 127783 | 0 | 127783
P01075 | 70 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 0.24 | -3.94 | 27.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1784.7 | 72.8 | 2.38 | - | 113024 | 0 | 113024
P01076 | 70 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.61 | -2.45 | 23.1 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1461.1 | 46 | 2.49 | - | 94823 | 0 | 94823
P01077 | 70 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.3 | -0.83 | 19.1 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 1117.5 | 25.4 | 2.69 | - | 74220 | 0 | 74220
P01078 | 70 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.38 | 0.97 | 15.5 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 745.4 | 11 | 3.04 | - | 50657 | 0 | 50657
P01079 | 70 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.79 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 20 | 353.5 | 2.7 | 3.87 | - | 24553 | 0 | 24553
P01080 | 70 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -1.96 | -5.35 | 32.9 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 2114.7 | 110.1 | 2.31 | - | 129879 | 0 | 129879
P01081 | 56 | -20 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.28 | -6.9 | 40 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 2069.7 | 108.1 | 2.55 | - | 147666 | 0 | 147666
P01082 | 56 | -15 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.49 | -5.69 | 34.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1835.4 | 79.7 | 2.6 | - | 133909 | 0 | 133909
P01083 | 56 | -10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -0.38 | -4.33 | 28.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1579.7 | 54.9 | 2.71 | - | 117764 | 0 | 117764
P01084 | 56 | -5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 2.21 | -2.7 | 23.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1285.7 | 33.8 | 2.89 | - | 97871 | 0 | 97871
P01085 | 56 | 0 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 5.08 | -0.92 | 19.4 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 978.4 | 18.4 | 3.16 | - | 75961 | 0 | 75961
P01086 | 56 | 5 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.31 | 0.93 | 15.6 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 646.6 | 7.9 | 3.6 | - | 51200 | 0 | 51200
P01087 | 56 | 10 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.76 | 2.86 | 12.4 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 20 | 307.8 | 1.6 | 4.69 | - | 24828 | 0 | 24828
P01088 | 56 | -16 | 15 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -2.93 | -5.98 | 35.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1889.7 | 85.5 | 2.59 | - | 137265 | 0 | 137265
P01089 | 25 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.39 | -6.97 | 40.3 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1876.2 | 78.1 | 3.34 | - | 176935 | 0 | 176935
P01090 | 25 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.3 | -5.57 | 33.8 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1646.3 | 56.2 | 3.46 | - | 157900 | 0 | 157900
P01091 | 25 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.02 | -4.07 | 27.9 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1401.4 | 37.4 | 3.72 | - | 136648 | 0 | 136648
P01092 | 25 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.63 | -2.44 | 23.1 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 1139 | 22.8 | 4.13 | - | 112850 | 0 | 112850
P01093 | 25 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.53 | -0.7 | 18.8 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 859.1 | 12.2 | 4.8 | - | 86418 | 0 | 86418
P01094 | 25 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.69 | 1.14 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 563.7 | 5 | 6.38 | - | 57582 | 0 | 57582
P01096 | 25 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.89 | -5.96 | 35.5 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1707.5 | 60.7 | 3.45 | - | 163223 | 0 | 163223
P01097 | 32.5 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.92 | -6.65 | 38.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1941.2 | 86.8 | 3.08 | - | 172691 | 0 | 172691
P01098 | 32.5 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.11 | -5.44 | 33.3 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1723.6 | 63.4 | 3.19 | - | 156104 | 0 | 156104
P01099 | 32.5 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.14 | -4 | 27.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1471.6 | 42.7 | 3.38 | - | 135629 | 0 | 135629
P01100 | 32.5 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.71 | -2.39 | 23 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 1196 | 26.1 | 3.67 | - | 112108 | 0 | 112108
P01101 | 32.5 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.59 | -0.66 | 18.8 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 901.4 | 13.9 | 4.14 | - | 85862 | 0 | 85862
P01102 | 32.5 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.63 | 1.11 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 600.6 | 6 | 4.97 | - | 58138 | 0 | 58138
P01103 | 32.5 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 12.01 | 3.01 | 12.1 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 20 | 277.8 | 1 | 6.57 | - | 27299 | 0 | 27299
P01104 | 32.5 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.64 | -5.79 | 34.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1783.5 | 68.2 | 3.18 | - | 160960 | 0 | 160960
P01105 | 40 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.61 | -6.44 | 37.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 2033.8 | 97.3 | 2.89 | - | 169798 | 0 | 169798
P01106 | 40 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.86 | -5.29 | 32.6 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1808.3 | 71.6 | 2.97 | - | 153889 | 0 | 153889
P01107 | 40 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.32 | -3.88 | 27.2 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1544.7 | 48.5 | 3.12 | - | 133917 | 0 | 133917
P01108 | 40 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.8 | -2.34 | 22.8 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 1261 | 29.9 | 3.36 | - | 111296 | 0 | 111296
P01109 | 40 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.61 | -0.65 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 954.1 | 16.1 | 3.73 | - | 85654 | 0 | 85654
P01110 | 40 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.64 | 1.12 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 634.9 | 7 | 4.36 | - | 57983 | 0 | 57983
P01111 | 40 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.99 | 2.99 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 20 | 295.7 | 1.3 | 5.68 | - | 27441 | 0 | 27441
P01112 | 40 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.27 | -5.55 | 33.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1858.6 | 76.7 | 2.95 | - | 157574 | 0 | 157574
P01113 | 47.5 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.26 | -6.2 | 36.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 2139.4 | 108.2 | 2.76 | - | 166618 | 0 | 166618
P01114 | 47.5 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.5 | -5.05 | 31.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1894.7 | 80.4 | 2.8 | - | 150609 | 0 | 150609
P01115 | 47.5 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.53 | -3.75 | 26.8 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1627.9 | 55.3 | 2.91 | - | 131996 | 0 | 131996
P01116 | 47.5 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.97 | -2.24 | 22.5 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1327.9 | 34.1 | 3.11 | - | 109760 | 0 | 109760
P01117 | 47.5 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.61 | -0.65 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 1017.7 | 18.9 | 3.4 | - | 85659 | 0 | 85659
P01118 | 47.5 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.66 | 1.13 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 674.2 | 8.1 | 3.92 | - | 57787 | 0 | 57787
P01119 | 47.5 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.96 | 2.96 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 20 | 317.8 | 1.7 | 5.03 | - | 27713 | 0 | 27713
P01120 | 47.5 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.98 | -5.36 | 32.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1956.7 | 86 | 2.81 | - | 154915 | 0 | 154915
P01121 | 55 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.69 | -5.82 | 34.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 2237.7 | 121.6 | 2.58 | - | 161394 | 0 | 161394
P01122 | 55 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.13 | -4.81 | 30.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1996.1 | 91.1 | 2.62 | - | 147183 | 0 | 147183
P01123 | 55 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.74 | -3.62 | 26.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1727.1 | 63.6 | 2.72 | - | 130103 | 0 | 130103
P01124 | 55 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.08 | -2.17 | 22.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1413.8 | 39.8 | 2.88 | - | 108719 | 0 | 108719
P01125 | 55 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.67 | -0.61 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 1085.4 | 22.1 | 3.13 | - | 85115 | 0 | 85115
P01126 | 55 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.75 | 1.18 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 712.9 | 9.4 | 3.53 | - | 57004 | 0 | 57004
P01127 | 55 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.95 | 2.95 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 20 | 341.7 | 2.2 | 4.53 | - | 27828 | 0 | 27828
P01128 | 55 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.48 | -5.04 | 31.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 2048.2 | 97.2 | 2.61 | - | 150371 | 0 | 150371
P01129 | 62.5 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.09 | -5.43 | 33.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2355.4 | 136.4 | 2.44 | - | 155956 | 0 | 155956
P01130 | 62.5 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.74 | -4.56 | 29.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 2117.7 | 104 | 2.47 | - | 143626 | 0 | 143626
P01131 | 62.5 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 1.03 | -3.44 | 25.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1836.5 | 73.6 | 2.54 | - | 127481 | 0 | 127481
P01132 | 62.5 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.28 | -2.05 | 22.1 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1506.6 | 46.4 | 2.67 | - | 106946 | 0 | 106946
P01133 | 62.5 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.83 | -0.52 | 18.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 1153.9 | 25.9 | 2.86 | - | 83655 | 0 | 83655
P01134 | 62.5 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.77 | 1.19 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 767.7 | 11.2 | 3.23 | - | 56844 | 0 | 56844
P01135 | 62.5 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 12 | 3 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 20 | 362.7 | 2.8 | 4.07 | - | 27399 | 0 | 27399
P01136 | 62.5 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.06 | -4.77 | 30.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 2171.5 | 110.9 | 2.45 | - | 146582 | 0 | 146582
P01137 | 70 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.45 | -5.02 | 31.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2496.2 | 154.4 | 2.3 | - | 150092 | 0 | 150092
P01138 | 70 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.19 | -4.19 | 28.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 2245.7 | 118.9 | 2.32 | - | 138642 | 0 | 138642
P01139 | 70 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 1.43 | -3.19 | 25.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1955.3 | 84.9 | 2.38 | - | 123830 | 0 | 123830
P01140 | 70 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.54 | -1.89 | 21.6 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1610.2 | 54.5 | 2.46 | - | 104504 | 0 | 104504
P01141 | 70 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.98 | -0.43 | 18.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 1238.7 | 30.5 | 2.64 | - | 82267 | 0 | 82267
P01142 | 70 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.81 | 1.22 | 15 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 830.1 | 13.3 | 2.96 | - | 56416 | 0 | 56416
P01143 | 70 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.97 | 2.97 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 20 | 398.2 | 3.4 | 3.68 | - | 27656 | 0 | 27656
P01144 | 70 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -0.5 | -4.41 | 29.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 2303 | 126.2 | 2.31 | - | 141446 | 0 | 141446
P01145 | 56 | -20 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.62 | -5.78 | 34.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 2253.8 | 123.5 | 2.56 | - | 160805 | 0 | 160805
P01146 | 56 | -15 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.08 | -4.78 | 30.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 2011.1 | 92.7 | 2.6 | - | 146725 | 0 | 146725
P01147 | 56 | -10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.77 | -3.6 | 26.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1741.5 | 64.8 | 2.7 | - | 129827 | 0 | 129827
P01148 | 56 | -5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 3.1 | -2.15 | 22.3 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1425.7 | 40.6 | 2.85 | - | 108525 | 0 | 108525
P01149 | 56 | 0 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.68 | -0.61 | 18.6 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 1095.3 | 22.6 | 3.09 | - | 85038 | 0 | 85038
P01150 | 56 | 5 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.75 | 1.18 | 15.1 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 719.6 | 9.6 | 3.49 | - | 56979 | 0 | 56979
P01151 | 56 | 10 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.95 | 2.95 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 20 | 345.1 | 2.3 | 4.47 | - | 27841 | 0 | 27841
P01152 | 56 | -16 | 15 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -1.44 | -5.01 | 31.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 2065.7 | 98.9 | 2.59 | - | 150049 | 0 | 150049
P01153 | 25 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3 | -6 | 35.9 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 2022.6 | 88.4 | 3.35 | - | 190744 | 0 | 190744
P01154 | 25 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.23 | -4.88 | 30.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1793 | 64.5 | 3.48 | - | 171972 | 0 | 171972
P01155 | 25 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.92 | -3.51 | 26.1 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1529.2 | 43.8 | 3.68 | - | 149108 | 0 | 149108
P01156 | 25 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.4 | -1.97 | 21.9 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 1239.6 | 26.6 | 4.07 | - | 122819 | 0 | 122819
P01157 | 25 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.13 | -0.34 | 18.1 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 933.6 | 14.1 | 4.73 | - | 93916 | 0 | 93916
P01158 | 25 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.05 | 1.35 | 14.8 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 617 | 5.9 | 6.22 | - | 63019 | 0 | 63019
P01160 | 25 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.63 | -5.14 | 32 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1843.1 | 69.2 | 3.44 | - | 176188 | 0 | 176188
P01161 | 32.5 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -2.71 | -5.84 | 35 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 2109.5 | 98.2 | 3.12 | - | 187657 | 0 | 187657
P01162 | 32.5 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.01 | -4.73 | 30.4 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1872.2 | 72.3 | 3.21 | - | 169564 | 0 | 169564
P01163 | 32.5 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.14 | -3.37 | 25.7 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1592.7 | 49 | 3.36 | - | 146791 | 0 | 146791
P01164 | 32.5 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.49 | -1.92 | 21.7 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 1300.9 | 30.4 | 3.62 | - | 121936 | 0 | 121936
P01165 | 32.5 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.19 | -0.3 | 18 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 979.5 | 16.1 | 4.09 | - | 93297 | 0 | 93297
P01166 | 32.5 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 8.96 | 1.3 | 14.9 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 660.6 | 7.2 | 4.82 | - | 63946 | 0 | 63946
P01167 | 32.5 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.15 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 20 | 307.5 | 1.4 | 6.31 | - | 30218 | 0 | 30218
P01168 | 32.5 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.31 | -4.93 | 31.1 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1914.8 | 77.4 | 3.17 | - | 172812 | 0 | 172812
P01169 | 40 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -2.35 | -5.6 | 34 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 2201.4 | 109.4 | 2.92 | - | 183798 | 0 | 183798
P01170 | 40 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.65 | -4.5 | 29.5 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1947.9 | 81.1 | 2.97 | - | 165766 | 0 | 165766
P01171 | 40 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.23 | -3.31 | 25.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1682.2 | 56.2 | 3.1 | - | 145831 | 0 | 145831
P01172 | 40 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.55 | -1.88 | 21.6 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 1373.9 | 34.8 | 3.32 | - | 121262 | 0 | 121262
P01173 | 40 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.13 | -0.34 | 18.1 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 1046.8 | 19 | 3.67 | - | 93980 | 0 | 93980
P01174 | 40 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.07 | 1.36 | 14.8 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 688.1 | 8.1 | 4.2 | - | 62837 | 0 | 62837
P01175 | 40 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.13 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 20 | 327 | 1.8 | 5.45 | - | 30347 | 0 | 30347
P01176 | 40 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.02 | -4.74 | 30.4 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 2001.7 | 86.8 | 2.95 | - | 169701 | 0 | 169701
P01177 | 47.5 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.87 | -5.29 | 32.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 2294.6 | 120.8 | 2.77 | - | 178705 | 0 | 178705
P01178 | 47.5 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.36 | -4.36 | 28.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 2046.8 | 91.4 | 2.79 | - | 162700 | 0 | 162700
P01179 | 47.5 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.51 | -3.14 | 25 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1761.8 | 63.4 | 2.89 | - | 142853 | 0 | 142853
P01180 | 47.5 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.69 | -1.8 | 21.4 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1449.4 | 40 | 3.06 | - | 119800 | 0 | 119800
P01181 | 47.5 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.19 | -0.31 | 18 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 1108.9 | 22 | 3.34 | - | 93339 | 0 | 93339
P01182 | 47.5 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.09 | 1.37 | 14.8 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 730.1 | 9.4 | 3.79 | - | 62586 | 0 | 62586
P01183 | 47.5 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.13 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 20 | 348 | 2.3 | 4.86 | - | 30347 | 0 | 30347
P01184 | 47.5 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.64 | -4.49 | 29.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 2092.5 | 96.8 | 2.79 | - | 165664 | 0 | 165664
P01185 | 55 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.28 | -4.91 | 31.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 2391.6 | 134.9 | 2.59 | - | 172499 | 0 | 172499
P01186 | 55 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.05 | -4.06 | 27.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 2147.7 | 102.5 | 2.64 | - | 158361 | 0 | 158361
P01187 | 55 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.77 | -2.98 | 24.5 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1860.1 | 72.3 | 2.71 | - | 140121 | 0 | 140121
P01188 | 55 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.83 | -1.71 | 21.2 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1538 | 46.2 | 2.85 | - | 118271 | 0 | 118271
P01189 | 55 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.34 | -0.22 | 17.8 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 1169.8 | 25.5 | 3.05 | - | 91729 | 0 | 91729
P01190 | 55 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.12 | 1.39 | 14.7 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 778.7 | 11 | 3.46 | - | 62271 | 0 | 62271
P01191 | 55 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.16 | 3.08 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 20 | 369.8 | 2.8 | 4.31 | - | 30121 | 0 | 30121
P01192 | 55 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.28 | -4.28 | 28.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 2204.1 | 109.5 | 2.61 | - | 161816 | 0 | 161816
P01193 | 62.5 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.72 | -4.55 | 29.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2515.8 | 151.1 | 2.44 | - | 166578 | 0 | 166578
P01194 | 62.5 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.44 | -3.81 | 27 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 2273.3 | 116.8 | 2.47 | - | 154183 | 0 | 154183
P01195 | 62.5 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 2.05 | -2.8 | 24.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1976.2 | 83.2 | 2.54 | - | 137178 | 0 | 137178
P01196 | 62.5 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 4 | -1.61 | 21 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1641.1 | 53.9 | 2.65 | - | 116491 | 0 | 116491
P01197 | 62.5 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.4 | -0.18 | 17.7 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 1256.2 | 30.2 | 2.81 | - | 91073 | 0 | 91073
P01198 | 62.5 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.16 | 1.41 | 14.7 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 835.5 | 13 | 3.16 | - | 61869 | 0 | 61869
P01199 | 62.5 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.14 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 20 | 400.8 | 3.3 | 3.91 | - | 30277 | 0 | 30277
P01200 | 62.5 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.15 | -4 | 27.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 2330.7 | 124.1 | 2.46 | - | 157330 | 0 | 157330
P01201 | 70 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.09 | -4.14 | 28.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2658.8 | 169.7 | 2.32 | - | 159869 | 0 | 159869
P01202 | 70 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.99 | -3.47 | 26 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 2404.2 | 132.1 | 2.34 | - | 148431 | 0 | 148431
P01203 | 70 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 2.39 | -2.61 | 23.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 2109.8 | 96.5 | 2.37 | - | 133615 | 0 | 133615
P01204 | 70 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 4.29 | -1.43 | 20.5 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1747.6 | 62.5 | 2.47 | - | 113420 | 0 | 113420
P01205 | 70 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.53 | -0.11 | 17.6 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 1351 | 35.7 | 2.6 | - | 89726 | 0 | 89726
P01206 | 70 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.26 | 1.47 | 14.6 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 893.6 | 15.3 | 2.87 | - | 60734 | 0 | 60734
P01207 | 70 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.13 | 3.07 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 20 | 437 | 4 | 3.55 | - | 30347 | 0 | 30347
P01208 | 70 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.73 | -3.63 | 26.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 2461.2 | 139.8 | 2.33 | - | 151158 | 0 | 151158
P01209 | 56 | -20 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.22 | -4.87 | 30.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 2408.7 | 137 | 2.57 | - | 171860 | 0 | 171860
P01210 | 56 | -15 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | 0.1 | -4.02 | 27.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 2163 | 104.2 | 2.61 | - | 157806 | 0 | 157806
P01211 | 56 | -10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.8 | -2.96 | 24.5 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1874.9 | 73.6 | 2.68 | - | 139775 | 0 | 139775
P01212 | 56 | -5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.85 | -1.7 | 21.2 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1550.7 | 47.1 | 2.82 | - | 118040 | 0 | 118040
P01213 | 56 | 0 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.34 | -0.22 | 17.8 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 1181.5 | 26.1 | 3.02 | - | 91729 | 0 | 91729
P01214 | 56 | 5 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.12 | 1.39 | 14.7 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 785.8 | 11.2 | 3.42 | - | 62223 | 0 | 62223
P01215 | 56 | 10 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.15 | 3.08 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 20 | 373.5 | 2.9 | 4.25 | - | 30133 | 0 | 30133
P01216 | 56 | -16 | 15 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.22 | -4.22 | 28.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 2220.1 | 111.3 | 2.59 | - | 161262 | 0 | 161262
P01217 | 25 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -1.86 | -5.28 | 32.6 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 2148.8 | 97.4 | 3.37 | - | 202647 | 0 | 202647
P01218 | 25 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.32 | -4.32 | 28.7 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1919.7 | 72.4 | 3.47 | - | 184126 | 0 | 184126
P01219 | 25 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.67 | -3.04 | 24.7 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1643 | 49.1 | 3.7 | - | 160207 | 0 | 160207
P01220 | 25 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.04 | -1.59 | 20.9 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 1329.3 | 30.1 | 4.04 | - | 131704 | 0 | 131704
P01221 | 25 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.49 | -0.13 | 17.6 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 1016.9 | 16.5 | 4.66 | - | 102291 | 0 | 102291
P01222 | 25 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.32 | 1.51 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 667.5 | 6.9 | 6.07 | - | 68182 | 0 | 68182
P01224 | 25 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.62 | -4.48 | 29.4 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1963.9 | 76.9 | 3.46 | - | 187740 | 0 | 187740
P01225 | 32.5 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -1.53 | -5.07 | 31.7 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 2233.8 | 107.6 | 3.14 | - | 198716 | 0 | 198716
P01226 | 32.5 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.09 | -4.14 | 28.1 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 2002.3 | 80.9 | 3.21 | - | 181350 | 0 | 181350
P01227 | 32.5 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.9 | -2.89 | 24.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1707.4 | 55.4 | 3.34 | - | 157356 | 0 | 157356
P01228 | 32.5 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.12 | -1.54 | 20.8 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 1394.6 | 34.3 | 3.61 | - | 130722 | 0 | 130722
P01229 | 32.5 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.52 | -0.11 | 17.6 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 1069.7 | 19 | 4 | - | 101888 | 0 | 101888
P01230 | 32.5 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.33 | 1.51 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 703.8 | 8.1 | 4.66 | - | 68122 | 0 | 68122
P01231 | 32.5 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.29 | 3.15 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 20 | 331 | 1.8 | 6.14 | - | 32535 | 0 | 32535
P01232 | 32.5 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.36 | -4.36 | 28.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 2045.9 | 85.6 | 3.2 | - | 184643 | 0 | 184643
P01233 | 40 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -1.04 | -4.75 | 30.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 2309.1 | 118.7 | 2.92 | - | 192783 | 0 | 192783
P01234 | 40 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.25 | -3.93 | 27.4 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 2083.3 | 89.6 | 3.01 | - | 177285 | 0 | 177285
P01235 | 40 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.09 | -2.78 | 24 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1790.1 | 62.6 | 3.09 | - | 155189 | 0 | 155189
P01236 | 40 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.22 | -1.48 | 20.6 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 1467 | 39.1 | 3.3 | - | 129480 | 0 | 129480
P01237 | 40 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.56 | -0.08 | 17.5 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 1128.8 | 21.8 | 3.6 | - | 101343 | 0 | 101343
P01238 | 40 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.36 | 1.53 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 742 | 9.3 | 4.1 | - | 67766 | 0 | 67766
P01239 | 40 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.28 | 3.15 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 20 | 352.1 | 2.3 | 5.3 | - | 32684 | 0 | 32684
P01240 | 40 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.05 | -4.12 | 28 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 2133.2 | 95.4 | 2.99 | - | 180850 | 0 | 180850
P01241 | 47.5 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.67 | -4.52 | 29.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 2418.4 | 132.4 | 2.75 | - | 188344 | 0 | 188344
P01242 | 47.5 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.67 | -3.67 | 26.6 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 2166.2 | 100.1 | 2.8 | - | 172195 | 0 | 172195
P01243 | 47.5 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.28 | -2.66 | 23.7 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1884.3 | 71.1 | 2.88 | - | 152789 | 0 | 152789
P01244 | 47.5 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.35 | -1.4 | 20.4 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1548.5 | 44.9 | 3.05 | - | 127989 | 0 | 127989
P01245 | 47.5 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.67 | -0.02 | 17.4 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 1188.7 | 24.9 | 3.31 | - | 100053 | 0 | 100053
P01246 | 47.5 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.38 | 1.54 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 787 | 10.8 | 3.7 | - | 67457 | 0 | 67457
P01247 | 47.5 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.27 | 3.14 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 20 | 376.5 | 2.7 | 4.71 | - | 32837 | 0 | 32837
P01248 | 47.5 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.38 | -3.85 | 27.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 2219.3 | 106.4 | 2.79 | - | 175704 | 0 | 175704
P01249 | 55 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.2 | -4.2 | 28.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 2532.8 | 146.8 | 2.61 | - | 182677 | 0 | 182677
P01250 | 55 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.04 | -3.44 | 25.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 2275.8 | 112.5 | 2.64 | - | 167807 | 0 | 167807
P01251 | 55 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.58 | -2.47 | 23.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1980.7 | 80.3 | 2.71 | - | 149203 | 0 | 149203
P01252 | 55 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.52 | -1.29 | 20.2 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1636.9 | 51.5 | 2.84 | - | 125879 | 0 | 125879
P01253 | 55 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.75 | 0.02 | 17.3 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 1264.2 | 29 | 3.05 | - | 99132 | 0 | 99132
P01254 | 55 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.42 | 1.56 | 14.4 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 838.8 | 12.6 | 3.38 | - | 67070 | 0 | 67070
P01255 | 55 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.3 | 3.16 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 20 | 398.8 | 3.2 | 4.2 | - | 32479 | 0 | 32479
P01256 | 55 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.78 | -3.6 | 26.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 2327.8 | 119.2 | 2.63 | - | 170900 | 0 | 170900
P01257 | 62.5 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.38 | -3.85 | 27.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2653.8 | 163.1 | 2.48 | - | 175713 | 0 | 175713
P01258 | 62.5 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.48 | -3.16 | 25.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 2396.2 | 126.9 | 2.48 | - | 162517 | 0 | 162517
P01259 | 62.5 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.9 | -2.28 | 22.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 2094.5 | 91.7 | 2.54 | - | 145387 | 0 | 145387
P01260 | 62.5 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.69 | -1.2 | 20 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1745.5 | 59.9 | 2.64 | - | 123904 | 0 | 123904
P01261 | 62.5 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.9 | 0.12 | 17.1 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 1341.4 | 33.8 | 2.8 | - | 97253 | 0 | 97253
P01262 | 62.5 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.46 | 1.58 | 14.4 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 899 | 14.8 | 3.11 | - | 66574 | 0 | 66574
P01263 | 62.5 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.28 | 3.15 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 20 | 432 | 3.8 | 3.81 | - | 32628 | 0 | 32628
P01264 | 62.5 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.2 | -3.34 | 25.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 2457.4 | 134.9 | 2.47 | - | 165878 | 0 | 165878
P01265 | 70 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.97 | -3.48 | 26 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2803.4 | 183.5 | 2.33 | - | 168560 | 0 | 168560
P01266 | 70 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.98 | -2.85 | 24.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 2534.4 | 143.5 | 2.35 | - | 156466 | 0 | 156466
P01267 | 70 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 3.25 | -2.07 | 22.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 2230.2 | 105.7 | 2.37 | - | 141239 | 0 | 141239
P01268 | 70 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.91 | -1.09 | 19.7 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1868.4 | 70.1 | 2.46 | - | 121259 | 0 | 121259
P01269 | 70 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 7.03 | 0.19 | 17 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 1441.2 | 40 | 2.58 | - | 95721 | 0 | 95721
P01270 | 70 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.54 | 1.63 | 14.3 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 964.8 | 17.4 | 2.87 | - | 65574 | 0 | 65574
P01271 | 70 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.28 | 3.14 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 20 | 471 | 4.5 | 3.46 | - | 32712 | 0 | 32712
P01272 | 70 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.75 | -2.99 | 24.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 2593.1 | 151.5 | 2.35 | - | 159257 | 0 | 159257
P01273 | 56 | -20 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.07 | -4.13 | 28.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 2539.1 | 148.1 | 2.59 | - | 181159 | 0 | 181159
P01274 | 56 | -15 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 1.09 | -3.4 | 25.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 2291.5 | 114.3 | 2.62 | - | 167184 | 0 | 167184
P01275 | 56 | -10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 2.62 | -2.45 | 23.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1995.4 | 81.7 | 2.69 | - | 148756 | 0 | 148756
P01276 | 56 | -5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.52 | -1.29 | 20.2 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1653.7 | 52.7 | 2.81 | - | 125879 | 0 | 125879
P01277 | 56 | 0 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.76 | 0.03 | 17.3 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 1275.1 | 29.6 | 3.02 | - | 98996 | 0 | 98996
P01278 | 56 | 5 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.42 | 1.56 | 14.4 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 846.3 | 12.9 | 3.35 | - | 67011 | 0 | 67011
P01279 | 56 | 10 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.29 | 3.15 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 20 | 402.9 | 3.2 | 4.14 | - | 32499 | 0 | 32499
P01280 | 56 | -16 | 15 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | 0.85 | -3.56 | 26.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 2341.5 | 121 | 2.61 | - | 170080 | 0 | 170080
P01281 | 25 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.15 | -7.49 | 43 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 1807.1 | 73.6 | 3.32 | - | 170420 | 0 | 170420
P01282 | 25 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.09 | -6.09 | 36.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 1595 | 52.8 | 3.49 | - | 152989 | 0 | 152989
P01283 | 25 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.53 | -4.43 | 29.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 1347.2 | 34.9 | 3.74 | - | 131366 | 0 | 131366
P01284 | 25 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.29 | -2.65 | 23.7 | R290 (Propane) | Countercurrent | -5 | 0 | 25 | 20 | 1084.6 | 20.8 | 4.18 | - | 107456 | 0 | 107456
P01285 | 25 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.24 | -0.86 | 19.2 | R290 (Propane) | Countercurrent | 0 | 0 | 25 | 20 | 820.1 | 11.2 | 4.86 | - | 82492 | 0 | 82492
P01286 | 25 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.51 | 1.04 | 15.4 | R290 (Propane) | Countercurrent | 5 | 0 | 25 | 20 | 537.1 | 4.6 | 6.5 | - | 54860 | 0 | 54860
P01288 | 25 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.45 | -6.33 | 37.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 1632.5 | 56.3 | 3.45 | - | 156054 | 0 | 156054
P01289 | 32.5 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -4.76 | -7.22 | 41.6 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 1879.2 | 81.5 | 3.11 | - | 167175 | 0 | 167175
P01290 | 32.5 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.77 | -5.88 | 35.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 1659.4 | 58.9 | 3.22 | - | 150293 | 0 | 150293
P01291 | 32.5 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.37 | -4.32 | 28.8 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 1410.5 | 39.6 | 3.39 | - | 129994 | 0 | 129994
P01292 | 32.5 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.37 | -2.63 | 23.5 | R290 (Propane) | Countercurrent | -5 | 0 | 32.5 | 20 | 1139.2 | 23.9 | 3.71 | - | 106779 | 0 | 106779
P01293 | 32.5 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.29 | -0.84 | 19.2 | R290 (Propane) | Countercurrent | 0 | 0 | 32.5 | 20 | 862.2 | 12.9 | 4.19 | - | 82127 | 0 | 82127
P01294 | 32.5 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.42 | 0.99 | 15.4 | R290 (Propane) | Countercurrent | 5 | 0 | 32.5 | 20 | 574.6 | 5.6 | 5.05 | - | 55622 | 0 | 55622
P01295 | 32.5 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.92 | 2.92 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 32.5 | 20 | 265.2 | 1 | 6.69 | - | 26069 | 0 | 26069
P01296 | 32.5 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.21 | -6.21 | 36.5 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 1706.7 | 63.3 | 3.19 | - | 154030 | 0 | 154030
P01297 | 40 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -4.39 | -6.97 | 40.4 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 1964.7 | 90.9 | 2.93 | - | 164036 | 0 | 164036
P01298 | 40 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.52 | -5.71 | 34.4 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 1740.8 | 66.5 | 3.01 | - | 148143 | 0 | 148143
P01299 | 40 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.21 | -4.21 | 28.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 1483.9 | 45.1 | 3.13 | - | 128640 | 0 | 128640
P01300 | 40 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.45 | -2.55 | 23.4 | R290 (Propane) | Countercurrent | -5 | 0 | 40 | 20 | 1202.5 | 27.5 | 3.38 | - | 106135 | 0 | 106135
P01301 | 40 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.34 | -0.81 | 19.1 | R290 (Propane) | Countercurrent | 0 | 0 | 40 | 20 | 909.8 | 14.8 | 3.76 | - | 81683 | 0 | 81683
P01302 | 40 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.44 | 1 | 15.4 | R290 (Propane) | Countercurrent | 5 | 0 | 40 | 20 | 607.6 | 6.4 | 4.42 | - | 55487 | 0 | 55487
P01303 | 40 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.9 | 2.94 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 40 | 20 | 282.7 | 1.2 | 5.79 | - | 26236 | 0 | 26236
P01304 | 40 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.87 | -5.95 | 35.5 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 1783.1 | 71.4 | 2.96 | - | 151174 | 0 | 151174
P01305 | 47.5 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.9 | -6.63 | 38.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 2052.5 | 102.2 | 2.73 | - | 159849 | 0 | 159849
P01306 | 47.5 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.13 | -5.46 | 33.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 1823.1 | 75.4 | 2.79 | - | 144922 | 0 | 144922
P01307 | 47.5 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.03 | -4.11 | 28 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 1567.7 | 51.8 | 2.92 | - | 127112 | 0 | 127112
P01308 | 47.5 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.53 | -2.47 | 23.2 | R290 (Propane) | Countercurrent | -5 | 0 | 47.5 | 20 | 1275.4 | 31.8 | 3.12 | - | 105414 | 0 | 105414
P01309 | 47.5 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.4 | -0.77 | 19 | R290 (Propane) | Countercurrent | 0 | 0 | 47.5 | 20 | 964.2 | 17.1 | 3.44 | - | 81153 | 0 | 81153
P01310 | 47.5 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.54 | 1.06 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 47.5 | 20 | 637 | 7.4 | 3.95 | - | 54599 | 0 | 54599
P01311 | 47.5 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.93 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 47.5 | 20 | 301.8 | 1.5 | 5.14 | - | 26315 | 0 | 26315
P01312 | 47.5 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.55 | -5.73 | 34.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 1874.6 | 80.9 | 2.77 | - | 148413 | 0 | 148413
P01313 | 55 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.38 | -6.28 | 37 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 2155.3 | 114.5 | 2.58 | - | 155452 | 0 | 155452
P01314 | 55 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.8 | -5.25 | 32.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 1927.3 | 86 | 2.62 | - | 142111 | 0 | 142111
P01315 | 55 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.28 | -3.91 | 27.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 1653.1 | 59.1 | 2.72 | - | 124524 | 0 | 124524
P01316 | 55 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.66 | -2.43 | 23 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 20 | 1356.9 | 37 | 2.9 | - | 104343 | 0 | 104343
P01317 | 55 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.42 | -0.76 | 19 | R290 (Propane) | Countercurrent | 0 | 0 | 55 | 20 | 1033.1 | 20.2 | 3.16 | - | 81012 | 0 | 81012
P01318 | 55 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.57 | 1.07 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 55 | 20 | 680.1 | 8.6 | 3.59 | - | 54385 | 0 | 54385
P01319 | 55 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.88 | 2.93 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 55 | 20 | 324.1 | 1.9 | 4.63 | - | 26400 | 0 | 26400
P01320 | 55 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.12 | -5.45 | 33.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 1971.8 | 91.2 | 2.62 | - | 144760 | 0 | 144760
P01321 | 62.5 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.84 | -5.92 | 35.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 2278.7 | 129.7 | 2.43 | - | 150877 | 0 | 150877
P01322 | 62.5 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.33 | -4.94 | 31.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 2036.6 | 97.7 | 2.47 | - | 138126 | 0 | 138126
P01323 | 62.5 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.56 | -3.73 | 26.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 1758.7 | 68.3 | 2.54 | - | 122079 | 0 | 122079
P01324 | 62.5 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.84 | -2.31 | 22.7 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 20 | 1448.2 | 43.2 | 2.68 | - | 102799 | 0 | 102799
P01325 | 62.5 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.5 | -0.71 | 18.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 20 | 1108.2 | 23.9 | 2.91 | - | 80342 | 0 | 80342
P01326 | 62.5 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.6 | 1.09 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 62.5 | 20 | 730.7 | 10.2 | 3.28 | - | 54111 | 0 | 54111
P01327 | 62.5 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.9 | 2.94 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 62.5 | 20 | 347.2 | 2.4 | 4.14 | - | 26228 | 0 | 26228
P01328 | 62.5 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.64 | -5.14 | 32 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 2084.7 | 103.9 | 2.45 | - | 140720 | 0 | 140720
P01329 | 70 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.15 | -5.47 | 33.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 2411.8 | 146.7 | 2.29 | - | 145014 | 0 | 145014
P01330 | 70 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -0.83 | -4.61 | 29.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 2168 | 112.3 | 2.31 | - | 133845 | 0 | 133845
P01331 | 70 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.89 | -3.53 | 26.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 1884.6 | 79.9 | 2.37 | - | 119349 | 0 | 119349
P01332 | 70 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 3.08 | -2.17 | 22.4 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 20 | 1552.4 | 50.8 | 2.49 | - | 100748 | 0 | 100748
P01333 | 70 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.65 | -0.62 | 18.7 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 20 | 1189.9 | 28.5 | 2.65 | - | 79028 | 0 | 79028
P01334 | 70 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.65 | 1.12 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 20 | 790.3 | 12.2 | 3 | - | 53712 | 0 | 53712
P01335 | 70 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.93 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 20 | 378.9 | 3.1 | 3.75 | - | 26315 | 0 | 26315
P01336 | 70 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.12 | -4.8 | 30.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 2219.7 | 119 | 2.31 | - | 136327 | 0 | 136327
P01337 | 56 | -20 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.29 | -6.23 | 36.8 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 2168.7 | 116.5 | 2.55 | - | 154733 | 0 | 154733
P01338 | 56 | -15 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -1.75 | -5.21 | 32.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 1942.2 | 87.5 | 2.6 | - | 141696 | 0 | 141696
P01339 | 56 | -10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 0.31 | -3.89 | 27.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 1666.2 | 60.2 | 2.7 | - | 124217 | 0 | 124217
P01340 | 56 | -5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.7 | -2.4 | 23 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 20 | 1366.6 | 37.7 | 2.86 | - | 104030 | 0 | 104030
P01341 | 56 | 0 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.43 | -0.75 | 19 | R290 (Propane) | Countercurrent | 0 | 0 | 56 | 20 | 1042.5 | 20.6 | 3.12 | - | 80933 | 0 | 80933
P01342 | 56 | 5 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.57 | 1.08 | 15.3 | R290 (Propane) | Countercurrent | 5 | 0 | 56 | 20 | 686.4 | 8.8 | 3.55 | - | 54352 | 0 | 54352
P01343 | 56 | 10 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.89 | 2.94 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 56 | 20 | 325 | 1.9 | 4.57 | - | 26267 | 0 | 26267
P01344 | 56 | -16 | 15 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.06 | -5.41 | 33.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 1986.5 | 92.8 | 2.59 | - | 144293 | 0 | 144293
P01345 | 25 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.55 | -17.29 | 21.5 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 612.6 | 12.9 | 3.31 | - | 57769 | 0 | 57769
P01346 | 25 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.36 | -14.07 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 377.4 | 3.8 | 3.82 | - | 36200 | 0 | 36200
P01347 | 25 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.71 | -11.82 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 118.2 | 0.8 | 5.76 | - | 11527 | 0 | 11527
P01348 | 25 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13.02 | -14.72 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 424.9 | 5.5 | 3.66 | - | 40615 | 0 | 40615
P01349 | 32.5 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.48 | -17.22 | 21.4 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 644.1 | 14.6 | 3.06 | - | 57297 | 0 | 57297
P01350 | 32.5 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.28 | -13.98 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 393.4 | 4.6 | 3.44 | - | 35628 | 0 | 35628
P01351 | 32.5 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.67 | -11.79 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 122.5 | 0.8 | 5.18 | - | 11290 | 0 | 11290
P01352 | 32.5 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.98 | -14.68 | 17 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 447.3 | 6.7 | 3.37 | - | 40373 | 0 | 40373
P01353 | 40 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.37 | -17.1 | 21.2 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 676.7 | 16.5 | 2.86 | - | 56496 | 0 | 56496
P01354 | 40 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.23 | -13.94 | 15.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 414.9 | 5.6 | 3.19 | - | 35306 | 0 | 35306
P01355 | 40 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.7 | -11.81 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 132.5 | 0.9 | 4.69 | - | 11487 | 0 | 11487
P01356 | 40 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.94 | -14.64 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 472.9 | 8.1 | 3.11 | - | 40093 | 0 | 40093
P01357 | 47.5 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.17 | -16.9 | 20.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 708.6 | 18.8 | 2.63 | - | 55188 | 0 | 55188
P01358 | 47.5 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.19 | -13.9 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 440.9 | 6.9 | 2.95 | - | 35044 | 0 | 35044
P01359 | 47.5 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.67 | -11.79 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 139.1 | 1 | 4.25 | - | 11278 | 0 | 11278
P01360 | 47.5 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.82 | -14.52 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 496 | 9.3 | 2.85 | - | 39271 | 0 | 39271
P01361 | 55 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.06 | -16.79 | 20.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 754.8 | 21.6 | 2.45 | - | 54440 | 0 | 54440
P01362 | 55 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.15 | -13.86 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 471.8 | 8.6 | 2.72 | - | 34790 | 0 | 34790
P01363 | 55 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.7 | -11.81 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 152.4 | 1.2 | 3.86 | - | 11479 | 0 | 11479
P01364 | 55 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.77 | -14.47 | 16.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 530.2 | 10.7 | 2.64 | - | 38924 | 0 | 38924
P01365 | 62.5 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.91 | -16.63 | 20.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 806.7 | 25.1 | 2.28 | - | 53412 | 0 | 53412
P01366 | 62.5 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.11 | -13.82 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 508.5 | 10.1 | 2.51 | - | 34489 | 0 | 34489
P01367 | 62.5 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.67 | -11.78 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 162.4 | 1.3 | 3.49 | - | 11270 | 0 | 11270
P01368 | 62.5 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.7 | -14.4 | 16.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 569.8 | 12.6 | 2.44 | - | 38462 | 0 | 38462
P01369 | 70 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -14.69 | -16.41 | 19.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 864 | 29.2 | 2.12 | - | 51951 | 0 | 51951
P01370 | 70 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -11.98 | -15.49 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 545 | 11.8 | 2.28 | - | 33646 | 0 | 33646
P01371 | 70 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.65 | -11.77 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 175.8 | 1.5 | 3.14 | - | 11135 | 0 | 11135
P01372 | 70 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.55 | -14.25 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 610.1 | 14.7 | 2.21 | - | 37472 | 0 | 37472
P01373 | 56 | -20 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.05 | -16.77 | 20.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 761.5 | 22.1 | 2.43 | - | 54331 | 0 | 54331
P01374 | 56 | -15 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.15 | -13.85 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 476.4 | 8.7 | 2.7 | - | 34756 | 0 | 34756
P01375 | 56 | -10 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.7 | -11.81 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 154.2 | 1.2 | 3.81 | - | 11495 | 0 | 11495
P01376 | 56 | -16 | -7 | 18194.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.76 | -14.46 | 16.7 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 535.1 | 11 | 2.61 | - | 38869 | 0 | 38869
P01377 | 25 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.86 | -16.58 | 20.2 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 691.8 | 16 | 3.21 | - | 65239 | 0 | 65239
P01378 | 25 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.9 | -15.34 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 423.3 | 5.5 | 3.61 | - | 40600 | 0 | 40600
P01379 | 25 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.58 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 134.2 | 0.9 | 5.4 | - | 13087 | 0 | 13087
P01380 | 25 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.56 | -14.26 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 482.4 | 7.9 | 3.53 | - | 46118 | 0 | 46118
P01381 | 32.5 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.78 | -16.5 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 725.9 | 18 | 2.99 | - | 64578 | 0 | 64578
P01382 | 32.5 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.85 | -15.26 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 443.8 | 6.6 | 3.32 | - | 40195 | 0 | 40195
P01383 | 32.5 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.6 | -11.72 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 143.8 | 1 | 4.87 | - | 13254 | 0 | 13254
P01384 | 32.5 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.53 | -14.23 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 508.1 | 8.9 | 3.25 | - | 45855 | 0 | 45855
P01385 | 40 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.57 | -16.29 | 19.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 752.6 | 20.1 | 2.76 | - | 62836 | 0 | 62836
P01386 | 40 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.81 | -15.21 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 468.9 | 8 | 3.08 | - | 39907 | 0 | 39907
P01387 | 40 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.58 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 150.7 | 1.1 | 4.39 | - | 13064 | 0 | 13064
P01388 | 40 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.4 | -14.1 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 528.2 | 10 | 2.97 | - | 44780 | 0 | 44780
P01389 | 47.5 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.46 | -16.17 | 19.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 794.2 | 22.8 | 2.58 | - | 61856 | 0 | 61856
P01390 | 47.5 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.81 | -15.2 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 501.8 | 9.2 | 2.84 | - | 39893 | 0 | 39893
P01391 | 47.5 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.6 | -11.72 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 163.1 | 1.2 | 4 | - | 13227 | 0 | 13227
P01392 | 47.5 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.35 | -14.05 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 560.4 | 11.4 | 2.76 | - | 44371 | 0 | 44371
P01393 | 55 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.33 | -16.05 | 19.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 843.7 | 26.2 | 2.4 | - | 60850 | 0 | 60850
P01394 | 55 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.75 | -15.11 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 533.9 | 10.6 | 2.63 | - | 39369 | 0 | 39369
P01395 | 55 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.57 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 172.8 | 1.4 | 3.62 | - | 13014 | 0 | 13014
P01396 | 55 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.29 | -13.99 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 597.6 | 13.2 | 2.56 | - | 43870 | 0 | 43870
P01397 | 62.5 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.18 | -15.89 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 899.4 | 30.3 | 2.24 | - | 59548 | 0 | 59548
P01398 | 62.5 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.69 | -15.01 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 573 | 12.4 | 2.43 | - | 38862 | 0 | 38862
P01399 | 62.5 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.55 | -11.68 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 185.7 | 1.5 | 3.26 | - | 12887 | 0 | 12887
P01400 | 62.5 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.16 | -13.87 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 634.2 | 15.3 | 2.34 | - | 42811 | 0 | 42811
P01401 | 70 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -13.95 | -15.65 | 18.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 958.3 | 34.8 | 2.09 | - | 57622 | 0 | 57622
P01402 | 70 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.56 | -14.83 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 612.3 | 14.5 | 2.21 | - | 37802 | 0 | 37802
P01403 | 70 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.57 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 205.5 | 1.8 | 2.95 | - | 13014 | 0 | 13014
P01404 | 70 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.06 | -13.77 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 683.1 | 17.9 | 2.15 | - | 41956 | 0 | 41956
P01405 | 56 | -20 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.32 | -16.03 | 19.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 850.6 | 26.7 | 2.38 | - | 60692 | 0 | 60692
P01406 | 56 | -15 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.74 | -15.09 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 538.8 | 10.8 | 2.61 | - | 39307 | 0 | 39307
P01407 | 56 | -10 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.57 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 175.2 | 1.4 | 3.57 | - | 13059 | 0 | 13059
P01408 | 56 | -16 | -7 | 22353.12 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.28 | -13.99 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 602.9 | 13.5 | 2.53 | - | 43792 | 0 | 43792
P01409 | 25 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.14 | -15.85 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 748.8 | 18.6 | 3.13 | - | 70612 | 0 | 70612
P01410 | 25 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.55 | -14.81 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 468.7 | 7.5 | 3.5 | - | 44956 | 0 | 44956
P01411 | 25 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.48 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 150 | 1 | 5.12 | - | 14627 | 0 | 14627
P01412 | 25 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.11 | -13.82 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 528.3 | 9.4 | 3.38 | - | 50505 | 0 | 50505
P01413 | 32.5 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.07 | -15.78 | 18.8 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 785.8 | 20.9 | 2.91 | - | 69908 | 0 | 69908
P01414 | 32.5 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.53 | -14.79 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 494.7 | 8.5 | 3.22 | - | 44802 | 0 | 44802
P01415 | 32.5 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.5 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 160.6 | 1.1 | 4.62 | - | 14798 | 0 | 14798
P01416 | 32.5 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.06 | -13.77 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 554.6 | 10.6 | 3.11 | - | 50057 | 0 | 50057
P01417 | 40 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.96 | -15.67 | 18.6 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 824.3 | 23.5 | 2.72 | - | 68820 | 0 | 68820
P01418 | 40 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.49 | -14.74 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 522 | 9.6 | 2.98 | - | 44423 | 0 | 44423
P01419 | 40 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.47 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 168.1 | 1.2 | 4.16 | - | 14574 | 0 | 14574
P01420 | 40 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.02 | -13.73 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 585.2 | 12 | 2.89 | - | 49612 | 0 | 49612
P01421 | 47.5 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.84 | -15.54 | 18.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 867.9 | 26.6 | 2.54 | - | 67590 | 0 | 67590
P01422 | 47.5 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.45 | -14.68 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 553.6 | 11 | 2.76 | - | 44007 | 0 | 44007
P01423 | 47.5 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.49 | -11.63 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 181.9 | 1.4 | 3.79 | - | 14748 | 0 | 14748
P01424 | 47.5 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.94 | -15.41 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 616.7 | 13.5 | 2.69 | - | 48825 | 0 | 48825
P01425 | 55 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.71 | -15.41 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 919.6 | 30.4 | 2.38 | - | 66327 | 0 | 66327
P01426 | 55 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.37 | -14.58 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 586.4 | 12.5 | 2.57 | - | 43242 | 0 | 43242
P01427 | 55 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.47 | -11.61 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 192.8 | 1.6 | 3.43 | - | 14523 | 0 | 14523
P01428 | 55 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.88 | -15.32 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 657.2 | 15.6 | 2.5 | - | 48251 | 0 | 48251
P01429 | 62.5 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.55 | -15.25 | 17.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 978.2 | 34.9 | 2.22 | - | 64766 | 0 | 64766
P01430 | 62.5 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.32 | -14.51 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 629.8 | 14.6 | 2.38 | - | 42713 | 0 | 42713
P01431 | 62.5 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.49 | -11.63 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 211.6 | 1.8 | 3.12 | - | 14689 | 0 | 14689
P01432 | 62.5 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.8 | -15.18 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 702.6 | 18.1 | 2.32 | - | 47427 | 0 | 47427
P01433 | 70 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.34 | -15.04 | 17.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1041.9 | 40.1 | 2.08 | - | 62647 | 0 | 62647
P01434 | 70 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.19 | -14.34 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 671 | 17 | 2.17 | - | 41425 | 0 | 41425
P01435 | 70 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.46 | -11.61 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 228.3 | 2.1 | 2.82 | - | 14456 | 0 | 14456
P01436 | 70 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.64 | -14.94 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 746.3 | 20.9 | 2.12 | - | 45833 | 0 | 45833
P01437 | 56 | -20 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -13.69 | -15.4 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 927.3 | 31 | 2.35 | - | 66165 | 0 | 66165
P01438 | 56 | -15 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.37 | -14.57 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 591.7 | 12.7 | 2.55 | - | 43167 | 0 | 43167
P01439 | 56 | -10 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.47 | -11.61 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 195.1 | 1.6 | 3.39 | - | 14546 | 0 | 14546
P01440 | 56 | -16 | -7 | 26641.8 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.87 | -15.3 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 662.9 | 15.9 | 2.48 | - | 48151 | 0 | 48151
P01441 | 25 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.66 | -15.36 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 810.3 | 21.4 | 3.07 | - | 76419 | 0 | 76419
P01442 | 25 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.31 | -14.49 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 515.7 | 8.6 | 3.49 | - | 49465 | 0 | 49465
P01443 | 25 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.4 | -11.55 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 165.1 | 1.1 | 4.87 | - | 16096 | 0 | 16096
P01444 | 25 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.82 | -15.22 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 579.1 | 10.8 | 3.36 | - | 55357 | 0 | 55357
P01445 | 32.5 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.58 | -15.28 | 17.9 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 848.7 | 24 | 2.86 | - | 75496 | 0 | 75496
P01446 | 32.5 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.22 | -14.38 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 535 | 9.7 | 3.14 | - | 48456 | 0 | 48456
P01447 | 32.5 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.42 | -11.57 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 177 | 1.3 | 4.41 | - | 16313 | 0 | 16313
P01448 | 32.5 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.72 | -15.06 | 15.2 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 599.6 | 12.1 | 3.05 | - | 54113 | 0 | 54113
P01449 | 40 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.45 | -15.15 | 17.7 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 886.8 | 26.7 | 2.69 | - | 74036 | 0 | 74036
P01450 | 40 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.19 | -14.34 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 565.2 | 11 | 2.92 | - | 48098 | 0 | 48098
P01451 | 40 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.4 | -11.55 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 184.9 | 1.4 | 3.97 | - | 16029 | 0 | 16029
P01452 | 40 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.68 | -15 | 15.1 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 633 | 13.7 | 2.83 | - | 53662 | 0 | 53662
P01453 | 47.5 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.32 | -15.02 | 17.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 931.1 | 30 | 2.52 | - | 72516 | 0 | 72516
P01454 | 47.5 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.15 | -14.29 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 599.1 | 12.6 | 2.71 | - | 47627 | 0 | 47627
P01455 | 47.5 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.41 | -11.56 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 200.1 | 1.6 | 3.62 | - | 16229 | 0 | 16229
P01456 | 47.5 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.61 | -14.91 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 668.6 | 15.6 | 2.64 | - | 52935 | 0 | 52935
P01457 | 55 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.18 | -14.88 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 983.1 | 34 | 2.37 | - | 70908 | 0 | 70908
P01458 | 55 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.09 | -14.21 | 14.3 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 636.5 | 14.4 | 2.52 | - | 46933 | 0 | 46933
P01459 | 55 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.39 | -11.54 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 211.9 | 1.8 | 3.28 | - | 15962 | 0 | 15962
P01460 | 55 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.52 | -14.77 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 705.9 | 17.7 | 2.47 | - | 51821 | 0 | 51821
P01461 | 62.5 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.03 | -14.74 | 17.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1046 | 39 | 2.21 | - | 69258 | 0 | 69258
P01462 | 62.5 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.95 | -13.95 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 668.2 | 16.3 | 2.31 | - | 45319 | 0 | 45319
P01463 | 62.5 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.41 | -11.56 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 232.2 | 2.1 | 2.99 | - | 16120 | 0 | 16120
P01464 | 62.5 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.44 | -14.67 | 14.8 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 755.5 | 20.5 | 2.29 | - | 50998 | 0 | 50998
P01465 | 70 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -12.85 | -14.55 | 16.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1116.9 | 45.1 | 2.06 | - | 67158 | 0 | 67158
P01466 | 70 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -10.87 | -13.87 | 14.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 720 | 19.2 | 2.13 | - | 44453 | 0 | 44453
P01467 | 70 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.38 | -11.53 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 249.4 | 2.4 | 2.7 | - | 15795 | 0 | 15795
P01468 | 70 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.33 | -14.52 | 14.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 808.8 | 23.8 | 2.12 | - | 49676 | 0 | 49676
P01469 | 56 | -20 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.16 | -14.87 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 991.5 | 34.6 | 2.35 | - | 70745 | 0 | 70745
P01470 | 56 | -15 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.08 | -14.2 | 14.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 642 | 14.7 | 2.49 | - | 46841 | 0 | 46841
P01471 | 56 | -10 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.39 | -11.55 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 214.4 | 1.8 | 3.24 | - | 15984 | 0 | 15984
P01472 | 56 | -16 | -7 | 30930.48 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.51 | -14.76 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 711.9 | 18 | 2.45 | - | 51714 | 0 | 51714
P01473 | 25 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.29 | -14.99 | 17.5 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 867.9 | 23.7 | 3.09 | - | 81844 | 0 | 81844
P01474 | 25 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11 | -14.1 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 542.7 | 9.6 | 3.36 | - | 52055 | 0 | 52055
P01475 | 25 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.33 | -11.49 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 177 | 1.2 | 4.73 | - | 17262 | 0 | 17262
P01476 | 25 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.55 | -14.82 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 619.8 | 12.2 | 3.3 | - | 59246 | 0 | 59246
P01477 | 32.5 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.14 | -14.85 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 899.3 | 26.4 | 2.85 | - | 80002 | 0 | 80002
P01478 | 32.5 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.97 | -14.06 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 570.1 | 10.8 | 3.1 | - | 51630 | 0 | 51630
P01479 | 32.5 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.34 | -11.5 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 189.5 | 1.4 | 4.27 | - | 17463 | 0 | 17463
P01480 | 32.5 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.48 | -14.72 | 14.8 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 646.1 | 13.6 | 3.06 | - | 58312 | 0 | 58312
P01481 | 40 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.03 | -14.73 | 17.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 940.7 | 29.5 | 2.67 | - | 78535 | 0 | 78535
P01482 | 40 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.93 | -13.93 | 14.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 601 | 12.3 | 2.88 | - | 51141 | 0 | 51141
P01483 | 40 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.36 | -11.52 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 203.7 | 1.6 | 3.89 | - | 17662 | 0 | 17662
P01484 | 40 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.37 | -14.58 | 14.7 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 671.8 | 15.2 | 2.81 | - | 56957 | 0 | 56957
P01485 | 47.5 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.91 | -14.62 | 16.9 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 988.9 | 33.2 | 2.51 | - | 77015 | 0 | 77015
P01486 | 47.5 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.88 | -13.88 | 14.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 636 | 13.9 | 2.68 | - | 50556 | 0 | 50556
P01487 | 47.5 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.33 | -11.5 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 214.2 | 1.7 | 3.52 | - | 17366 | 0 | 17366
P01488 | 47.5 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.31 | -14.49 | 14.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 709 | 17.3 | 2.61 | - | 56136 | 0 | 56136
P01489 | 55 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.77 | -14.47 | 16.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 1042 | 37.5 | 2.36 | - | 75156 | 0 | 75156
P01490 | 55 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.78 | -13.78 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 667.7 | 15.9 | 2.45 | - | 49232 | 0 | 49232
P01491 | 55 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.35 | -11.51 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 233.1 | 2 | 3.21 | - | 17557 | 0 | 17557
P01492 | 55 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.25 | -14.41 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 753.2 | 19.8 | 2.43 | - | 55298 | 0 | 55298
P01493 | 62.5 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.6 | -14.31 | 16.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 1101.7 | 42.5 | 2.21 | - | 72948 | 0 | 72948
P01494 | 62.5 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.71 | -13.71 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 711.5 | 18.3 | 2.27 | - | 48258 | 0 | 48258
P01495 | 62.5 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.33 | -11.49 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 248.5 | 2.3 | 2.91 | - | 17252 | 0 | 17252
P01496 | 62.5 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.16 | -14.3 | 14.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 802 | 22.8 | 2.27 | - | 54139 | 0 | 54139
P01497 | 70 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.35 | -14.05 | 16.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1158.1 | 48.3 | 2.03 | - | 69636 | 0 | 69636
P01498 | 70 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.6 | -13.6 | 13.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 760.1 | 21 | 2.12 | - | 46926 | 0 | 46926
P01499 | 70 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.34 | -11.5 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 275 | 2.7 | 2.64 | - | 17417 | 0 | 17417
P01500 | 70 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.06 | -14.18 | 14.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 860.4 | 26.5 | 2.1 | - | 52841 | 0 | 52841
P01501 | 56 | -20 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -12.75 | -14.45 | 16.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 1049.7 | 38.1 | 2.34 | - | 74891 | 0 | 74891
P01502 | 56 | -15 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.77 | -13.77 | 13.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 672.6 | 16.1 | 2.42 | - | 49071 | 0 | 49071
P01503 | 56 | -10 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.35 | -11.51 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 235.8 | 2 | 3.17 | - | 17582 | 0 | 17582
P01504 | 56 | -16 | -7 | 35089.2 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.24 | -14.4 | 14.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 759.7 | 20.2 | 2.41 | - | 55180 | 0 | 55180
P01505 | 25 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.44 | -16.15 | 19.4 | R290 (Propane) | Countercurrent | -20 | 0 | 25 | 20 | 722.8 | 17.5 | 3.14 | - | 68165 | 0 | 68165
P01506 | 25 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.74 | -15.1 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 25 | 20 | 452.8 | 6.6 | 3.62 | - | 43434 | 0 | 43434
P01507 | 25 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.52 | -11.66 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 25 | 20 | 142.8 | 0.9 | 5.24 | - | 13926 | 0 | 13926
P01508 | 25 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.33 | -14.04 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 25 | 20 | 511.1 | 8.7 | 3.48 | - | 48856 | 0 | 48856
P01509 | 32.5 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.34 | -16.05 | 19.3 | R290 (Propane) | Countercurrent | -20 | 0 | 32.5 | 20 | 756.2 | 19.6 | 2.92 | - | 67272 | 0 | 67272
P01510 | 32.5 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.65 | -14.97 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 32.5 | 20 | 470.7 | 7.8 | 3.26 | - | 42629 | 0 | 42629
P01511 | 32.5 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.55 | -11.68 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 32.5 | 20 | 154 | 1.1 | 4.7 | - | 14195 | 0 | 14195
P01512 | 32.5 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.29 | -14 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 32.5 | 20 | 537.5 | 9.8 | 3.2 | - | 48509 | 0 | 48509
P01513 | 40 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.25 | -15.96 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 40 | 20 | 795.8 | 22.2 | 2.73 | - | 66442 | 0 | 66442
P01514 | 40 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.63 | -14.94 | 15.1 | R290 (Propane) | Countercurrent | -15 | 0 | 40 | 20 | 498.7 | 8.9 | 3.01 | - | 42443 | 0 | 42443
P01515 | 40 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.52 | -11.65 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 40 | 20 | 160.1 | 1.2 | 4.26 | - | 13883 | 0 | 13883
P01516 | 40 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.24 | -13.95 | 15.9 | R290 (Propane) | Countercurrent | -16 | 0 | 40 | 20 | 566.4 | 11.2 | 2.97 | - | 48016 | 0 | 48016
P01517 | 47.5 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.11 | -15.82 | 18.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 20 | 836.7 | 25 | 2.56 | - | 65167 | 0 | 65167
P01518 | 47.5 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.59 | -14.87 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 20 | 528.8 | 10.1 | 2.8 | - | 42036 | 0 | 42036
P01519 | 47.5 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.55 | -11.68 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 47.5 | 20 | 174.6 | 1.3 | 3.86 | - | 14158 | 0 | 14158
P01520 | 47.5 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.14 | -13.84 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 20 | 594.4 | 12.7 | 2.71 | - | 47055 | 0 | 47055
P01521 | 55 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.97 | -15.68 | 18.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 20 | 885.4 | 28.4 | 2.39 | - | 63859 | 0 | 63859
P01522 | 55 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.55 | -14.82 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 20 | 565.7 | 11.8 | 2.59 | - | 41713 | 0 | 41713
P01523 | 55 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.51 | -11.65 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 20 | 183.8 | 1.5 | 3.51 | - | 13843 | 0 | 13843
P01524 | 55 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.07 | -13.77 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 20 | 632.4 | 14.6 | 2.52 | - | 46427 | 0 | 46427
P01525 | 62.5 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.81 | -15.52 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 20 | 942.5 | 32.7 | 2.24 | - | 62404 | 0 | 62404
P01526 | 62.5 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.41 | -14.62 | 14.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 20 | 595.5 | 13.4 | 2.37 | - | 40386 | 0 | 40386
P01527 | 62.5 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.54 | -11.67 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 20 | 203.4 | 1.7 | 3.18 | - | 14117 | 0 | 14117
P01528 | 62.5 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.99 | -15.49 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 20 | 677 | 17 | 2.34 | - | 45699 | 0 | 45699
P01529 | 70 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.57 | -15.28 | 17.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 20 | 1001.6 | 37.5 | 2.09 | - | 60224 | 0 | 60224
P01530 | 70 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.34 | -14.53 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 20 | 644 | 15.8 | 2.18 | - | 39761 | 0 | 39761
P01531 | 70 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.51 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 20 | 217.7 | 1.9 | 2.88 | - | 13789 | 0 | 13789
P01532 | 70 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.87 | -15.3 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 20 | 726.8 | 19.8 | 2.17 | - | 44640 | 0 | 44640
P01533 | 56 | -20 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -13.95 | -15.65 | 18.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 20 | 892.4 | 29 | 2.37 | - | 63670 | 0 | 63670
P01534 | 56 | -15 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.54 | -14.8 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 20 | 569.9 | 12 | 2.57 | - | 41582 | 0 | 41582
P01535 | 56 | -10 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.51 | -11.65 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 20 | 186 | 1.5 | 3.47 | - | 13865 | 0 | 13865
P01536 | 56 | -16 | -7 | 24692.4 | 20 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.06 | -13.77 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 20 | 637.9 | 14.9 | 2.49 | - | 46339 | 0 | 46339
P00010 | 47.5 | -20 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.47 | -19.35 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 290.7 | 2.9 | 4.47 | - | 30893 | 0 | 30893
P00011 | 47.5 | -15 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.96 | -15.79 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 61.5 | 0.4 | 8.01 | - | 6631 | 0 | 6631
P00012 | 47.5 | -16 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.63 | -16.46 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 104.6 | 0.8 | 6.48 | - | 11254 | 0 | 11254
P00013 | 55 | -20 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.47 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 305.6 | 3.2 | 3.95 | - | 30927 | 0 | 30927
P00014 | 55 | -15 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.77 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 63.6 | 0.5 | 7.16 | - | 6538 | 0 | 6538
P00015 | 55 | -16 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.65 | -16.48 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 111.3 | 0.8 | 5.71 | - | 11404 | 0 | 11404
P00016 | 62.5 | -20 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.48 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 322.3 | 3.5 | 3.59 | - | 30949 | 0 | 30949
P00017 | 62.5 | -15 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.96 | -15.79 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 68.1 | 0.5 | 6.51 | - | 6654 | 0 | 6654
P00018 | 62.5 | -16 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.67 | -16.5 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 118.3 | 0.9 | 5.14 | - | 11513 | 0 | 11513
P00019 | 70 | -20 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.48 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 341.2 | 4 | 3.3 | - | 30968 | 0 | 30968
P00020 | 70 | -15 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.77 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 70.8 | 0.5 | 5.91 | - | 6538 | 0 | 6538
P00021 | 70 | -16 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.64 | -16.47 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 123.1 | 1 | 4.63 | - | 11330 | 0 | 11330
P00022 | 56 | -20 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.47 | -19.36 | 15.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 307.7 | 3.2 | 3.9 | - | 30930 | 0 | 30930
P00023 | 56 | -15 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -13.95 | -15.77 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 64 | 0.5 | 7.08 | - | 6538 | 0 | 6538
P00024 | 56 | -16 | -13 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -14.65 | -16.49 | 11.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 112.2 | 0.9 | 5.63 | - | 11419 | 0 | 11419
P00034 | 47.5 | -20 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.16 | -19.03 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 332.3 | 3.5 | 4.25 | - | 35313 | 0 | 35313
P00035 | 47.5 | -15 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.72 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 70.2 | 0.5 | 7.54 | - | 7576 | 0 | 7576
P00036 | 47.5 | -16 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.51 | -16.34 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 119.2 | 0.9 | 6.08 | - | 12819 | 0 | 12819
P00037 | 55 | -20 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.16 | -19.04 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 349.2 | 3.8 | 3.77 | - | 35335 | 0 | 35335
P00038 | 55 | -15 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 71.9 | 0.5 | 6.72 | - | 7393 | 0 | 7393
P00039 | 55 | -16 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.54 | -16.37 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 127.5 | 1 | 5.32 | - | 13069 | 0 | 13069
P00040 | 62.5 | -20 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.16 | -19.03 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 367.5 | 4.3 | 3.43 | - | 35294 | 0 | 35294
P00041 | 62.5 | -15 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.89 | -15.72 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 77.8 | 0.6 | 6.07 | - | 7596 | 0 | 7596
P00042 | 62.5 | -16 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.55 | -16.39 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 135.6 | 1.1 | 4.79 | - | 13194 | 0 | 13194
P00043 | 70 | -20 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.15 | -19.02 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 387.9 | 4.9 | 3.17 | - | 35203 | 0 | 35203
P00044 | 70 | -15 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.91 | -15.74 | 10.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 83.7 | 0.6 | 5.52 | - | 7734 | 0 | 7734
P00045 | 70 | -16 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.52 | -16.35 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 140 | 1.2 | 4.33 | - | 12891 | 0 | 12891
P00046 | 56 | -20 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -17.16 | -19.04 | 14.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 351.5 | 3.9 | 3.72 | - | 35336 | 0 | 35336
P00047 | 56 | -15 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 72.6 | 0.5 | 6.63 | - | 7411 | 0 | 7411
P00048 | 56 | -16 | -13 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -14.54 | -16.37 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 128.5 | 1 | 5.24 | - | 13086 | 0 | 13086
P00058 | 47.5 | -20 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.91 | -18.78 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 372.1 | 4.1 | 4.07 | - | 39546 | 0 | 39546
P00059 | 47.5 | -15 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.83 | -15.66 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 77.7 | 0.5 | 7.18 | - | 8383 | 0 | 8383
P00060 | 47.5 | -16 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.46 | -16.29 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 136.9 | 1 | 5.86 | - | 14726 | 0 | 14726
P00061 | 55 | -20 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.88 | -18.75 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 388 | 4.6 | 3.63 | - | 39265 | 0 | 39265
P00062 | 55 | -15 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 83.5 | 0.6 | 6.39 | - | 8583 | 0 | 8583
P00063 | 55 | -16 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.43 | -16.26 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 141.1 | 1.1 | 5.07 | - | 14458 | 0 | 14458
P00064 | 62.5 | -20 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.86 | -18.73 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 407.2 | 5.5 | 3.32 | - | 39100 | 0 | 39100
P00065 | 62.5 | -15 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.83 | -15.66 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 86 | 0.6 | 5.76 | - | 8395 | 0 | 8395
P00066 | 62.5 | -16 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.45 | -16.28 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 150.4 | 1.2 | 4.56 | - | 14638 | 0 | 14638
P00067 | 70 | -20 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.83 | -18.7 | 14.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 427.6 | 6.6 | 3.08 | - | 38814 | 0 | 38814
P00068 | 70 | -15 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 92.9 | 0.7 | 5.21 | - | 8583 | 0 | 8583
P00069 | 70 | -16 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.46 | -16.3 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 161 | 1.4 | 4.15 | - | 14820 | 0 | 14820
P00070 | 56 | -20 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.88 | -18.75 | 14.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 390.5 | 4.8 | 3.59 | - | 39247 | 0 | 39247
P00071 | 56 | -15 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 84 | 0.6 | 6.31 | - | 8583 | 0 | 8583
P00072 | 56 | -16 | -13 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -14.43 | -16.27 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 142.6 | 1.1 | 4.99 | - | 14513 | 0 | 14513
P00082 | 47.5 | -20 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.67 | -18.53 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 405.3 | 5.1 | 3.97 | - | 43074 | 0 | 43074
P00083 | 47.5 | -15 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.79 | -15.61 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 85.5 | 0.6 | 6.88 | - | 9226 | 0 | 9226
P00084 | 47.5 | -16 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.37 | -16.2 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 149.7 | 1.1 | 5.63 | - | 16107 | 0 | 16107
P00085 | 55 | -20 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.64 | -18.51 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 423 | 6 | 3.53 | - | 42811 | 0 | 42811
P00086 | 55 | -15 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 91.3 | 0.7 | 6.11 | - | 9385 | 0 | 9385
P00087 | 55 | -16 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.35 | -16.18 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 154.3 | 1.2 | 4.87 | - | 15812 | 0 | 15812
P00088 | 62.5 | -20 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.62 | -18.49 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 443.4 | 7.1 | 3.24 | - | 42580 | 0 | 42580
P00089 | 62.5 | -15 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.79 | -15.61 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 94.7 | 0.7 | 5.47 | - | 9246 | 0 | 9246
P00090 | 62.5 | -16 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.36 | -16.19 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 164.2 | 1.4 | 4.37 | - | 15984 | 0 | 15984
P00091 | 70 | -20 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.51 | -18.37 | 13.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 454.6 | 8 | 2.97 | - | 41263 | 0 | 41263
P00092 | 70 | -15 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 101.6 | 0.8 | 4.98 | - | 9385 | 0 | 9385
P00093 | 70 | -16 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.38 | -16.21 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 176.3 | 1.6 | 3.97 | - | 16227 | 0 | 16227
P00094 | 56 | -20 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.64 | -18.51 | 14 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 425.7 | 6.1 | 3.49 | - | 42785 | 0 | 42785
P00095 | 56 | -15 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 91.9 | 0.7 | 6.03 | - | 9385 | 0 | 9385
P00096 | 56 | -16 | -13 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -14.35 | -16.18 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 155.5 | 1.3 | 4.8 | - | 15835 | 0 | 15835
P00106 | 47.5 | -20 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.44 | -18.3 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 431.1 | 6.1 | 3.91 | - | 45814 | 0 | 45814
P00107 | 47.5 | -15 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.75 | -15.57 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 92.1 | 0.7 | 6.64 | - | 9933 | 0 | 9933
P00108 | 47.5 | -16 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.3 | -16.13 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 161.4 | 1.3 | 5.44 | - | 17362 | 0 | 17362
P00109 | 55 | -20 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.42 | -18.28 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 450.1 | 7.1 | 3.49 | - | 45546 | 0 | 45546
P00110 | 55 | -15 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.72 | -15.55 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 93.6 | 0.7 | 5.9 | - | 9621 | 0 | 9621
P00111 | 55 | -16 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.32 | -16.15 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 171.6 | 1.4 | 4.76 | - | 17584 | 0 | 17584
P00112 | 62.5 | -20 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.39 | -18.25 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 470.6 | 8.4 | 3.21 | - | 45191 | 0 | 45191
P00113 | 62.5 | -15 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.74 | -15.57 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 101.3 | 0.8 | 5.29 | - | 9887 | 0 | 9887
P00114 | 62.5 | -16 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.29 | -16.12 | 11.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 177 | 1.5 | 4.22 | - | 17226 | 0 | 17226
P00115 | 70 | -20 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.35 | -18.21 | 13.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 492.4 | 9.9 | 2.97 | - | 44691 | 0 | 44691
P00116 | 70 | -15 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.8 | -15.63 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 115.3 | 0.9 | 4.88 | - | 10647 | 0 | 10647
P00117 | 70 | -16 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.3 | -16.13 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 188.9 | 1.7 | 3.84 | - | 17387 | 0 | 17387
P00118 | 56 | -20 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.41 | -18.27 | 13.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 452.7 | 7.3 | 3.45 | - | 45504 | 0 | 45504
P00119 | 56 | -15 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -13.72 | -15.55 | 10.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 94.5 | 0.7 | 5.81 | - | 9646 | 0 | 9646
P00120 | 56 | -16 | -13 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -14.32 | -16.15 | 11.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 173 | 1.4 | 4.69 | - | 17608 | 0 | 17608
P00130 | 47.5 | -20 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -17.01 | -18.89 | 14.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 354.2 | 3.8 | 4.14 | - | 37644 | 0 | 37644
P00131 | 47.5 | -15 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.85 | -15.68 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 74.2 | 0.5 | 7.33 | - | 8008 | 0 | 8008
P00132 | 47.5 | -16 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.5 | -16.33 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 130.7 | 1 | 5.99 | - | 14058 | 0 | 14058
P00133 | 55 | -20 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -17.01 | -18.89 | 14.5 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 372 | 4.2 | 3.68 | - | 37644 | 0 | 37644
P00134 | 55 | -15 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 79.5 | 0.6 | 6.55 | - | 8172 | 0 | 8172
P00135 | 55 | -16 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.47 | -16.31 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 134.9 | 1.1 | 5.2 | - | 13822 | 0 | 13822
P00136 | 62.5 | -20 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -17.01 | -18.89 | 14.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 392 | 4.9 | 3.37 | - | 37644 | 0 | 37644
P00137 | 62.5 | -15 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.86 | -15.69 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 82.4 | 0.6 | 5.88 | - | 8047 | 0 | 8047
P00138 | 62.5 | -16 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.49 | -16.32 | 11.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 143.6 | 1.2 | 4.67 | - | 13973 | 0 | 13973
P00139 | 70 | -20 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.93 | -18.8 | 14.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 405.9 | 5.8 | 3.05 | - | 36841 | 0 | 36841
P00140 | 70 | -15 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.88 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 89 | 0.7 | 5.35 | - | 8222 | 0 | 8222
P00141 | 70 | -16 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.46 | -16.3 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 149.2 | 1.3 | 4.2 | - | 13738 | 0 | 13738
P00142 | 56 | -20 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -17.01 | -18.89 | 14.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 374.5 | 4.3 | 3.63 | - | 37644 | 0 | 37644
P00143 | 56 | -15 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -13.87 | -15.7 | 10.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 80.2 | 0.6 | 6.46 | - | 8191 | 0 | 8191
P00144 | 56 | -16 | -13 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -14.48 | -16.31 | 11.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 136 | 1.1 | 5.12 | - | 13842 | 0 | 13842
P00157 | 47.5 | -20 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.36 | -17.07 | 23.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 592.6 | 11 | 4.18 | - | 62974 | 0 | 62974
P00158 | 47.5 | -15 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.05 | -13.74 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 377.5 | 3.5 | 5.11 | - | 40722 | 0 | 40722
P00160 | 47.5 | -16 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.73 | -14.4 | 18.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 420.7 | 4.8 | 4.85 | - | 45253 | 0 | 45253
P00161 | 55 | -20 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.29 | -17 | 22.9 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 617.7 | 12.3 | 3.69 | - | 62514 | 0 | 62514
P00162 | 55 | -15 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.05 | -13.74 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 396.1 | 4.2 | 4.33 | - | 40722 | 0 | 40722
P00163 | 55 | -10 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.43 | -11.53 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 156.3 | 1 | 6.07 | - | 16316 | 0 | 16316
P00164 | 55 | -16 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.73 | -14.4 | 18.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 441.5 | 5.8 | 4.15 | - | 45253 | 0 | 45253
P00165 | 62.5 | -20 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.23 | -16.93 | 22.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 646.5 | 13.9 | 3.37 | - | 62083 | 0 | 62083
P00166 | 62.5 | -15 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.04 | -13.72 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 416.3 | 5 | 3.87 | - | 40647 | 0 | 40647
P00167 | 62.5 | -10 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.45 | -11.55 | 12.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 166.1 | 1.1 | 5.35 | - | 16484 | 0 | 16484
P00168 | 62.5 | -16 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.69 | -14.37 | 18.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 462.4 | 6.9 | 3.73 | - | 45003 | 0 | 45003
P00169 | 70 | -20 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.15 | -16.85 | 22.6 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 678.3 | 15.7 | 3.12 | - | 61560 | 0 | 61560
P00170 | 70 | -15 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.02 | -13.7 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 438 | 6.1 | 3.53 | - | 40462 | 0 | 40462
P00171 | 70 | -10 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.41 | -11.51 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 172.1 | 1.2 | 4.76 | - | 16175 | 0 | 16175
P00172 | 70 | -16 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.66 | -14.34 | 18 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 486.9 | 8.1 | 3.41 | - | 44823 | 0 | 44823
P00173 | 56 | -20 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.28 | -16.99 | 22.9 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 621.4 | 12.5 | 3.64 | - | 62457 | 0 | 62457
P00174 | 56 | -15 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.05 | -13.74 | 17 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 398.7 | 4.3 | 4.25 | - | 40722 | 0 | 40722
P00175 | 56 | -10 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -8.43 | -11.53 | 12.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 157.4 | 1 | 5.96 | - | 16330 | 0 | 16330
P00176 | 56 | -16 | -6 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.72 | -14.39 | 18.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 443.9 | 5.9 | 4.08 | - | 45187 | 0 | 45187
P00189 | 47.5 | -20 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.61 | -16.3 | 21.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 669.9 | 13.7 | 4.04 | - | 71192 | 0 | 71192
P00190 | 47.5 | -15 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.62 | -14.85 | 16.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 430.5 | 5.1 | 4.9 | - | 46442 | 0 | 46442
P00192 | 47.5 | -16 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.23 | -13.91 | 17.3 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 478.8 | 7 | 4.67 | - | 51501 | 0 | 51501
P00193 | 55 | -20 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.55 | -16.24 | 21.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 698.2 | 15.3 | 3.59 | - | 70654 | 0 | 70654
P00194 | 55 | -15 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.61 | -14.83 | 16.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 450.8 | 6.1 | 4.15 | - | 46346 | 0 | 46346
P00195 | 55 | -10 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.27 | -11.4 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 179.4 | 1.2 | 5.69 | - | 18729 | 0 | 18729
P00196 | 55 | -16 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.23 | -13.91 | 17.3 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 502.5 | 7.9 | 3.99 | - | 51501 | 0 | 51501
P00197 | 62.5 | -20 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.48 | -16.17 | 21.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 729.6 | 17.2 | 3.28 | - | 70066 | 0 | 70066
P00198 | 62.5 | -15 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.59 | -14.81 | 16.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 473.3 | 7.3 | 3.72 | - | 46212 | 0 | 46212
P00199 | 62.5 | -10 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.29 | -11.41 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 190.2 | 1.3 | 5.01 | - | 18875 | 0 | 18875
P00200 | 62.5 | -16 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.2 | -13.88 | 17.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 526 | 9 | 3.59 | - | 51192 | 0 | 51192
P00201 | 70 | -20 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.36 | -16.05 | 21 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 761.4 | 19.2 | 3.06 | - | 69102 | 0 | 69102
P00202 | 70 | -15 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.57 | -14.77 | 16.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 498.1 | 8.2 | 3.4 | - | 46009 | 0 | 46009
P00203 | 70 | -10 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.26 | -11.39 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 198.2 | 1.4 | 4.44 | - | 18627 | 0 | 18627
P00204 | 70 | -16 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.15 | -13.83 | 17.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 552.1 | 10.1 | 3.29 | - | 50818 | 0 | 50818
P00205 | 56 | -20 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.54 | -16.23 | 21.4 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 702.1 | 15.5 | 3.54 | - | 70575 | 0 | 70575
P00206 | 56 | -15 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.61 | -14.83 | 16.4 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 453.8 | 6.3 | 4.08 | - | 46346 | 0 | 46346
P00207 | 56 | -10 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -8.27 | -11.4 | 12.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 180.7 | 1.2 | 5.58 | - | 18745 | 0 | 18745
P00208 | 56 | -16 | -6 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.23 | -13.91 | 17.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 505.9 | 8.1 | 3.93 | - | 51501 | 0 | 51501
P00221 | 47.5 | -20 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.98 | -15.66 | 20.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 739.2 | 16.3 | 3.96 | - | 78560 | 0 | 78560
P00222 | 47.5 | -15 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.23 | -14.23 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 477.7 | 6.9 | 4.76 | - | 51535 | 0 | 51535
P00224 | 47.5 | -16 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.81 | -15.12 | 16.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 531.6 | 8.5 | 4.52 | - | 57177 | 0 | 57177
P00225 | 55 | -20 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.9 | -15.58 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 768.5 | 18.1 | 3.52 | - | 77766 | 0 | 77766
P00226 | 55 | -15 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.22 | -14.22 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 500.1 | 7.7 | 4.01 | - | 51416 | 0 | 51416
P00227 | 55 | -10 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.12 | -11.27 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 199.9 | 1.3 | 5.43 | - | 20869 | 0 | 20869
P00228 | 55 | -16 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.78 | -15.08 | 16.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 555.1 | 9.5 | 3.86 | - | 56893 | 0 | 56893
P00229 | 62.5 | -20 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.82 | -15.5 | 20 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 802.2 | 20.3 | 3.23 | - | 77035 | 0 | 77035
P00230 | 62.5 | -15 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.2 | -14.2 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 524 | 8.7 | 3.6 | - | 51162 | 0 | 51162
P00231 | 62.5 | -10 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.13 | -11.29 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 211.7 | 1.5 | 4.77 | - | 21008 | 0 | 21008
P00232 | 62.5 | -16 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.74 | -15.02 | 16.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 580.5 | 10.6 | 3.49 | - | 56491 | 0 | 56491
P00233 | 70 | -20 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.73 | -15.41 | 19.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 839.1 | 22.7 | 3 | - | 76159 | 0 | 76159
P00234 | 70 | -15 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.11 | -14.11 | 15.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 544.8 | 9.8 | 3.25 | - | 50321 | 0 | 50321
P00235 | 70 | -10 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.1 | -11.26 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 220.2 | 1.6 | 4.23 | - | 20692 | 0 | 20692
P00236 | 70 | -16 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.71 | -14.97 | 16.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 610.3 | 12.1 | 3.2 | - | 56181 | 0 | 56181
P00237 | 56 | -20 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.89 | -15.56 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 772.7 | 18.4 | 3.47 | - | 77667 | 0 | 77667
P00238 | 56 | -15 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.22 | -14.22 | 15.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 503.3 | 7.9 | 3.95 | - | 51397 | 0 | 51397
P00239 | 56 | -10 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -8.12 | -11.28 | 12 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 201.4 | 1.3 | 5.33 | - | 20888 | 0 | 20888
P00240 | 56 | -16 | -6 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.76 | -15.06 | 16.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 557.6 | 9.6 | 3.8 | - | 56762 | 0 | 56762
P00253 | 47.5 | -20 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.4 | -15.08 | 19.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 796.1 | 18.5 | 3.91 | - | 84605 | 0 | 84605
P00254 | 47.5 | -15 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.91 | -13.91 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 520.8 | 8 | 4.66 | - | 56187 | 0 | 56187
P00256 | 47.5 | -16 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.43 | -14.59 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 577.3 | 9.8 | 4.44 | - | 62097 | 0 | 62097
P00257 | 55 | -20 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.26 | -14.93 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 819.9 | 20.6 | 3.42 | - | 82977 | 0 | 82977
P00258 | 55 | -15 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.89 | -13.89 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 543.5 | 8.9 | 3.93 | - | 55881 | 0 | 55881
P00259 | 55 | -10 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8 | -11.17 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 219 | 1.5 | 5.23 | - | 22860 | 0 | 22860
P00260 | 55 | -16 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.4 | -14.54 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 602.1 | 10.9 | 3.79 | - | 61710 | 0 | 61710
P00261 | 62.5 | -20 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.18 | -14.85 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 854.6 | 23 | 3.15 | - | 82069 | 0 | 82069
P00262 | 62.5 | -15 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.86 | -13.86 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 569.2 | 10.1 | 3.53 | - | 55575 | 0 | 55575
P00263 | 62.5 | -10 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8.01 | -11.19 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 232 | 1.7 | 4.58 | - | 23027 | 0 | 23027
P00264 | 62.5 | -16 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.36 | -14.49 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 629.5 | 12.3 | 3.42 | - | 61263 | 0 | 61263
P00265 | 70 | -20 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.09 | -14.77 | 18.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 893.2 | 25.7 | 2.93 | - | 81071 | 0 | 81071
P00266 | 70 | -15 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.82 | -13.82 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 597 | 11.3 | 3.24 | - | 55143 | 0 | 55143
P00267 | 70 | -10 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8.03 | -11.2 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 246.8 | 1.9 | 4.12 | - | 23188 | 0 | 23188
P00268 | 70 | -16 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 650.7 | 13.7 | 3.1 | - | 59899 | 0 | 59899
P00269 | 56 | -20 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.25 | -14.92 | 19 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 824.4 | 20.9 | 3.38 | - | 82861 | 0 | 82861
P00270 | 56 | -15 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.88 | -13.88 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 546.7 | 9.1 | 3.87 | - | 55837 | 0 | 55837
P00271 | 56 | -10 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -8 | -11.18 | 11.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 220.6 | 1.5 | 5.12 | - | 22883 | 0 | 22883
P00272 | 56 | -16 | -6 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.39 | -14.53 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 605.6 | 11.1 | 3.73 | - | 61654 | 0 | 61654
P00285 | 47.5 | -20 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.94 | -14.62 | 18.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 847.2 | 20.6 | 3.89 | - | 90037 | 0 | 90037
P00286 | 47.5 | -15 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.66 | -13.66 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 560 | 9.1 | 4.56 | - | 60418 | 0 | 60418
P00288 | 47.5 | -16 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.13 | -14.13 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 619 | 11.1 | 4.34 | - | 66582 | 0 | 66582
P00289 | 55 | -20 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.86 | -14.54 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 879.9 | 22.9 | 3.46 | - | 89044 | 0 | 89044
P00290 | 55 | -15 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.62 | -13.62 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 583 | 10.1 | 3.84 | - | 59939 | 0 | 59939
P00291 | 55 | -10 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.9 | -11.09 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 236.4 | 1.7 | 5.05 | - | 24683 | 0 | 24683
P00292 | 55 | -16 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.1 | -14.1 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 645.1 | 12.4 | 3.71 | - | 66118 | 0 | 66118
P00293 | 62.5 | -20 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.77 | -14.44 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 913.8 | 25.4 | 3.17 | - | 87756 | 0 | 87756
P00294 | 62.5 | -15 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.59 | -13.59 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 609.5 | 11.4 | 3.46 | - | 59515 | 0 | 59515
P00295 | 62.5 | -10 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.92 | -11.11 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 250.8 | 1.9 | 4.43 | - | 24883 | 0 | 24883
P00296 | 62.5 | -16 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.03 | -14.03 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 670 | 13.7 | 3.37 | - | 65206 | 0 | 65206
P00297 | 70 | -20 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.62 | -14.29 | 17.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 945.7 | 28.2 | 2.92 | - | 85838 | 0 | 85838
P00298 | 70 | -15 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.55 | -13.55 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 638.9 | 12.8 | 3.18 | - | 59017 | 0 | 59017
P00299 | 70 | -10 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.93 | -11.12 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 266.5 | 2.1 | 3.99 | - | 25039 | 0 | 25039
P00300 | 70 | -16 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.98 | -13.98 | 15.5 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 701.7 | 15.4 | 3.11 | - | 64594 | 0 | 64594
P00301 | 56 | -20 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.85 | -14.53 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 884.5 | 23.2 | 3.41 | - | 88903 | 0 | 88903
P00302 | 56 | -15 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.62 | -13.62 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 586.4 | 10.3 | 3.78 | - | 59886 | 0 | 59886
P00303 | 56 | -10 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -7.9 | -11.1 | 11.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 238.1 | 1.7 | 4.95 | - | 24699 | 0 | 24699
P00304 | 56 | -16 | -6 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.09 | -14.09 | 15.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 648.8 | 12.6 | 3.65 | - | 66051 | 0 | 66051
P00317 | 47.5 | -20 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.23 | -15.92 | 20.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 707.2 | 15 | 4 | - | 75151 | 0 | 75151
P00318 | 47.5 | -15 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.39 | -14.53 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 456.3 | 6.1 | 4.84 | - | 49224 | 0 | 49224
P00320 | 47.5 | -16 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.99 | -15.42 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 508.3 | 7.8 | 4.6 | - | 54673 | 0 | 54673
P00321 | 55 | -20 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.16 | -15.84 | 20.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 735.9 | 16.8 | 3.55 | - | 74472 | 0 | 74472
P00322 | 55 | -15 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.37 | -14.51 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 476.9 | 7.1 | 4.09 | - | 49025 | 0 | 49025
P00323 | 55 | -10 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.18 | -11.32 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 190.4 | 1.2 | 5.56 | - | 19881 | 0 | 19881
P00324 | 55 | -16 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.96 | -15.37 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 530.8 | 8.7 | 3.93 | - | 54404 | 0 | 54404
P00325 | 62.5 | -20 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.02 | -15.7 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 762.2 | 18.8 | 3.21 | - | 73192 | 0 | 73192
P00326 | 62.5 | -15 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.35 | -14.48 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 500.5 | 8 | 3.67 | - | 48867 | 0 | 48867
P00327 | 62.5 | -10 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.19 | -11.34 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 201.8 | 1.4 | 4.88 | - | 20027 | 0 | 20027
P00328 | 62.5 | -16 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.93 | -15.31 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 555.7 | 9.8 | 3.54 | - | 54082 | 0 | 54082
P00329 | 70 | -20 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.92 | -15.6 | 20.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 796.6 | 21.1 | 2.98 | - | 72306 | 0 | 72306
P00330 | 70 | -15 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.33 | -14.46 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 527 | 9.1 | 3.35 | - | 48681 | 0 | 48681
P00331 | 70 | -10 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.16 | -11.31 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 210.1 | 1.5 | 4.33 | - | 19744 | 0 | 19744
P00332 | 70 | -16 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.89 | -15.25 | 16.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 583.9 | 11.1 | 3.25 | - | 53748 | 0 | 53748
P00333 | 56 | -20 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.15 | -15.83 | 20.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 740 | 17 | 3.51 | - | 74382 | 0 | 74382
P00334 | 56 | -15 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.37 | -14.5 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 479.9 | 7.2 | 4.02 | - | 49007 | 0 | 49007
P00335 | 56 | -10 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -8.18 | -11.33 | 12.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 191.9 | 1.3 | 5.45 | - | 19901 | 0 | 19901
P00336 | 56 | -16 | -6 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.96 | -15.36 | 16.9 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 534 | 8.9 | 3.87 | - | 54364 | 0 | 54364
P00355 | 47.5 | -20 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.95 | -14.37 | 33 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 860.4 | 20.1 | 4.12 | - | 91440 | 0 | 91440
P00356 | 47.5 | -15 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.96 | -12.51 | 25.2 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 665.4 | 11.1 | 4.94 | - | 71783 | 0 | 71783
P00360 | 47.5 | -16 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.58 | -13.11 | 26.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 705.4 | 12.7 | 4.71 | - | 75870 | 0 | 75870
P00361 | 55 | -20 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.84 | -14.26 | 32.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 896.2 | 22.5 | 3.63 | - | 90698 | 0 | 90698
P00362 | 55 | -15 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.89 | -12.44 | 25.1 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 693.8 | 12.6 | 4.09 | - | 71332 | 0 | 71332
P00363 | 55 | -10 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.68 | -9.77 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 482.1 | 5.8 | 4.94 | - | 50330 | 0 | 50330
P00364 | 55 | -5 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3.03 | -7.15 | 13.9 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 249.3 | 1.4 | 6.5 | - | 26420 | 0 | 26420
P00366 | 55 | -16 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.52 | -13.05 | 26.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 736.4 | 14.4 | 3.97 | - | 75472 | 0 | 75472
P00367 | 62.5 | -20 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.71 | -14.13 | 32.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 935.6 | 25.3 | 3.33 | - | 89843 | 0 | 89843
P00368 | 62.5 | -15 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.83 | -12.39 | 24.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 726.6 | 14.3 | 3.66 | - | 70946 | 0 | 70946
P00369 | 62.5 | -10 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.67 | -9.76 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 506.5 | 6.7 | 4.26 | - | 50258 | 0 | 50258
P00370 | 62.5 | -5 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 259.8 | 1.5 | 5.44 | - | 26184 | 0 | 26184
P00371 | 62.5 | 0 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 21.3 | 0.1 | 12.83 | - | 2183 | 0 | 2183
P00372 | 62.5 | -16 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.44 | -12.98 | 26.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 770.4 | 16.2 | 3.57 | - | 74971 | 0 | 74971
P00373 | 70 | -20 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.49 | -13.92 | 31.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 974.2 | 28.2 | 3.09 | - | 88421 | 0 | 88421
P00374 | 70 | -15 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.77 | -12.33 | 24.8 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 763.8 | 16.2 | 3.36 | - | 70557 | 0 | 70557
P00375 | 70 | -10 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.62 | -9.72 | 18.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 530.9 | 7.6 | 3.84 | - | 49888 | 0 | 49888
P00376 | 70 | -5 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -3.01 | -7.13 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 274.9 | 1.7 | 4.79 | - | 26267 | 0 | 26267
P00377 | 70 | 0 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | 0.68 | -4.69 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 21.8 | 0.1 | 12.27 | - | 2113 | 0 | 2113
P00378 | 70 | -16 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.37 | -12.9 | 26.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 809.2 | 18.4 | 3.29 | - | 74490 | 0 | 74490
P00379 | 56 | -20 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.83 | -14.25 | 32.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 901.3 | 22.8 | 3.58 | - | 90591 | 0 | 90591
P00380 | 56 | -15 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.88 | -12.43 | 25.1 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 698 | 12.8 | 4.02 | - | 71284 | 0 | 71284
P00381 | 56 | -10 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.68 | -9.77 | 18.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 485.2 | 6 | 4.82 | - | 50323 | 0 | 50323
P00382 | 56 | -5 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.99 | -7.12 | 13.8 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 248 | 1.4 | 6.31 | - | 26111 | 0 | 26111
P00384 | 56 | -16 | 1 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.51 | -13.04 | 26.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 740.8 | 14.6 | 3.91 | - | 75414 | 0 | 75414
P00403 | 47.5 | -20 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.74 | -14.41 | 29.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 965.4 | 24.5 | 4.07 | - | 102594 | 0 | 102594
P00404 | 47.5 | -15 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.12 | -11.75 | 23.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 755.3 | 14 | 4.8 | - | 81486 | 0 | 81486
P00408 | 47.5 | -16 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.68 | -12.25 | 24.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 799.5 | 15.9 | 4.59 | - | 85993 | 0 | 85993
P00409 | 55 | -20 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.56 | -14.19 | 29.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 999.1 | 27 | 3.61 | - | 101106 | 0 | 101106
P00410 | 55 | -15 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.05 | -11.69 | 23.3 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 787 | 15.8 | 3.96 | - | 80906 | 0 | 80906
P00411 | 55 | -10 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.16 | -9.38 | 18.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 551.5 | 7.4 | 4.71 | - | 57579 | 0 | 57579
P00412 | 55 | -5 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.73 | -6.94 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 283.2 | 1.6 | 6.13 | - | 30007 | 0 | 30007
P00414 | 55 | -16 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.6 | -12.18 | 24.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 832.4 | 17.9 | 3.87 | - | 85309 | 0 | 85309
P00415 | 62.5 | -20 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.61 | -14.24 | 29.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1056.6 | 31.2 | 3.28 | - | 101467 | 0 | 101467
P00416 | 62.5 | -15 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.98 | -11.62 | 23.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 822.3 | 17.7 | 3.56 | - | 80288 | 0 | 80288
P00417 | 62.5 | -10 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.13 | -9.35 | 18 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 578 | 8.5 | 4.08 | - | 57351 | 0 | 57351
P00418 | 62.5 | -5 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.74 | -6.95 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 298.4 | 1.8 | 5.11 | - | 30076 | 0 | 30076
P00419 | 62.5 | 0 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 23.7 | 0.1 | 12.34 | - | 2388 | 0 | 2388
P00420 | 62.5 | -16 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.54 | -12.12 | 24.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 871.5 | 20.1 | 3.49 | - | 84814 | 0 | 84814
P00421 | 70 | -20 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.4 | -14 | 28.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1099.6 | 34.7 | 3.05 | - | 99805 | 0 | 99805
P00422 | 70 | -15 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.91 | -11.57 | 23 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 863.5 | 20.1 | 3.27 | - | 79764 | 0 | 79764
P00423 | 70 | -10 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.07 | -9.31 | 17.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 605 | 9.5 | 3.69 | - | 56853 | 0 | 56853
P00424 | 70 | -5 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.75 | -6.95 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 315.6 | 2.1 | 4.51 | - | 30150 | 0 | 30150
P00425 | 70 | 0 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | 0.65 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 29.1 | 0.1 | 11.31 | - | 2777 | 0 | 2777
P00426 | 70 | -16 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.43 | -12.02 | 24.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 912 | 22.7 | 3.21 | - | 83956 | 0 | 83956
P00427 | 56 | -20 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.54 | -14.16 | 29 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1003.8 | 27.5 | 3.54 | - | 100937 | 0 | 100937
P00428 | 56 | -15 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.04 | -11.68 | 23.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 791.6 | 16 | 3.9 | - | 80839 | 0 | 80839
P00429 | 56 | -10 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.15 | -9.37 | 18.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 554.9 | 7.6 | 4.6 | - | 57551 | 0 | 57551
P00430 | 56 | -5 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.73 | -6.94 | 13.5 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 285.1 | 1.7 | 5.95 | - | 30016 | 0 | 30016
P00432 | 56 | -16 | 1 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.6 | -12.18 | 24.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 838 | 18.2 | 3.81 | - | 85309 | 0 | 85309
P00451 | 47.5 | -20 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.85 | -13.39 | 27.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1069.7 | 29.3 | 4.04 | - | 113684 | 0 | 113684
P00456 | 47.5 | -16 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.87 | -11.53 | 22.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 880.4 | 18.9 | 4.53 | - | 94695 | 0 | 94695
P00457 | 55 | -20 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.75 | -13.29 | 27.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1113.7 | 32.8 | 3.54 | - | 112708 | 0 | 112708
P00458 | 55 | -15 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.3 | -11.05 | 21.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 867.6 | 18.8 | 3.89 | - | 89197 | 0 | 89197
P00459 | 55 | -10 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.67 | -9.02 | 17.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 612.9 | 9 | 4.56 | - | 63989 | 0 | 63989
P00460 | 55 | -5 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.57 | -6.84 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 323.4 | 1.9 | 5.95 | - | 34273 | 0 | 34273
P00462 | 55 | -16 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.79 | -11.46 | 22.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 915.9 | 21.1 | 3.8 | - | 93873 | 0 | 93873
P00463 | 62.5 | -20 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.63 | -13.17 | 26.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1162.1 | 36.8 | 3.24 | - | 111599 | 0 | 111599
P00464 | 62.5 | -15 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.22 | -10.98 | 21.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 905.3 | 21.1 | 3.49 | - | 88389 | 0 | 88389
P00465 | 62.5 | -10 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.54 | -8.92 | 17.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 632.2 | 10.1 | 3.92 | - | 62739 | 0 | 62739
P00466 | 62.5 | -5 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.51 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 334.2 | 2.3 | 4.9 | - | 33692 | 0 | 33692
P00467 | 62.5 | 0 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.7 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 28.2 | 0.1 | 11.79 | - | 2881 | 0 | 2881
P00468 | 62.5 | -16 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.72 | -11.41 | 22.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 958.5 | 23.8 | 3.45 | - | 93279 | 0 | 93279
P00469 | 70 | -20 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.44 | -12.97 | 26.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1209 | 40.8 | 3.03 | - | 109735 | 0 | 109735
P00470 | 70 | -15 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.14 | -10.92 | 21.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 949.2 | 23.7 | 3.22 | - | 87676 | 0 | 87676
P00471 | 70 | -10 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.51 | -8.9 | 17.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 663.9 | 11.4 | 3.54 | - | 62381 | 0 | 62381
P00472 | 70 | -5 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 353.2 | 2.8 | 4.33 | - | 33743 | 0 | 33743
P00473 | 70 | 0 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | 0.7 | -4.67 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 29.5 | 0.1 | 11.09 | - | 2858 | 0 | 2858
P00474 | 70 | -16 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.56 | -11.27 | 22.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 996.1 | 26.4 | 3.19 | - | 91694 | 0 | 91694
P00475 | 56 | -20 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.73 | -13.27 | 27 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1119.8 | 33.3 | 3.5 | - | 112560 | 0 | 112560
P00476 | 56 | -15 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.29 | -11.04 | 21.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 872.5 | 19.1 | 3.82 | - | 89109 | 0 | 89109
P00477 | 56 | -10 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.67 | -9.02 | 17.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 616.6 | 9.2 | 4.46 | - | 63951 | 0 | 63951
P00478 | 56 | -5 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.5 | -6.79 | 13.2 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 318.6 | 2 | 5.69 | - | 33548 | 0 | 33548
P00480 | 56 | -16 | 1 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.78 | -11.45 | 22.7 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 921.3 | 21.5 | 3.75 | - | 93797 | 0 | 93797
P00499 | 47.5 | -20 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -10.12 | -12.66 | 25.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1165.7 | 33.5 | 4.08 | - | 123881 | 0 | 123881
P00504 | 47.5 | -16 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.17 | -10.94 | 21.5 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 949 | 21.4 | 4.54 | - | 102075 | 0 | 102075
P00505 | 55 | -20 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.94 | -12.49 | 25.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1203.4 | 37.5 | 3.53 | - | 121786 | 0 | 121786
P00506 | 55 | -15 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.65 | -10.52 | 20.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 936.8 | 21.4 | 3.85 | - | 96306 | 0 | 96306
P00507 | 55 | -10 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.19 | -8.67 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 659.8 | 10.5 | 4.39 | - | 68880 | 0 | 68880
P00508 | 55 | -5 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.24 | -6.61 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 340.3 | 2.3 | 6.13 | - | 36063 | 0 | 36063
P00510 | 55 | -16 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.08 | -10.87 | 21.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 986 | 24 | 3.79 | - | 101055 | 0 | 101055
P00511 | 62.5 | -20 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.79 | -12.35 | 24.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1251.7 | 41.7 | 3.22 | - | 120197 | 0 | 120197
P00512 | 62.5 | -15 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.55 | -10.44 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 975.4 | 23.9 | 3.47 | - | 95233 | 0 | 95233
P00513 | 62.5 | -10 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.15 | -8.64 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 690.2 | 11.8 | 3.81 | - | 68491 | 0 | 68491
P00514 | 62.5 | -5 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.31 | -6.66 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 365.5 | 3 | 4.73 | - | 36844 | 0 | 36844
P00515 | 62.5 | 0 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 30.5 | 0.1 | 11.43 | - | 3123 | 0 | 3123
P00516 | 62.5 | -16 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.09 | -10.88 | 21.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1040.3 | 27.4 | 3.41 | - | 101244 | 0 | 101244
P00517 | 70 | -20 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.65 | -12.22 | 24.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1307.1 | 46.7 | 3 | - | 118634 | 0 | 118634
P00518 | 70 | -15 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.55 | -10.44 | 20.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1030.1 | 27.3 | 3.19 | - | 95151 | 0 | 95151
P00519 | 70 | -10 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.08 | -8.59 | 16.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 720.2 | 13.2 | 3.47 | - | 67677 | 0 | 67677
P00520 | 70 | -5 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.31 | -6.66 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 385.9 | 3.6 | 4.18 | - | 36870 | 0 | 36870
P00521 | 70 | 0 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 32.8 | 0.1 | 10.6 | - | 3138 | 0 | 3138
P00522 | 70 | -16 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.99 | -10.8 | 21.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1087.6 | 30.9 | 3.14 | - | 100115 | 0 | 100115
P00523 | 56 | -20 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.92 | -12.47 | 25.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1210.1 | 38 | 3.48 | - | 121630 | 0 | 121630
P00524 | 56 | -15 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.64 | -10.51 | 20.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 941.8 | 21.7 | 3.79 | - | 96185 | 0 | 96185
P00525 | 56 | -10 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.18 | -8.66 | 16.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 663.6 | 10.6 | 4.29 | - | 68832 | 0 | 68832
P00526 | 56 | -5 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.31 | -6.65 | 13 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 349.5 | 2.5 | 5.51 | - | 36796 | 0 | 36796
P00528 | 56 | -16 | 1 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.05 | -10.85 | 21.3 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 990.2 | 24.2 | 3.73 | - | 100810 | 0 | 100810
P00547 | 47.5 | -20 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.36 | -11.96 | 23.9 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1231.4 | 37.4 | 4.04 | - | 130864 | 0 | 130864
P00552 | 47.5 | -16 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.72 | -10.58 | 20.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 1024.2 | 24.6 | 4.49 | - | 110164 | 0 | 110164
P00553 | 55 | -20 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.23 | -11.84 | 23.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1276.7 | 41.6 | 3.5 | - | 129203 | 0 | 129203
P00554 | 55 | -15 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.09 | -10.09 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 993.6 | 23.6 | 3.86 | - | 102148 | 0 | 102148
P00555 | 55 | -10 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.89 | -8.45 | 16.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 712.2 | 11.8 | 4.39 | - | 74351 | 0 | 74351
P00556 | 55 | -5 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.09 | -6.51 | 12.8 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 368.5 | 2.9 | 5.95 | - | 39046 | 0 | 39046
P00558 | 55 | -16 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.66 | -10.53 | 20.6 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1067 | 27.6 | 3.74 | - | 109351 | 0 | 109351
P00559 | 62.5 | -20 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.08 | -11.72 | 23.3 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1326.6 | 46.1 | 3.21 | - | 127392 | 0 | 127392
P00560 | 62.5 | -15 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.14 | -10.14 | 19.7 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1053.6 | 27.4 | 3.43 | - | 102871 | 0 | 102871
P00561 | 62.5 | -10 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.85 | -8.42 | 16.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 744.5 | 13.3 | 3.81 | - | 73879 | 0 | 73879
P00562 | 62.5 | -5 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 393.9 | 3.7 | 4.59 | - | 39702 | 0 | 39702
P00563 | 62.5 | 0 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.73 | -4.65 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 33.1 | 0.1 | 11.08 | - | 3383 | 0 | 3383
P00564 | 62.5 | -16 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.53 | -10.42 | 20.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1106.8 | 30.5 | 3.39 | - | 107710 | 0 | 107710
P00565 | 70 | -20 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.96 | -11.61 | 23.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1386.1 | 51.5 | 3 | - | 125806 | 0 | 125806
P00566 | 70 | -15 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.01 | -10.01 | 19.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1095.5 | 30.4 | 3.17 | - | 101196 | 0 | 101196
P00567 | 70 | -10 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.75 | -8.35 | 16 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 773.4 | 15 | 3.41 | - | 72675 | 0 | 72675
P00568 | 70 | -5 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 415.6 | 4.5 | 4.07 | - | 39702 | 0 | 39702
P00569 | 70 | 0 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | 0.72 | -4.66 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 36.4 | 0.2 | 10.27 | - | 3536 | 0 | 3536
P00570 | 70 | -16 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.49 | -10.39 | 20.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1165 | 34.8 | 3.11 | - | 107242 | 0 | 107242
P00571 | 56 | -20 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.21 | -11.83 | 23.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1283.4 | 42.2 | 3.46 | - | 128997 | 0 | 128997
P00572 | 56 | -15 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.08 | -10.08 | 19.6 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 999.1 | 24 | 3.79 | - | 102036 | 0 | 102036
P00573 | 56 | -10 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.88 | -8.45 | 16.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 716.3 | 12 | 4.28 | - | 74291 | 0 | 74291
P00574 | 56 | -5 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -2.14 | -6.55 | 12.9 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 377.1 | 3.2 | 5.36 | - | 39702 | 0 | 39702
P00576 | 56 | -16 | 1 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.65 | -10.52 | 20.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1072.9 | 28 | 3.68 | - | 109230 | 0 | 109230
P00595 | 47.5 | -20 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.35 | -13.94 | 28.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1033.2 | 27.1 | 4.12 | - | 109801 | 0 | 109801
P00600 | 47.5 | -16 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.27 | -11.88 | 23.7 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 848.8 | 17.7 | 4.55 | - | 91298 | 0 | 91298
P00601 | 55 | -20 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.13 | -13.7 | 28 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1066.1 | 30.4 | 3.56 | - | 107889 | 0 | 107889
P00602 | 55 | -15 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.67 | -11.36 | 22.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 836 | 17.6 | 3.91 | - | 85945 | 0 | 85945
P00603 | 55 | -10 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.81 | -9.12 | 17.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 579.7 | 8.3 | 4.57 | - | 60518 | 0 | 60518
P00604 | 55 | -5 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.59 | -6.85 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 301.2 | 1.8 | 6 | - | 31918 | 0 | 31918
P00606 | 55 | -16 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.15 | -11.78 | 23.5 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 880.8 | 19.7 | 3.83 | - | 90269 | 0 | 90269
P00607 | 62.5 | -20 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.05 | -13.6 | 27.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1115.6 | 34.1 | 3.27 | - | 107127 | 0 | 107127
P00608 | 62.5 | -15 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.56 | -11.26 | 22.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 870.1 | 19.6 | 3.52 | - | 84956 | 0 | 84956
P00609 | 62.5 | -10 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.78 | -9.1 | 17.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 607.5 | 9.4 | 3.96 | - | 60278 | 0 | 60278
P00610 | 62.5 | -5 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.61 | -6.86 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 317.8 | 2 | 4.99 | - | 32036 | 0 | 32036
P00611 | 62.5 | 0 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.69 | -4.68 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 26.7 | 0.1 | 12.03 | - | 2770 | 0 | 2770
P00612 | 62.5 | -16 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.05 | -11.68 | 23.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 917.7 | 22.1 | 3.46 | - | 89308 | 0 | 89308
P00613 | 70 | -20 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.88 | -13.42 | 27.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1163.4 | 38.2 | 3.03 | - | 105590 | 0 | 105590
P00614 | 70 | -15 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.45 | -11.18 | 22.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 909.5 | 22 | 3.24 | - | 84017 | 0 | 84017
P00615 | 70 | -10 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.74 | -9.06 | 17.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 637.1 | 10.6 | 3.57 | - | 59865 | 0 | 59865
P00616 | 70 | -5 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.63 | -6.88 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 337.8 | 2.4 | 4.39 | - | 32276 | 0 | 32276
P00617 | 70 | 0 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | 0.67 | -4.7 | 10.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 30.4 | 0.1 | 11.1 | - | 2954 | 0 | 2954
P00618 | 70 | -16 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.94 | -11.59 | 23.1 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 960.1 | 24.8 | 3.19 | - | 88382 | 0 | 88382
P00619 | 56 | -20 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.12 | -13.68 | 28 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1072.2 | 30.9 | 3.51 | - | 107769 | 0 | 107769
P00620 | 56 | -15 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.66 | -11.35 | 22.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 840.7 | 17.8 | 3.85 | - | 85860 | 0 | 85860
P00621 | 56 | -10 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.81 | -9.12 | 17.5 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 583.2 | 8.4 | 4.46 | - | 60489 | 0 | 60489
P00622 | 56 | -5 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.59 | -6.85 | 13.4 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 303.3 | 1.8 | 5.81 | - | 31934 | 0 | 31934
P00624 | 56 | -16 | 1 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.14 | -11.77 | 23.5 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 885.6 | 20 | 3.77 | - | 90163 | 0 | 90163
P00646 | 47.5 | -20 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.72 | -12.6 | 44.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1125.2 | 30.3 | 4.25 | - | 119578 | 0 | 119578
P00652 | 47.5 | -16 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.29 | -10.52 | 35.6 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 967.3 | 20.7 | 4.86 | - | 104050 | 0 | 104050
P00653 | 55 | -20 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.59 | -12.48 | 43.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1173.3 | 34.1 | 3.7 | - | 118739 | 0 | 118739
P00654 | 55 | -15 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.62 | -10 | 33.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 970.5 | 21.3 | 4.1 | - | 99776 | 0 | 99776
P00655 | 55 | -10 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.62 | -7.8 | 25.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 771.8 | 12.7 | 4.68 | - | 80573 | 0 | 80573
P00656 | 55 | -5 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.18 | -5.48 | 19.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 553.1 | 6.1 | 6.22 | - | 58608 | 0 | 58608
P00659 | 55 | -16 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.16 | -10.41 | 35.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1006.8 | 23.2 | 4.04 | - | 103188 | 0 | 103188
P00660 | 62.5 | -20 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.42 | -12.33 | 42.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1225.6 | 38.5 | 3.38 | - | 117692 | 0 | 117692
P00661 | 62.5 | -15 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.61 | -9.99 | 33.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1021.4 | 24.5 | 3.66 | - | 99727 | 0 | 99727
P00662 | 62.5 | -10 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.5 | -7.72 | 25.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 804.2 | 14.3 | 4.03 | - | 79799 | 0 | 79799
P00663 | 62.5 | -5 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.24 | -5.51 | 19.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 585 | 7.2 | 4.75 | - | 58967 | 0 | 58967
P00664 | 62.5 | 0 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.27 | -3.27 | 14.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 357.6 | 2.3 | 6.08 | - | 36593 | 0 | 36593
P00666 | 62.5 | -16 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.16 | -10.41 | 35.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1060.3 | 27.1 | 3.56 | - | 103188 | 0 | 103188
P00667 | 70 | -20 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.16 | -12.09 | 41.9 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1278.4 | 43 | 3.15 | - | 116028 | 0 | 116028
P00668 | 70 | -15 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.44 | -9.86 | 33 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1067.9 | 27.9 | 3.32 | - | 98644 | 0 | 98644
P00669 | 70 | -10 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.42 | -7.66 | 25.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 844.2 | 16.3 | 3.63 | - | 79323 | 0 | 79323
P00670 | 70 | -5 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.21 | -5.49 | 19.4 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 615.2 | 8.2 | 4.17 | - | 58770 | 0 | 58770
P00671 | 70 | 0 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.34 | -3.23 | 14.8 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 372.3 | 2.8 | 5.13 | - | 36128 | 0 | 36128
P00672 | 70 | 5 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 6.2 | -0.87 | 11.3 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 116.7 | 0.4 | 7.87 | - | 11504 | 0 | 11504
P00673 | 70 | -16 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.02 | -10.3 | 34.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1111.3 | 30.8 | 3.27 | - | 102294 | 0 | 102294
P00674 | 56 | -20 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.57 | -12.46 | 43.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1180 | 34.7 | 3.65 | - | 118612 | 0 | 118612
P00675 | 56 | -15 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.6 | -9.98 | 33.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 975.9 | 21.7 | 4.03 | - | 99663 | 0 | 99663
P00676 | 56 | -10 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.61 | -7.79 | 25.9 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 776.4 | 12.9 | 4.56 | - | 80522 | 0 | 80522
P00677 | 56 | -5 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.26 | -5.53 | 19.5 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 561.4 | 6.4 | 5.71 | - | 59113 | 0 | 59113
P00680 | 56 | -16 | 8 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.29 | -10.52 | 35.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1022.2 | 24.2 | 3.94 | - | 104067 | 0 | 104067
P00702 | 47.5 | -20 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -9.25 | -11.25 | 38.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1273.5 | 37.7 | 4.22 | - | 135339 | 0 | 135339
P00709 | 55 | -20 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -9.1 | -11.17 | 38.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1326 | 42.3 | 3.66 | - | 134187 | 0 | 134187
P00710 | 55 | -15 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.53 | -9.17 | 30.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1108.9 | 27 | 4.02 | - | 114009 | 0 | 114009
P00711 | 55 | -10 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.62 | -7.11 | 23.8 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 873.4 | 15.8 | 4.56 | - | 91183 | 0 | 91183
P00712 | 55 | -5 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.54 | -5.06 | 18.4 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 632.3 | 7.8 | 5.96 | - | 67010 | 0 | 67010
P00715 | 55 | -16 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.96 | -9.5 | 31.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1145.6 | 29.9 | 3.89 | - | 117409 | 0 | 117409
P00716 | 62.5 | -20 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.92 | -11.02 | 37.6 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1382.7 | 47.4 | 3.34 | - | 132776 | 0 | 132776
P00717 | 62.5 | -15 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.34 | -9.03 | 30 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1152.3 | 30.7 | 3.55 | - | 112514 | 0 | 112514
P00718 | 62.5 | -10 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.53 | -7.05 | 23.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 911.7 | 17.9 | 3.92 | - | 90465 | 0 | 90465
P00719 | 62.5 | -5 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.59 | -5.1 | 18.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 668.6 | 9.1 | 4.55 | - | 67396 | 0 | 67396
P00720 | 62.5 | 0 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.71 | -3 | 14.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 405.6 | 3.5 | 5.71 | - | 41500 | 0 | 41500
P00722 | 62.5 | -16 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.88 | -9.44 | 31.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1199.8 | 33.8 | 3.5 | - | 116765 | 0 | 116765
P00723 | 70 | -20 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.64 | -10.8 | 36.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1438.8 | 52.7 | 3.12 | - | 130584 | 0 | 130584
P00724 | 70 | -15 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.23 | -8.95 | 29.7 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1208.6 | 34.8 | 3.26 | - | 111639 | 0 | 111639
P00725 | 70 | -10 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.44 | -6.99 | 23.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 955.5 | 20.3 | 3.55 | - | 89779 | 0 | 89779
P00726 | 70 | -5 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.56 | -5.07 | 18.4 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 702.5 | 10.4 | 4 | - | 67114 | 0 | 67114
P00727 | 70 | 0 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.68 | -3.02 | 14.5 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 430.2 | 4 | 4.84 | - | 41748 | 0 | 41748
P00728 | 70 | 5 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 6.31 | -0.81 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 134.5 | 0.5 | 7.35 | - | 13265 | 0 | 13265
P00729 | 70 | -16 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.72 | -9.32 | 31 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1255.1 | 38.2 | 3.21 | - | 115532 | 0 | 115532
P00730 | 56 | -20 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -9.08 | -11.15 | 38.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1333.3 | 42.9 | 3.61 | - | 134016 | 0 | 134016
P00731 | 56 | -15 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.52 | -9.17 | 30.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1115.4 | 27.5 | 3.94 | - | 113912 | 0 | 113912
P00732 | 56 | -10 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.61 | -7.11 | 23.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 878.4 | 16.1 | 4.45 | - | 91107 | 0 | 91107
P00733 | 56 | -5 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.62 | -5.11 | 18.5 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 642.1 | 8.1 | 5.47 | - | 67608 | 0 | 67608
P00736 | 56 | -16 | 8 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.96 | -9.5 | 31.7 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1153.3 | 30.4 | 3.83 | - | 117409 | 0 | 117409
P00758 | 47.5 | -20 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.95 | -10.26 | 34.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1404.1 | 44.6 | 4.24 | - | 149214 | 0 | 149214
P00765 | 55 | -20 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.8 | -10.14 | 34.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1460.4 | 49.9 | 3.64 | - | 147792 | 0 | 147792
P00766 | 55 | -15 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.5 | -8.42 | 27.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1227.6 | 32.4 | 3.97 | - | 126203 | 0 | 126203
P00767 | 55 | -10 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.74 | -6.51 | 22.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 961.9 | 18.7 | 4.51 | - | 100422 | 0 | 100422
P00768 | 55 | -5 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.02 | -4.7 | 17.5 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 703.7 | 9.4 | 5.79 | - | 74567 | 0 | 74567
P00771 | 55 | -16 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.99 | -8.78 | 29.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1276.4 | 35.7 | 3.89 | - | 130814 | 0 | 130814
P00772 | 62.5 | -20 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.61 | -9.99 | 33.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1520.4 | 55.7 | 3.33 | - | 146001 | 0 | 146001
P00773 | 62.5 | -15 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.38 | -8.38 | 27.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1281.7 | 36.6 | 3.54 | - | 125142 | 0 | 125142
P00774 | 62.5 | -10 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.66 | -6.46 | 21.9 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1004.7 | 21.2 | 3.87 | - | 99694 | 0 | 99694
P00775 | 62.5 | -5 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -0.03 | -4.73 | 17.6 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 744.6 | 11.1 | 4.42 | - | 75054 | 0 | 75054
P00776 | 62.5 | 0 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 2.99 | -2.82 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 457.8 | 4.3 | 5.46 | - | 46842 | 0 | 46842
P00778 | 62.5 | -16 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.77 | -8.62 | 28.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1323.1 | 40.2 | 3.46 | - | 128763 | 0 | 128763
P00779 | 70 | -20 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.33 | -9.77 | 32.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1579.4 | 61.6 | 3.11 | - | 143347 | 0 | 143347
P00780 | 70 | -15 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.17 | -8.17 | 27.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1333.5 | 41.3 | 3.23 | - | 123182 | 0 | 123182
P00781 | 70 | -10 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.69 | -6.48 | 22 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1063.8 | 24.5 | 3.49 | - | 99961 | 0 | 99961
P00782 | 70 | -5 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.02 | -4.7 | 17.5 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 780.6 | 12.6 | 3.89 | - | 74574 | 0 | 74574
P00783 | 70 | 0 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 2.98 | -2.83 | 14.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 483.1 | 4.9 | 4.64 | - | 46884 | 0 | 46884
P00784 | 70 | 5 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 6.42 | -0.74 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 150.2 | 0.6 | 7.01 | - | 14805 | 0 | 14805
P00785 | 70 | -16 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.61 | -8.5 | 28.2 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1382.9 | 45.2 | 3.18 | - | 127301 | 0 | 127301
P00786 | 56 | -20 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.78 | -10.12 | 34 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1468.2 | 50.7 | 3.59 | - | 147574 | 0 | 147574
P00787 | 56 | -15 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.48 | -8.41 | 27.9 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1234.5 | 33 | 3.9 | - | 126074 | 0 | 126074
P00788 | 56 | -10 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.72 | -6.5 | 22 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 966.3 | 19 | 4.39 | - | 100227 | 0 | 100227
P00789 | 56 | -5 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -0.06 | -4.75 | 17.7 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 715.2 | 9.9 | 5.32 | - | 75302 | 0 | 75302
P00792 | 56 | -16 | 8 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.97 | -8.76 | 29.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1283.5 | 36.3 | 3.82 | - | 130666 | 0 | 130666
P00814 | 47.5 | -20 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.74 | -9.33 | 31.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1506.2 | 50.9 | 4.25 | - | 160066 | 0 | 160066
P00821 | 55 | -20 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.58 | -9.21 | 30.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1563.9 | 56.8 | 3.61 | - | 158268 | 0 | 158268
P00822 | 55 | -15 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.54 | -7.75 | 25.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1324.1 | 37.6 | 3.91 | - | 136126 | 0 | 136126
P00823 | 55 | -10 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.18 | -6.18 | 21.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1058.8 | 22.3 | 4.43 | - | 110540 | 0 | 110540
P00827 | 55 | -16 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -5.08 | -8.08 | 26.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1385.3 | 41.2 | 3.88 | - | 141982 | 0 | 141982
P00828 | 62.5 | -20 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.38 | -9.06 | 30.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1625.8 | 63 | 3.29 | - | 156123 | 0 | 156123
P00829 | 62.5 | -15 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.4 | -7.65 | 25.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1378.4 | 42.1 | 3.48 | - | 134591 | 0 | 134591
P00830 | 62.5 | -10 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.13 | -6.13 | 21 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1107.6 | 25.3 | 3.79 | - | 109913 | 0 | 109913
P00831 | 62.5 | -5 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.49 | -4.4 | 16.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 808.3 | 12.9 | 4.32 | - | 81481 | 0 | 81481
P00832 | 62.5 | 0 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.26 | -2.65 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 502.4 | 5 | 5.31 | - | 51402 | 0 | 51402
P00834 | 62.5 | -16 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.82 | -7.94 | 26.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1430.6 | 46.1 | 3.43 | - | 139220 | 0 | 139220
P00835 | 70 | -20 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.17 | -8.91 | 29.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1694.7 | 70.2 | 3.06 | - | 153818 | 0 | 153818
P00836 | 70 | -15 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.25 | -7.55 | 25.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1439.7 | 47.3 | 3.2 | - | 132988 | 0 | 132988
P00837 | 70 | -10 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.05 | -6.05 | 20.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1160.9 | 28.7 | 3.43 | - | 109088 | 0 | 109088
P00838 | 70 | -5 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.54 | -4.37 | 16.9 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 847.4 | 14.6 | 3.83 | - | 80960 | 0 | 80960
P00839 | 70 | 0 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.28 | -2.64 | 13.9 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 527.7 | 5.8 | 4.49 | - | 51215 | 0 | 51215
P00840 | 70 | 5 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 6.5 | -0.69 | 11.1 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 164.7 | 0.7 | 6.73 | - | 16243 | 0 | 16243
P00841 | 70 | -16 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.66 | -7.83 | 26 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1492.6 | 51.6 | 3.17 | - | 137394 | 0 | 137394
P00842 | 56 | -20 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.55 | -9.19 | 30.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1571.9 | 57.6 | 3.56 | - | 157999 | 0 | 157999
P00843 | 56 | -15 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.52 | -7.73 | 25.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1331.3 | 38.2 | 3.83 | - | 135962 | 0 | 135962
P00844 | 56 | -10 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.18 | -6.18 | 21.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1065.1 | 22.7 | 4.31 | - | 110468 | 0 | 110468
P00845 | 56 | -5 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.46 | -4.42 | 17 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 777.1 | 11.5 | 5.22 | - | 81821 | 0 | 81821
P00848 | 56 | -16 | 8 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -5.06 | -8.06 | 26.9 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1392.8 | 41.8 | 3.81 | - | 141792 | 0 | 141792
P00870 | 47.5 | -20 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.94 | -8.74 | 29 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1615.8 | 56.6 | 4.36 | - | 171711 | 0 | 171711
P00877 | 55 | -20 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.76 | -8.61 | 28.5 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1675 | 62.8 | 3.67 | - | 169512 | 0 | 169512
P00878 | 55 | -15 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.82 | -7.25 | 24.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1415.7 | 42.4 | 3.88 | - | 145547 | 0 | 145547
P00879 | 55 | -10 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.61 | -5.76 | 20.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1133.1 | 25.1 | 4.43 | - | 118299 | 0 | 118299
P00883 | 55 | -16 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.23 | -7.53 | 25 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1469.2 | 46.3 | 3.81 | - | 150577 | 0 | 150577
P00884 | 62.5 | -20 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.53 | -8.45 | 28 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1735.9 | 69.5 | 3.33 | - | 166695 | 0 | 166695
P00885 | 62.5 | -15 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.63 | -7.12 | 23.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1466.5 | 46.8 | 3.48 | - | 143193 | 0 | 143193
P00886 | 62.5 | -10 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.53 | -5.71 | 20 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1183.1 | 28.5 | 3.75 | - | 117398 | 0 | 117398
P00887 | 62.5 | -5 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 0.91 | -4.09 | 16.4 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 865.3 | 14.5 | 4.27 | - | 87226 | 0 | 87226
P00888 | 62.5 | 0 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.49 | -2.51 | 13.7 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 542.3 | 5.8 | 5.15 | - | 55492 | 0 | 55492
P00890 | 62.5 | -16 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.1 | -7.44 | 24.8 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1531.1 | 51.8 | 3.42 | - | 149003 | 0 | 149003
P00891 | 70 | -20 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.21 | -8.21 | 27.2 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1793.1 | 77 | 3.07 | - | 162747 | 0 | 162747
P00892 | 70 | -15 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.55 | -7.07 | 23.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1540.3 | 53.1 | 3.18 | - | 142280 | 0 | 142280
P00893 | 70 | -10 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.46 | -5.66 | 19.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1239 | 32.3 | 3.4 | - | 116420 | 0 | 116420
P00894 | 70 | -5 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 0.96 | -4.09 | 16.4 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 906.7 | 16.4 | 3.78 | - | 86625 | 0 | 86625
P00895 | 70 | 0 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.53 | -2.47 | 13.6 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 567.1 | 6.5 | 4.4 | - | 55033 | 0 | 55033
P00896 | 70 | 5 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 6.57 | -0.65 | 11 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 178.2 | 0.7 | 6.49 | - | 17571 | 0 | 17571
P00897 | 70 | -16 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.88 | -7.29 | 24.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1589.5 | 57.4 | 3.16 | - | 146319 | 0 | 146319
P00898 | 56 | -20 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.72 | -8.58 | 28.4 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1680.5 | 63.6 | 3.6 | - | 168919 | 0 | 168919
P00899 | 56 | -15 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.8 | -7.24 | 24.1 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1423.3 | 43 | 3.81 | - | 145356 | 0 | 145356
P00900 | 56 | -10 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.6 | -5.75 | 20.1 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1139.7 | 25.5 | 4.3 | - | 118210 | 0 | 118210
P00904 | 56 | -16 | 8 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.14 | -7.47 | 24.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1468.9 | 46.5 | 3.77 | - | 149538 | 0 | 149538
P00926 | 47.5 | -20 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.47 | -10.66 | 36.1 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1343.6 | 41.3 | 4.23 | - | 142789 | 0 | 142789
P00933 | 55 | -20 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.31 | -10.54 | 35.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1397.2 | 46.3 | 3.65 | - | 141396 | 0 | 141396
P00934 | 55 | -15 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.83 | -8.66 | 28.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1165.8 | 30 | 3.96 | - | 119858 | 0 | 119858
P00935 | 55 | -10 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.15 | -6.79 | 22.9 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 925.8 | 17.5 | 4.52 | - | 96659 | 0 | 96659
P00936 | 55 | -5 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.2 | -4.84 | 17.9 | R290 (Propane) | Countercurrent | -5 | 0 | 55 | 60 | 670.3 | 8.6 | 5.86 | - | 71032 | 0 | 71032
P00939 | 55 | -16 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.51 | -9.16 | 30.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1227.2 | 33.3 | 3.9 | - | 125772 | 0 | 125772
P00940 | 62.5 | -20 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.05 | -10.33 | 34.8 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1448.6 | 51.8 | 3.31 | - | 139109 | 0 | 139109
P00941 | 62.5 | -15 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.79 | -8.63 | 28.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1224.5 | 34.2 | 3.52 | - | 119556 | 0 | 119556
P00942 | 62.5 | -10 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.06 | -6.73 | 22.7 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 966 | 19.8 | 3.88 | - | 95854 | 0 | 95854
P00943 | 62.5 | -5 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.25 | -4.88 | 17.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 709.4 | 10.2 | 4.48 | - | 71505 | 0 | 71505
P00944 | 62.5 | 0 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.88 | -2.89 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 433.8 | 3.9 | 5.56 | - | 44386 | 0 | 44386
P00946 | 62.5 | -16 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.24 | -8.96 | 29.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1268.3 | 37.3 | 3.47 | - | 123426 | 0 | 123426
P00947 | 70 | -20 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.82 | -10.15 | 34.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1511 | 58 | 3.07 | - | 137146 | 0 | 137146
P00948 | 70 | -15 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.59 | -8.49 | 28.1 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1275 | 38.2 | 3.24 | - | 117771 | 0 | 117771
P00949 | 70 | -10 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.08 | -6.74 | 22.7 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1021.4 | 22.8 | 3.51 | - | 95976 | 0 | 95976
P00950 | 70 | -5 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.2 | -4.84 | 17.9 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 744.1 | 11.6 | 3.94 | - | 71083 | 0 | 71083
P00951 | 70 | 0 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 2.87 | -2.9 | 14.3 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 457.8 | 4.5 | 4.72 | - | 44431 | 0 | 44431
P00952 | 70 | 5 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 6.37 | -0.77 | 11.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 142.9 | 0.6 | 7.18 | - | 14087 | 0 | 14087
P00953 | 70 | -16 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.07 | -8.83 | 29.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1324.4 | 41.9 | 3.2 | - | 121913 | 0 | 121913
P00954 | 56 | -20 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.29 | -10.52 | 35.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1404.7 | 46.9 | 3.6 | - | 141194 | 0 | 141194
P00955 | 56 | -15 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.82 | -8.65 | 28.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1172.5 | 30.4 | 3.89 | - | 119744 | 0 | 119744
P00956 | 56 | -10 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.15 | -6.79 | 22.8 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 931.2 | 17.8 | 4.41 | - | 96580 | 0 | 96580
P00957 | 56 | -5 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.28 | -4.89 | 18 | R290 (Propane) | Countercurrent | -5 | 0 | 56 | 60 | 681.5 | 9.1 | 5.39 | - | 71754 | 0 | 71754
P00960 | 56 | -16 | 8 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.5 | -9.15 | 30.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1234.2 | 33.9 | 3.83 | - | 125644 | 0 | 125644
P00985 | 47.5 | -20 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -8.53 | -9.94 | 57.6 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1380.4 | 41.9 | 4.38 | - | 146694 | 27 | 146667
P00993 | 55 | -20 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -8.26 | -9.73 | 56.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1432.7 | 46.8 | 3.77 | - | 144985 | 0 | 144985
P00994 | 55 | -15 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.58 | -7.78 | 44.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1247.7 | 32.2 | 4.12 | - | 128271 | 0 | 128271
P00995 | 55 | -10 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.62 | -5.78 | 34.7 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1051.7 | 20.7 | 4.74 | - | 109798 | 0 | 109798
P01000 | 55 | -16 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.16 | -8.16 | 46.9 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1286.8 | 35 | 4.03 | - | 131877 | 0 | 131877
P01001 | 62.5 | -20 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.99 | -9.53 | 55.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1492.8 | 52.6 | 3.42 | - | 143352 | 0 | 143352
P01002 | 62.5 | -15 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.43 | -7.68 | 44.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1303.9 | 36.5 | 3.66 | - | 127315 | 0 | 127315
P01003 | 62.5 | -10 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.55 | -5.73 | 34.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1102.1 | 23.7 | 4.03 | - | 109363 | 0 | 109363
P01004 | 62.5 | -5 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.72 | -3.63 | 26.5 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 882.4 | 14 | 4.6 | - | 88950 | 0 | 88950
P01005 | 62.5 | 0 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.09 | -1.56 | 20.8 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 664.4 | 7.5 | 5.52 | - | 67980 | 0 | 67980
P01008 | 62.5 | -16 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.02 | -8.1 | 46.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1346.6 | 39.6 | 3.61 | - | 131051 | 0 | 131051
P01009 | 70 | -20 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.71 | -9.32 | 53.7 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1559.6 | 59.1 | 3.18 | - | 141557 | 0 | 141557
P01010 | 70 | -15 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.3 | -7.59 | 43.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1369.9 | 41.5 | 3.36 | - | 126544 | 0 | 126544
P01011 | 70 | -10 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.4 | -5.63 | 34.1 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1153.8 | 26.9 | 3.63 | - | 108412 | 0 | 108412
P01012 | 70 | -5 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.87 | -3.54 | 26.2 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 921.8 | 16 | 4 | - | 88066 | 0 | 88066
P01013 | 70 | 0 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.11 | -1.55 | 20.8 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 699.3 | 8.6 | 4.62 | - | 67868 | 0 | 67868
P01014 | 70 | 5 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.76 | 0.61 | 16.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 457.3 | 3.6 | 5.77 | - | 45091 | 0 | 45091
P01015 | 70 | 10 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 11.59 | 2.77 | 12.5 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 60 | 212.2 | 0.7 | 7.83 | - | 21236 | 0 | 21236
P01016 | 70 | -16 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.82 | -7.95 | 45.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1409.8 | 44.9 | 3.31 | - | 129774 | 0 | 129774
P01017 | 56 | -20 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -8.23 | -9.71 | 56.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1440.6 | 47.5 | 3.72 | - | 144802 | 0 | 144802
P01018 | 56 | -15 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.54 | -7.76 | 44.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1253.5 | 32.7 | 4.04 | - | 128015 | 0 | 128015
P01019 | 56 | -10 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.61 | -5.77 | 34.7 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1058.2 | 21 | 4.61 | - | 109751 | 0 | 109751
P01024 | 56 | -16 | 15 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.13 | -8.13 | 46.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1293.6 | 35.5 | 3.96 | - | 131691 | 0 | 131691
P01049 | 47.5 | -20 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.6 | -8.5 | 48.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1556.4 | 51.5 | 4.45 | - | 165403 | 0 | 165403
P01057 | 55 | -20 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.35 | -8.35 | 47.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1615.9 | 57.7 | 3.75 | - | 163524 | 0 | 163524
P01058 | 55 | -15 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.01 | -6.71 | 39.1 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1415.9 | 40.4 | 4.06 | - | 145563 | 0 | 145563
P01059 | 55 | -10 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.38 | -4.97 | 31.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1201.1 | 26.3 | 4.64 | - | 125391 | 0 | 125391
P01064 | 55 | -16 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.57 | -7.09 | 41 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1462 | 43.7 | 4 | - | 149834 | 0 | 149834
P01065 | 62.5 | -20 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.1 | -8.1 | 46.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1682.7 | 64.4 | 3.41 | - | 161592 | 0 | 161592
P01066 | 62.5 | -15 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.84 | -6.59 | 38.5 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1477.5 | 45.6 | 3.61 | - | 144263 | 0 | 144263
P01067 | 62.5 | -10 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.29 | -4.92 | 31.1 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1257.1 | 30.1 | 3.94 | - | 124747 | 0 | 124747
P01068 | 62.5 | -5 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.96 | -2.86 | 24.2 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 990 | 17.3 | 4.47 | - | 99791 | 0 | 99791
P01069 | 62.5 | 0 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.84 | -1.1 | 19.8 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 760.2 | 9.6 | 5.3 | - | 77783 | 0 | 77783
P01072 | 62.5 | -16 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.4 | -6.97 | 40.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1526.3 | 49.3 | 3.57 | - | 148538 | 0 | 148538
P01073 | 70 | -20 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -5.78 | -7.92 | 45.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1753 | 71.8 | 3.17 | - | 159110 | 0 | 159110
P01074 | 70 | -15 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.68 | -6.49 | 38 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1548.7 | 51.4 | 3.32 | - | 143055 | 0 | 143055
P01075 | 70 | -10 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.12 | -4.81 | 30.7 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1313.8 | 34 | 3.56 | - | 123451 | 0 | 123451
P01076 | 70 | -5 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.82 | -2.95 | 24.5 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 1056.2 | 20.5 | 3.89 | - | 100904 | 0 | 100904
P01077 | 70 | 0 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.86 | -1.09 | 19.7 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 799.9 | 11.1 | 4.44 | - | 77635 | 0 | 77635
P01078 | 70 | 5 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.2 | 0.87 | 15.7 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 527.6 | 4.7 | 5.47 | - | 52019 | 0 | 52019
P01079 | 70 | 10 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 11.79 | 2.88 | 12.3 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 60 | 245.2 | 0.8 | 7.41 | - | 24543 | 0 | 24543
P01080 | 70 | -16 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.17 | -6.82 | 39.6 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1594.5 | 55.6 | 3.28 | - | 146777 | 0 | 146777
P01081 | 56 | -20 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.32 | -8.32 | 47.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1624.1 | 58.5 | 3.69 | - | 163251 | 0 | 163251
P01082 | 56 | -15 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.99 | -6.7 | 39 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1424 | 41 | 3.99 | - | 145428 | 0 | 145428
P01083 | 56 | -10 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.37 | -4.96 | 31.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1208.2 | 26.8 | 4.51 | - | 125317 | 0 | 125317
P01088 | 56 | -16 | 15 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.57 | -7.09 | 41 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1471.8 | 44.5 | 3.93 | - | 149834 | 0 | 149834
P01113 | 47.5 | -20 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -5.05 | -7.42 | 42.7 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1722 | 61.4 | 4.52 | - | 183003 | 0 | 183003
P01121 | 55 | -20 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.75 | -7.22 | 41.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1781.6 | 67.9 | 3.77 | - | 180298 | 0 | 180298
P01122 | 55 | -15 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.66 | -5.81 | 34.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1567.7 | 48.3 | 4.05 | - | 161174 | 0 | 161174
P01123 | 55 | -10 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | -0.27 | -4.27 | 28.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1334.8 | 31.9 | 4.6 | - | 139350 | 0 | 139350
P01128 | 55 | -16 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.1 | -6.1 | 36.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1611.3 | 52 | 3.98 | - | 165135 | 0 | 165135
P01129 | 62.5 | -20 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.48 | -7.03 | 40.7 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1851.8 | 75.5 | 3.43 | - | 177823 | 0 | 177823
P01130 | 62.5 | -15 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.49 | -5.69 | 34.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1634.3 | 54.2 | 3.59 | - | 159568 | 0 | 159568
P01131 | 62.5 | -10 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | -0.17 | -4.17 | 28.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1395.1 | 36.2 | 3.88 | - | 138441 | 0 | 138441
P01132 | 62.5 | -5 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.61 | -2.45 | 23.1 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 1121 | 21.8 | 4.35 | - | 112995 | 0 | 112995
P01133 | 62.5 | 0 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.51 | -0.7 | 18.9 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 845.7 | 11.7 | 5.16 | - | 86530 | 0 | 86530
P01136 | 62.5 | -16 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.96 | -5.96 | 35.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1684.1 | 58.4 | 3.56 | - | 163891 | 0 | 163891
P01137 | 70 | -20 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.15 | -6.81 | 39.5 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1925.9 | 83.9 | 3.17 | - | 174801 | 0 | 174801
P01138 | 70 | -15 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.2 | -5.51 | 33.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1699.3 | 61 | 3.28 | - | 156971 | 0 | 156971
P01139 | 70 | -10 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.03 | -4.07 | 27.8 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1453.6 | 41.2 | 3.47 | - | 136588 | 0 | 136588
P01140 | 70 | -5 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.67 | -2.42 | 23 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 1177.7 | 25 | 3.81 | - | 112508 | 0 | 112508
P01141 | 70 | 0 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.56 | -0.67 | 18.8 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 887 | 13.3 | 4.32 | - | 86084 | 0 | 86084
P01142 | 70 | 5 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.62 | 1.11 | 15.2 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 590.1 | 5.7 | 5.25 | - | 58184 | 0 | 58184
P01143 | 70 | 10 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 11.95 | 2.95 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 60 | 277.7 | 1 | 7.05 | - | 27790 | 0 | 27790
P01144 | 70 | -16 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.72 | -5.85 | 35 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1756.7 | 65.6 | 3.26 | - | 161705 | 0 | 161705
P01145 | 56 | -20 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.72 | -7.19 | 41.5 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1790.7 | 68.9 | 3.72 | - | 179994 | 0 | 179994
P01146 | 56 | -15 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.64 | -5.79 | 34.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1576.3 | 49.1 | 3.97 | - | 160978 | 0 | 160978
P01147 | 56 | -10 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | -0.26 | -4.26 | 28.5 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1342.5 | 32.5 | 4.46 | - | 139243 | 0 | 139243
P01152 | 56 | -16 | 15 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.08 | -6.08 | 36.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1620.7 | 52.9 | 3.9 | - | 164993 | 0 | 164993
P01185 | 55 | -20 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3.43 | -6.32 | 37.2 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1929.7 | 77.7 | 3.78 | - | 195287 | 0 | 195287
P01186 | 55 | -15 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.59 | -5.11 | 31.9 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1709 | 56.1 | 4.06 | - | 175704 | 0 | 175704
P01187 | 55 | -10 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.76 | -3.61 | 26.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1445.2 | 37.3 | 4.55 | - | 150878 | 0 | 150878
P01192 | 55 | -16 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.9 | -5.31 | 32.7 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1747.3 | 59.8 | 3.99 | - | 179079 | 0 | 179079
P01193 | 62.5 | -20 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3.17 | -6.17 | 36.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 2005 | 86.1 | 3.42 | - | 192542 | 0 | 192542
P01194 | 62.5 | -15 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.33 | -4.94 | 31.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1771.5 | 62.2 | 3.6 | - | 172966 | 0 | 172966
P01195 | 62.5 | -10 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.88 | -3.53 | 26.2 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1507.1 | 42.1 | 3.82 | - | 149555 | 0 | 149555
P01196 | 62.5 | -5 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.39 | -1.98 | 21.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 1220.4 | 25.5 | 4.28 | - | 123014 | 0 | 123014
P01197 | 62.5 | 0 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.12 | -0.35 | 18.1 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 919.5 | 13.5 | 5.08 | - | 94085 | 0 | 94085
P01200 | 62.5 | -16 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.7 | -5.18 | 32.2 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1818.3 | 66.7 | 3.55 | - | 176958 | 0 | 176958
P01201 | 70 | -20 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -2.81 | -5.9 | 35.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 2078.8 | 94.7 | 3.19 | - | 188680 | 0 | 188680
P01202 | 70 | -15 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.09 | -4.78 | 30.6 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1844.8 | 69.6 | 3.29 | - | 170412 | 0 | 170412
P01203 | 70 | -10 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.02 | -3.45 | 25.9 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1576.1 | 47.5 | 3.45 | - | 148099 | 0 | 148099
P01204 | 70 | -5 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.45 | -1.95 | 21.8 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 1280.7 | 29.1 | 3.75 | - | 122355 | 0 | 122355
P01205 | 70 | 0 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.17 | -0.31 | 18 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 963.2 | 15.4 | 4.26 | - | 93479 | 0 | 93479
P01206 | 70 | 5 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 8.96 | 1.3 | 14.9 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 649.1 | 6.8 | 5.09 | - | 64004 | 0 | 64004
P01207 | 70 | 10 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 12.23 | 3.12 | 12 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 60 | 293 | 1.2 | 7.12 | - | 29325 | 0 | 29325
P01208 | 70 | -16 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.4 | -4.99 | 31.4 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1888 | 74.6 | 3.25 | - | 173790 | 0 | 173790
P01209 | 56 | -20 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3.4 | -6.3 | 37.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1939.4 | 78.8 | 3.72 | - | 194940 | 0 | 194940
P01210 | 56 | -15 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.56 | -5.09 | 31.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1718.2 | 57 | 3.97 | - | 175468 | 0 | 175468
P01211 | 56 | -10 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.77 | -3.6 | 26.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1453.5 | 37.9 | 4.41 | - | 150756 | 0 | 150756
P01216 | 56 | -16 | 15 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.88 | -5.3 | 32.6 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1756.5 | 60.7 | 3.91 | - | 178816 | 0 | 178816
P01249 | 55 | -20 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -2.21 | -5.52 | 33.6 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 2044.5 | 85.4 | 3.83 | - | 206904 | 0 | 206904
P01250 | 55 | -15 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.57 | -4.45 | 29.3 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1819.6 | 62.5 | 4.08 | - | 187067 | 0 | 187067
P01251 | 55 | -10 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.48 | -3.16 | 25.1 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1556 | 42 | 4.61 | - | 162453 | 0 | 162453
P01256 | 55 | -16 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.96 | -4.7 | 30.2 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1871.9 | 67.2 | 4.01 | - | 191843 | 0 | 191843
P01257 | 62.5 | -20 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -2.03 | -5.4 | 33.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 2131.8 | 95.1 | 3.44 | - | 204719 | 0 | 204719
P01258 | 62.5 | -15 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.38 | -4.32 | 28.8 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1892.4 | 69.7 | 3.59 | - | 184776 | 0 | 184776
P01259 | 62.5 | -10 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.62 | -3.07 | 24.8 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1619.9 | 47.2 | 3.85 | - | 160745 | 0 | 160745
P01260 | 62.5 | -5 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.02 | -1.6 | 20.9 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 1309.2 | 28.9 | 4.25 | - | 131972 | 0 | 131972
P01261 | 62.5 | 0 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.66 | -0.03 | 17.4 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 979.8 | 15.1 | 5.07 | - | 100253 | 0 | 100253
P01264 | 62.5 | -16 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.76 | -4.57 | 29.7 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1946.5 | 74.9 | 3.55 | - | 189431 | 0 | 189431
P01265 | 70 | -20 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -1.65 | -5.15 | 32 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 2204.4 | 104 | 3.21 | - | 200073 | 0 | 200073
P01266 | 70 | -15 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.17 | -4.17 | 28.3 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1973.7 | 77.9 | 3.29 | - | 182315 | 0 | 182315
P01267 | 70 | -10 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.77 | -2.98 | 24.6 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1692.4 | 53.2 | 3.47 | - | 159024 | 0 | 159024
P01268 | 70 | -5 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.09 | -1.56 | 20.8 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 1372 | 32.8 | 3.73 | - | 131078 | 0 | 131078
P01269 | 70 | 0 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.51 | -0.12 | 17.6 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 1051.3 | 18.1 | 4.18 | - | 102032 | 0 | 102032
P01270 | 70 | 5 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.32 | 1.51 | 14.5 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 691.6 | 7.8 | 4.92 | - | 68187 | 0 | 68187
P01271 | 70 | 10 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 12.36 | 3.19 | 11.9 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 60 | 317.3 | 1.5 | 6.92 | - | 31761 | 0 | 31761
P01272 | 70 | -16 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.45 | -4.38 | 29 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 2017.7 | 82.6 | 3.28 | - | 185729 | 0 | 185729
P01273 | 56 | -20 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -2.26 | -5.55 | 33.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 2063.8 | 87.2 | 3.75 | - | 207445 | 0 | 207445
P01274 | 56 | -15 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.54 | -4.43 | 29.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1829 | 63.4 | 3.99 | - | 186785 | 0 | 186785
P01275 | 56 | -10 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.5 | -3.15 | 25 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1564.6 | 42.7 | 4.45 | - | 162277 | 0 | 162277
P01280 | 56 | -16 | 15 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.94 | -4.69 | 30.2 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1881.7 | 68.2 | 3.93 | - | 191563 | 0 | 191563
P01305 | 47.5 | -20 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.72 | -7.88 | 45.2 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 1649.3 | 56.9 | 4.49 | - | 175276 | 0 | 175276
P01313 | 55 | -20 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.49 | -7.72 | 44.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 1712.6 | 63.7 | 3.75 | - | 173308 | 0 | 173308
P01314 | 55 | -15 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.32 | -6.24 | 36.8 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 1506.9 | 45.1 | 4.05 | - | 154923 | 0 | 154923
P01315 | 55 | -10 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.72 | -4.54 | 29.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 1273 | 29.2 | 4.62 | - | 132906 | 0 | 132906
P01320 | 55 | -16 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.81 | -6.57 | 38.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 1552.4 | 48.7 | 3.98 | - | 159103 | 0 | 159103
P01321 | 62.5 | -20 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.24 | -7.55 | 43.4 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 1782.7 | 71 | 3.41 | - | 171187 | 0 | 171187
P01322 | 62.5 | -15 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.15 | -6.15 | 36.3 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 1572.3 | 50.7 | 3.59 | - | 153515 | 0 | 153515
P01323 | 62.5 | -10 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.56 | -4.44 | 29.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 1325.8 | 33.4 | 3.88 | - | 131559 | 0 | 131559
P01324 | 62.5 | -5 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.19 | -2.72 | 23.8 | R290 (Propane) | Countercurrent | -5 | 0 | 62.5 | 60 | 1074.9 | 19.9 | 4.44 | - | 108357 | 0 | 108357
P01325 | 62.5 | 0 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.18 | -0.9 | 19.3 | R290 (Propane) | Countercurrent | 0 | 0 | 62.5 | 60 | 811.2 | 10.8 | 5.21 | - | 83004 | 0 | 83004
P01328 | 62.5 | -16 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.55 | -6.4 | 37.6 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 1611.9 | 54.2 | 3.56 | - | 156864 | 0 | 156864
P01329 | 70 | -20 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -4.95 | -7.35 | 42.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 1859.2 | 79.2 | 3.17 | - | 168747 | 0 | 168747
P01330 | 70 | -15 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.87 | -5.95 | 35.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 1636.5 | 56.6 | 3.31 | - | 151172 | 0 | 151172
P01331 | 70 | -10 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.44 | -4.37 | 29 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 1389.5 | 38 | 3.5 | - | 130568 | 0 | 130568
P01332 | 70 | -5 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.33 | -2.67 | 23.6 | R290 (Propane) | Countercurrent | -5 | 0 | 70 | 60 | 1121.3 | 22.8 | 3.85 | - | 107123 | 0 | 107123
P01333 | 70 | 0 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.27 | -0.85 | 19.2 | R290 (Propane) | Countercurrent | 0 | 0 | 70 | 60 | 847.6 | 12.3 | 4.37 | - | 82257 | 0 | 82257
P01334 | 70 | 5 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.42 | 0.99 | 15.4 | R290 (Propane) | Countercurrent | 5 | 0 | 70 | 60 | 564.5 | 5.3 | 5.33 | - | 55661 | 0 | 55661
P01335 | 70 | 10 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 11.92 | 2.92 | 12.2 | R290 (Propane) | Countercurrent | 10 | 0 | 70 | 60 | 260 | 0.9 | 7.1 | - | 26023 | 0 | 26023
P01336 | 70 | -16 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.29 | -6.23 | 36.8 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 1680.9 | 60.8 | 3.27 | - | 154731 | 0 | 154731
P01337 | 56 | -20 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.46 | -7.7 | 44.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 1721.6 | 64.7 | 3.69 | - | 173047 | 0 | 173047
P01338 | 56 | -15 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.3 | -6.23 | 36.8 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 1515.3 | 45.8 | 3.97 | - | 154752 | 0 | 154752
P01339 | 56 | -10 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.7 | -4.54 | 29.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 1280.5 | 29.7 | 4.49 | - | 132814 | 0 | 132814
P01344 | 56 | -16 | 15 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.72 | -6.51 | 38.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 1555.1 | 49.1 | 3.92 | - | 158315 | 0 | 158315
P01357 | 47.5 | -20 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.7 | -17.44 | 21.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 552.6 | 9.8 | 4.21 | - | 58725 | 0 | 58725
P01358 | 47.5 | -15 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.36 | -14.07 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 335.6 | 2.8 | 5.22 | - | 36208 | 0 | 36208
P01360 | 47.5 | -16 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13.05 | -14.76 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 380 | 3.6 | 4.92 | - | 40878 | 0 | 40878
P01361 | 55 | -20 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.64 | -17.38 | 21.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 576.3 | 11 | 3.72 | - | 58321 | 0 | 58321
P01362 | 55 | -15 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.37 | -14.07 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 352.4 | 3.1 | 4.42 | - | 36235 | 0 | 36235
P01363 | 55 | -10 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.67 | -11.78 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 108 | 0.7 | 6.73 | - | 11271 | 0 | 11271
P01364 | 55 | -16 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13.04 | -14.75 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 398.1 | 4.3 | 4.21 | - | 40804 | 0 | 40804
P01365 | 62.5 | -20 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.58 | -17.31 | 21.6 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 603.1 | 12.4 | 3.4 | - | 57917 | 0 | 57917
P01366 | 62.5 | -15 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.36 | -14.07 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 370.9 | 3.6 | 3.95 | - | 36214 | 0 | 36214
P01367 | 62.5 | -10 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.7 | -11.81 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 115.5 | 0.7 | 5.97 | - | 11464 | 0 | 11464
P01368 | 62.5 | -16 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13.02 | -14.72 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 417.8 | 5.2 | 3.78 | - | 40661 | 0 | 40661
P01369 | 70 | -20 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.51 | -17.25 | 21.4 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 633.1 | 14 | 3.14 | - | 57466 | 0 | 57466
P01370 | 70 | -15 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.28 | -13.99 | 16 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 386.1 | 4.3 | 3.54 | - | 35669 | 0 | 35669
P01371 | 70 | -10 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.72 | -11.83 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 123.3 | 0.8 | 5.39 | - | 11586 | 0 | 11586
P01372 | 70 | -16 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13 | -14.7 | 17 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 440 | 6.3 | 3.46 | - | 40504 | 0 | 40504
P01373 | 56 | -20 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.63 | -17.37 | 21.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 579.7 | 11.2 | 3.67 | - | 58270 | 0 | 58270
P01374 | 56 | -15 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.37 | -14.07 | 16.1 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 354.8 | 3.1 | 4.34 | - | 36237 | 0 | 36237
P01375 | 56 | -10 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -8.67 | -11.79 | 11.6 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 108.8 | 0.7 | 6.62 | - | 11286 | 0 | 11286
P01376 | 56 | -16 | -7 | 18194.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -13.04 | -14.74 | 17.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 400.7 | 4.4 | 4.14 | - | 40796 | 0 | 40796
P01389 | 47.5 | -20 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -15.01 | -16.73 | 20.5 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 625.2 | 12.2 | 4.06 | - | 66444 | 0 | 66444
P01390 | 47.5 | -15 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.99 | -15.49 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 383.3 | 3.7 | 4.97 | - | 41349 | 0 | 41349
P01392 | 47.5 | -16 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.61 | -14.31 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 432.5 | 5.3 | 4.71 | - | 46524 | 0 | 46524
P01393 | 55 | -20 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.95 | -16.67 | 20.4 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 651.8 | 13.7 | 3.6 | - | 65964 | 0 | 65964
P01394 | 55 | -15 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.99 | -15.49 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 402.2 | 4.5 | 4.16 | - | 41349 | 0 | 41349
P01395 | 55 | -10 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.56 | -11.69 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 124.1 | 0.8 | 6.29 | - | 12957 | 0 | 12957
P01396 | 55 | -16 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.6 | -14.3 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 452.9 | 6.4 | 4.04 | - | 46416 | 0 | 46416
P01397 | 62.5 | -20 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.88 | -16.61 | 20.2 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 681.1 | 15.4 | 3.3 | - | 65406 | 0 | 65406
P01398 | 62.5 | -15 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.9 | -15.35 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 416.4 | 5.2 | 3.72 | - | 40654 | 0 | 40654
P01399 | 62.5 | -10 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.57 | -11.7 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 131.5 | 0.8 | 5.59 | - | 13053 | 0 | 13053
P01400 | 62.5 | -16 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.57 | -14.27 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 474.4 | 7.6 | 3.64 | - | 46167 | 0 | 46167
P01401 | 70 | -20 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.81 | -16.53 | 20.1 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 714.1 | 17.3 | 3.06 | - | 64813 | 0 | 64813
P01402 | 70 | -15 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.88 | -15.31 | 15.4 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 438.1 | 6.3 | 3.4 | - | 40468 | 0 | 40468
P01403 | 70 | -10 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.59 | -11.72 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 140.6 | 0.9 | 5.04 | - | 13208 | 0 | 13208
P01404 | 70 | -16 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.55 | -14.25 | 16.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 499.8 | 8.6 | 3.34 | - | 46008 | 0 | 46008
P01405 | 56 | -20 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.94 | -16.67 | 20.3 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 655.6 | 13.9 | 3.56 | - | 65895 | 0 | 65895
P01406 | 56 | -15 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.99 | -15.49 | 15.5 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 404.9 | 4.6 | 4.09 | - | 41349 | 0 | 41349
P01407 | 56 | -10 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -8.56 | -11.69 | 11.5 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 125 | 0.8 | 6.19 | - | 12969 | 0 | 12969
P01408 | 56 | -16 | -7 | 22353.12 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.59 | -14.3 | 16.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 455.8 | 6.5 | 3.98 | - | 46399 | 0 | 46399
P01421 | 47.5 | -20 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.43 | -16.14 | 19.4 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 691 | 14.6 | 3.98 | - | 73437 | 0 | 73437
P01422 | 47.5 | -15 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.59 | -14.87 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 420.4 | 5 | 4.73 | - | 45358 | 0 | 45358
P01424 | 47.5 | -16 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.21 | -13.92 | 15.9 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 479.2 | 7.1 | 4.57 | - | 51544 | 0 | 51544
P01425 | 55 | -20 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.27 | -15.99 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 710.8 | 16.2 | 3.48 | - | 71929 | 0 | 71929
P01426 | 55 | -15 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.58 | -14.86 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 440.2 | 5.9 | 4.02 | - | 45261 | 0 | 45261
P01427 | 55 | -10 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.5 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 141.8 | 0.9 | 6.07 | - | 14801 | 0 | 14801
P01428 | 55 | -16 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.2 | -13.91 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 501.6 | 8 | 3.91 | - | 51408 | 0 | 51408
P01429 | 62.5 | -20 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.17 | -15.88 | 18.9 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 737.9 | 17.9 | 3.21 | - | 70860 | 0 | 70860
P01430 | 62.5 | -15 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.55 | -14.82 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 461.1 | 7 | 3.61 | - | 45023 | 0 | 45023
P01431 | 62.5 | -10 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.47 | -11.62 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 146.8 | 1 | 5.31 | - | 14571 | 0 | 14571
P01432 | 62.5 | -16 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.16 | -13.86 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 523.2 | 9 | 3.53 | - | 50977 | 0 | 50977
P01433 | 70 | -20 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.1 | -15.81 | 18.8 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 773.6 | 20.1 | 2.97 | - | 70210 | 0 | 70210
P01434 | 70 | -15 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.54 | -14.8 | 14.9 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 485.6 | 8.1 | 3.31 | - | 44855 | 0 | 44855
P01435 | 70 | -10 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.49 | -11.63 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 156.9 | 1.1 | 4.78 | - | 14741 | 0 | 14741
P01436 | 70 | -16 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.08 | -13.78 | 15.7 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 545.2 | 10.1 | 3.19 | - | 50188 | 0 | 50188
P01437 | 56 | -20 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.27 | -15.98 | 19.1 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 714.7 | 16.4 | 3.43 | - | 71840 | 0 | 71840
P01438 | 56 | -15 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.58 | -14.86 | 15 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 443 | 6.1 | 3.95 | - | 45246 | 0 | 45246
P01439 | 56 | -10 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -8.5 | -11.64 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 142.9 | 0.9 | 5.96 | - | 14823 | 0 | 14823
P01440 | 56 | -16 | -7 | 26641.8 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.2 | -13.9 | 15.8 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 504.8 | 8.2 | 3.85 | - | 51387 | 0 | 51387
P01453 | 47.5 | -20 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.81 | -15.52 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 735.6 | 16.6 | 3.86 | - | 78176 | 0 | 78176
P01454 | 47.5 | -15 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.35 | -14.55 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 463.2 | 6.5 | 4.73 | - | 49970 | 0 | 49970
P01456 | 47.5 | -16 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.89 | -15.33 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 522 | 8.3 | 4.48 | - | 56150 | 0 | 56150
P01457 | 55 | -20 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.77 | -15.47 | 18.3 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 767.4 | 18.6 | 3.43 | - | 77655 | 0 | 77655
P01458 | 55 | -15 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.34 | -14.53 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 484 | 7.4 | 4 | - | 49757 | 0 | 49757
P01459 | 55 | -10 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.42 | -11.57 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 156.3 | 1 | 5.8 | - | 16313 | 0 | 16313
P01460 | 55 | -16 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.86 | -15.29 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 544.8 | 9.3 | 3.84 | - | 55831 | 0 | 55831
P01461 | 62.5 | -20 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.68 | -15.39 | 18.1 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 798.9 | 20.6 | 3.15 | - | 76718 | 0 | 76718
P01462 | 62.5 | -15 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.32 | -14.5 | 14.6 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 507.6 | 8.3 | 3.59 | - | 49565 | 0 | 49565
P01463 | 62.5 | -10 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.4 | -11.55 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 161.7 | 1.1 | 5.05 | - | 16041 | 0 | 16041
P01464 | 62.5 | -16 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.84 | -15.24 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 570.3 | 10.4 | 3.46 | - | 55499 | 0 | 55499
P01465 | 70 | -20 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.6 | -15.3 | 18 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 834.8 | 23 | 2.93 | - | 75767 | 0 | 75767
P01466 | 70 | -15 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.23 | -14.39 | 14.5 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 525.8 | 9.3 | 3.23 | - | 48571 | 0 | 48571
P01467 | 70 | -10 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.42 | -11.56 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 172.8 | 1.2 | 4.56 | - | 16236 | 0 | 16236
P01468 | 70 | -16 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.79 | -15.17 | 15.3 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 596.9 | 11.7 | 3.18 | - | 54950 | 0 | 54950
P01469 | 56 | -20 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.76 | -15.46 | 18.2 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 771.6 | 18.8 | 3.38 | - | 77563 | 0 | 77563
P01470 | 56 | -15 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.33 | -14.52 | 14.7 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 487 | 7.5 | 3.93 | - | 49738 | 0 | 49738
P01471 | 56 | -10 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -8.42 | -11.57 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 157.3 | 1 | 5.7 | - | 16313 | 0 | 16313
P01472 | 56 | -16 | -7 | 30930.48 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.86 | -15.27 | 15.4 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 547.4 | 9.4 | 3.78 | - | 55724 | 0 | 55724
P01485 | 47.5 | -20 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.5 | -15.2 | 17.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 796.4 | 18.7 | 3.87 | - | 84638 | 0 | 84638
P01486 | 47.5 | -15 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.14 | -14.28 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 500 | 7.5 | 4.61 | - | 53938 | 0 | 53938
P01488 | 47.5 | -16 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.63 | -14.93 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 560.1 | 9.4 | 4.37 | - | 60248 | 0 | 60248
P01489 | 55 | -20 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.4 | -15.11 | 17.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 823.8 | 20.6 | 3.45 | - | 83368 | 0 | 83368
P01490 | 55 | -15 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.12 | -14.25 | 14.4 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 521.2 | 8.4 | 3.89 | - | 53585 | 0 | 53585
P01491 | 55 | -10 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.34 | -11.5 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 167.6 | 1.1 | 5.63 | - | 17497 | 0 | 17497
P01492 | 55 | -16 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.6 | -14.89 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 584.1 | 10.5 | 3.75 | - | 59864 | 0 | 59864
P01493 | 62.5 | -20 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.31 | -15.02 | 17.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 855.9 | 22.9 | 3.17 | - | 82196 | 0 | 82196
P01494 | 62.5 | -15 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.01 | -14.11 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 534.4 | 9.3 | 3.46 | - | 52177 | 0 | 52177
P01495 | 62.5 | -10 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.36 | -11.52 | 11.3 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 178.3 | 1.2 | 4.96 | - | 17694 | 0 | 17694
P01496 | 62.5 | -16 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.54 | -14.8 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 607.1 | 11.6 | 3.4 | - | 59082 | 0 | 59082
P01497 | 70 | -20 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.16 | -14.87 | 17.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 884.3 | 25.4 | 2.92 | - | 80259 | 0 | 80259
P01498 | 70 | -15 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.98 | -14.08 | 14.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 560.5 | 10.4 | 3.18 | - | 51777 | 0 | 51777
P01499 | 70 | -10 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.34 | -11.5 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 185.1 | 1.3 | 4.42 | - | 17396 | 0 | 17396
P01500 | 70 | -16 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.49 | -14.74 | 14.9 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 635.6 | 13 | 3.14 | - | 58511 | 0 | 58511
P01501 | 56 | -20 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.39 | -15.1 | 17.6 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 828.1 | 20.9 | 3.41 | - | 83241 | 0 | 83241
P01502 | 56 | -15 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.03 | -14.14 | 14.3 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 513.7 | 8.4 | 3.79 | - | 52463 | 0 | 52463
P01503 | 56 | -10 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -8.35 | -11.51 | 11.2 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 169 | 1.1 | 5.52 | - | 17523 | 0 | 17523
P01504 | 56 | -16 | -7 | 35089.2 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.59 | -14.88 | 15 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 587.5 | 10.7 | 3.69 | - | 59808 | 0 | 59808
P01517 | 47.5 | -20 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.66 | -16.38 | 19.8 | R290 (Propane) | Countercurrent | -20 | 0 | 47.5 | 60 | 660.9 | 13.5 | 4.02 | - | 70239 | 0 | 70239
P01518 | 47.5 | -15 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.78 | -15.16 | 15.3 | R290 (Propane) | Countercurrent | -15 | 0 | 47.5 | 60 | 406.2 | 4.4 | 4.89 | - | 43823 | 0 | 43823
P01520 | 47.5 | -16 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.37 | -14.08 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 47.5 | 60 | 457.8 | 6.3 | 4.65 | - | 49245 | 0 | 49245
P01521 | 55 | -20 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.6 | -16.32 | 19.7 | R290 (Propane) | Countercurrent | -20 | 0 | 55 | 60 | 688.4 | 15.1 | 3.57 | - | 69665 | 0 | 69665
P01522 | 55 | -15 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.77 | -15.14 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 55 | 60 | 425 | 5.2 | 4.15 | - | 43694 | 0 | 43694
P01523 | 55 | -10 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.55 | -11.68 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 55 | 60 | 135.9 | 0.8 | 6.17 | - | 14192 | 0 | 14192
P01524 | 55 | -16 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.35 | -14.05 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 55 | 60 | 478.3 | 7.4 | 3.98 | - | 49016 | 0 | 49016
P01525 | 62.5 | -20 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.46 | -16.17 | 19.5 | R290 (Propane) | Countercurrent | -20 | 0 | 62.5 | 60 | 711.6 | 16.8 | 3.22 | - | 68334 | 0 | 68334
P01526 | 62.5 | -15 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.75 | -15.11 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 62.5 | 60 | 445.6 | 6.2 | 3.73 | - | 43510 | 0 | 43510
P01527 | 62.5 | -10 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.51 | -11.65 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 62.5 | 60 | 139.8 | 0.9 | 5.43 | - | 13873 | 0 | 13873
P01528 | 62.5 | -16 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.37 | -14.07 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 62.5 | 60 | 505.1 | 8.4 | 3.57 | - | 49156 | 0 | 49156
P01529 | 70 | -20 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.37 | -16.08 | 19.3 | R290 (Propane) | Countercurrent | -20 | 0 | 70 | 60 | 744.1 | 18.9 | 2.99 | - | 67540 | 0 | 67540
P01530 | 70 | -15 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.73 | -15.08 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 70 | 60 | 469.3 | 7.5 | 3.41 | - | 43352 | 0 | 43352
P01531 | 70 | -10 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.54 | -11.68 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 70 | 60 | 150.5 | 1 | 4.86 | - | 14146 | 0 | 14146
P01532 | 70 | -16 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.31 | -14.01 | 16 | R290 (Propane) | Countercurrent | -16 | 0 | 70 | 60 | 528.3 | 9.4 | 3.29 | - | 48633 | 0 | 48633
P01533 | 56 | -20 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.59 | -16.31 | 19.7 | R290 (Propane) | Countercurrent | -20 | 0 | 56 | 60 | 692.3 | 15.3 | 3.52 | - | 69582 | 0 | 69582
P01534 | 56 | -15 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.77 | -15.14 | 15.2 | R290 (Propane) | Countercurrent | -15 | 0 | 56 | 60 | 427.6 | 5.3 | 4.08 | - | 43673 | 0 | 43673
P01535 | 56 | -10 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -8.55 | -11.68 | 11.4 | R290 (Propane) | Countercurrent | -10 | 0 | 56 | 60 | 137 | 0.9 | 6.06 | - | 14210 | 0 | 14210
P01536 | 56 | -16 | -7 | 24692.4 | 60 | 0 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.35 | -14.05 | 16.1 | R290 (Propane) | Countercurrent | -16 | 0 | 56 | 60 | 481.3 | 7.5 | 3.92 | - | 48994 | 0 | 48994
P00004 | 47.5 | -20 | -13 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.28 | -19.16 | 14.9 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 273.1 | 2.8 | 4.17 | - | 29609 | 0 | 29609
P00005 | 55 | -20 | -13 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.3 | -19.18 | 14.9 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 287.5 | 3.1 | 3.7 | - | 29712 | 0 | 29712
P00006 | 62.5 | -20 | -13 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.3 | -19.18 | 14.9 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 303 | 3.4 | 3.35 | - | 29748 | 0 | 29748
P00007 | 70 | -20 | -13 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.31 | -19.18 | 14.9 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 320.4 | 3.8 | 3.08 | - | 29767 | 0 | 29767
P00008 | 56 | -20 | -13 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -13 | -14.83 | 10 | -17.3 | -19.18 | 14.9 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 289.4 | 3.1 | 3.64 | - | 29717 | 0 | 29717
P00012 | 47.5 | -20 | -13 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.98 | -18.85 | 14.4 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 311.5 | 3.4 | 3.96 | - | 33782 | 0 | 33782
P00013 | 55 | -20 | -13 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.98 | -18.85 | 14.4 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 327.2 | 3.8 | 3.52 | - | 33822 | 0 | 33822
P00014 | 62.5 | -20 | -13 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.98 | -18.86 | 14.4 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 344.7 | 4.2 | 3.2 | - | 33842 | 0 | 33842
P00015 | 70 | -20 | -13 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.92 | -18.79 | 14.3 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 357.8 | 4.6 | 2.9 | - | 33251 | 0 | 33251
P00016 | 56 | -20 | -13 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -13 | -14.83 | 10 | -16.98 | -18.85 | 14.4 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 329.5 | 3.8 | 3.47 | - | 33826 | 0 | 33826
P00020 | 47.5 | -20 | -13 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.7 | -18.57 | 14.1 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 345.6 | 4 | 3.81 | - | 37478 | 0 | 37478
P00021 | 55 | -20 | -13 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.65 | -18.52 | 14 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 357.4 | 4.4 | 3.33 | - | 36943 | 0 | 36943
P00022 | 62.5 | -20 | -13 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.65 | -18.52 | 14 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 376.3 | 4.9 | 3.04 | - | 36951 | 0 | 36951
P00023 | 70 | -20 | -13 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.63 | -18.5 | 14 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 395.9 | 5.7 | 2.81 | - | 36787 | 0 | 36787
P00024 | 56 | -20 | -13 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -13 | -14.83 | 10 | -16.65 | -18.52 | 14 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 359.8 | 4.4 | 3.29 | - | 36945 | 0 | 36945
P00028 | 47.5 | -20 | -13 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.48 | -18.34 | 13.8 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 376.6 | 4.5 | 3.71 | - | 40839 | 0 | 40839
P00029 | 55 | -20 | -13 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.47 | -18.33 | 13.8 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 394.4 | 5.2 | 3.31 | - | 40759 | 0 | 40759
P00030 | 62.5 | -20 | -13 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.45 | -18.31 | 13.7 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 412.8 | 6.1 | 3.03 | - | 40537 | 0 | 40537
P00031 | 70 | -20 | -13 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.43 | -18.29 | 13.7 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 433.7 | 7.2 | 2.81 | - | 40297 | 0 | 40297
P00032 | 56 | -20 | -13 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -13 | -14.83 | 10 | -16.47 | -18.33 | 13.8 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 396.8 | 5.3 | 3.27 | - | 40742 | 0 | 40742
P00036 | 47.5 | -20 | -13 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.29 | -18.15 | 13.5 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 404.6 | 5.5 | 3.61 | - | 43869 | 0 | 43869
P00037 | 55 | -20 | -13 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.28 | -18.14 | 13.5 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 423.1 | 6.4 | 3.23 | - | 43727 | 0 | 43727
P00038 | 62.5 | -20 | -13 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.26 | -18.11 | 13.5 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 442.1 | 7.4 | 2.97 | - | 43408 | 0 | 43408
P00039 | 70 | -20 | -13 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.16 | -18.01 | 13.4 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 452.7 | 8.2 | 2.72 | - | 42064 | 0 | 42064
P00040 | 56 | -20 | -13 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -13 | -14.83 | 10 | -16.28 | -18.14 | 13.5 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 425.7 | 6.5 | 3.19 | - | 43704 | 0 | 43704
P00044 | 47.5 | -20 | -13 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 329.9 | 3.7 | 3.89 | - | 35774 | 0 | 35774
P00045 | 55 | -20 | -13 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 346 | 4.1 | 3.45 | - | 35763 | 0 | 35763
P00046 | 62.5 | -20 | -13 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 364.4 | 4.5 | 3.15 | - | 35781 | 0 | 35781
P00047 | 70 | -20 | -13 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 384.5 | 5.1 | 2.9 | - | 35728 | 0 | 35728
P00048 | 56 | -20 | -13 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -13 | -14.83 | 10 | -16.81 | -18.68 | 14.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 348.4 | 4.1 | 3.41 | - | 35767 | 0 | 35767
P00058 | 47.5 | -20 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.26 | -16.96 | 22.8 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 574.2 | 10.7 | 4.04 | - | 62264 | 0 | 62264
P00059 | 47.5 | -15 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.95 | -15.35 | 16.9 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 363.6 | 3.3 | 4.9 | - | 40027 | 0 | 40027
P00060 | 47.5 | -16 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.63 | -14.3 | 18 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 406.1 | 4.5 | 4.65 | - | 44578 | 0 | 44578
P00061 | 55 | -20 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.2 | -16.91 | 22.7 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 599.1 | 12 | 3.57 | - | 61924 | 0 | 61924
P00062 | 55 | -15 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.95 | -15.34 | 16.9 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 380.8 | 3.9 | 4.15 | - | 39991 | 0 | 39991
P00063 | 55 | -16 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.61 | -14.29 | 17.9 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 424.8 | 5.4 | 3.98 | - | 44472 | 0 | 44472
P00064 | 62.5 | -20 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.14 | -16.85 | 22.6 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 626.4 | 13.5 | 3.26 | - | 61509 | 0 | 61509
P00065 | 62.5 | -15 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.94 | -15.34 | 16.9 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 400.3 | 4.6 | 3.71 | - | 39965 | 0 | 39965
P00066 | 62.5 | -16 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.59 | -14.27 | 17.9 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 445.3 | 6.4 | 3.58 | - | 44319 | 0 | 44319
P00067 | 70 | -20 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.04 | -16.74 | 22.4 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 654.3 | 15 | 3.03 | - | 60803 | 0 | 60803
P00068 | 70 | -15 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.83 | -15.15 | 16.7 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 414.3 | 5.4 | 3.35 | - | 39181 | 0 | 39181
P00069 | 70 | -16 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.56 | -14.23 | 17.8 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 468 | 7.6 | 3.28 | - | 44106 | 0 | 44106
P00070 | 56 | -20 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -15.2 | -16.9 | 22.7 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 602.6 | 12.2 | 3.52 | - | 61872 | 0 | 61872
P00071 | 56 | -15 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -11.95 | -15.34 | 16.9 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 383.2 | 4 | 4.08 | - | 39984 | 0 | 39984
P00072 | 56 | -16 | -6 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -6 | -9.6 | 10 | -12.61 | -14.29 | 17.9 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 427.4 | 5.5 | 3.92 | - | 44455 | 0 | 44455
P00082 | 47.5 | -20 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.52 | -16.21 | 21.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 649.6 | 13.3 | 3.91 | - | 70434 | 0 | 70434
P00083 | 47.5 | -15 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.52 | -14.71 | 16.2 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 414.4 | 4.8 | 4.69 | - | 45623 | 0 | 45623
P00084 | 47.5 | -16 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.13 | -13.81 | 17.2 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 461.8 | 6.6 | 4.47 | - | 50687 | 0 | 50687
P00085 | 55 | -20 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.47 | -16.15 | 21.2 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 677 | 14.9 | 3.46 | - | 69974 | 0 | 69974
P00086 | 55 | -15 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.41 | -14.56 | 16.1 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 426 | 5.5 | 3.93 | - | 44738 | 0 | 44738
P00087 | 55 | -16 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.12 | -13.8 | 17.1 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 482.7 | 7.6 | 3.83 | - | 50532 | 0 | 50532
P00088 | 62.5 | -20 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.4 | -16.09 | 21.1 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 706.9 | 16.7 | 3.17 | - | 69410 | 0 | 69410
P00089 | 62.5 | -15 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.4 | -14.54 | 16.1 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 446.5 | 6.5 | 3.52 | - | 44579 | 0 | 44579
P00090 | 62.5 | -16 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.1 | -13.78 | 17.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 506.3 | 8.6 | 3.45 | - | 50385 | 0 | 50385
P00091 | 70 | -20 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.28 | -15.97 | 20.9 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 736.8 | 18.5 | 2.95 | - | 68462 | 0 | 68462
P00092 | 70 | -15 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.37 | -14.51 | 16 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 469.2 | 7.7 | 3.23 | - | 44376 | 0 | 44376
P00093 | 70 | -16 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.06 | -13.74 | 17.1 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 531.5 | 9.7 | 3.16 | - | 50098 | 0 | 50098
P00094 | 56 | -20 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -14.46 | -16.15 | 21.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 680.8 | 15.1 | 3.42 | - | 69903 | 0 | 69903
P00095 | 56 | -15 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -11.41 | -14.56 | 16.1 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 428.6 | 5.6 | 3.86 | - | 44720 | 0 | 44720
P00096 | 56 | -16 | -6 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -6 | -9.6 | 10 | -12.11 | -13.79 | 17.1 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 485.7 | 7.7 | 3.77 | - | 50516 | 0 | 50516
P00106 | 47.5 | -20 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.88 | -15.56 | 20.1 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 715.8 | 15.8 | 3.82 | - | 77612 | 0 | 77612
P00107 | 47.5 | -15 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.07 | -14.07 | 15.6 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 453.6 | 6.4 | 4.48 | - | 49941 | 0 | 49941
P00108 | 47.5 | -16 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.72 | -15 | 16.5 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 513.6 | 8.2 | 4.35 | - | 56376 | 0 | 56376
P00109 | 55 | -20 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.82 | -15.49 | 20 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 744.8 | 17.6 | 3.4 | - | 76985 | 0 | 76985
P00110 | 55 | -15 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.06 | -14.06 | 15.6 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 474 | 7.4 | 3.79 | - | 49780 | 0 | 49780
P00111 | 55 | -16 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.69 | -14.95 | 16.5 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 535.6 | 9.2 | 3.71 | - | 56071 | 0 | 56071
P00112 | 62.5 | -20 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.75 | -15.43 | 19.9 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 777.2 | 19.7 | 3.11 | - | 76307 | 0 | 76307
P00113 | 62.5 | -15 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.04 | -14.04 | 15.6 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 497.3 | 8.3 | 3.4 | - | 49655 | 0 | 49655
P00114 | 62.5 | -16 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.66 | -14.91 | 16.5 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 560.6 | 10.3 | 3.35 | - | 55785 | 0 | 55785
P00115 | 70 | -20 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.63 | -15.31 | 19.7 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 809 | 21.8 | 2.9 | - | 75171 | 0 | 75171
P00116 | 70 | -15 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.02 | -14.02 | 15.5 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 522.4 | 9.3 | 3.12 | - | 49404 | 0 | 49404
P00117 | 70 | -16 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.52 | -14.71 | 16.2 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 576.8 | 11.3 | 3.04 | - | 54361 | 0 | 54361
P00118 | 56 | -20 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -13.81 | -15.49 | 20 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 748.9 | 17.9 | 3.35 | - | 76893 | 0 | 76893
P00119 | 56 | -15 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.05 | -14.05 | 15.6 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 477 | 7.5 | 3.73 | - | 49765 | 0 | 49765
P00120 | 56 | -16 | -6 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -6 | -9.6 | 10 | -11.69 | -14.95 | 16.5 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 538.8 | 9.3 | 3.65 | - | 56036 | 0 | 56036
P00130 | 47.5 | -20 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.33 | -15.01 | 19.1 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 773.5 | 18.1 | 3.78 | - | 83870 | 0 | 83870
P00131 | 47.5 | -15 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.83 | -13.83 | 15.3 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 501.2 | 7.7 | 4.46 | - | 55177 | 0 | 55177
P00132 | 47.5 | -16 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.33 | -14.46 | 16 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 555.6 | 9.4 | 4.25 | - | 60984 | 0 | 60984
P00133 | 55 | -20 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.27 | -14.94 | 19 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 803.9 | 20.1 | 3.35 | - | 83089 | 0 | 83089
P00134 | 55 | -15 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.8 | -13.8 | 15.2 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 522.1 | 8.6 | 3.76 | - | 54824 | 0 | 54824
P00135 | 55 | -16 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 572.2 | 10.5 | 3.57 | - | 59899 | 0 | 59899
P00136 | 62.5 | -20 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.18 | -14.86 | 18.9 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 836.5 | 22.3 | 3.08 | - | 82132 | 0 | 82132
P00137 | 62.5 | -15 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.72 | -13.72 | 15.1 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 539.9 | 9.6 | 3.33 | - | 53907 | 0 | 53907
P00138 | 62.5 | -16 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.21 | -14.21 | 15.8 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 598.6 | 11.7 | 3.23 | - | 59573 | 0 | 59573
P00139 | 70 | -20 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.1 | -14.78 | 18.7 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 873.9 | 24.9 | 2.86 | - | 81205 | 0 | 81205
P00140 | 70 | -15 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.68 | -13.68 | 15.1 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 565.9 | 10.7 | 3.05 | - | 53523 | 0 | 53523
P00141 | 70 | -16 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.17 | -14.17 | 15.7 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 626.7 | 13.1 | 2.97 | - | 59064 | 0 | 59064
P00142 | 56 | -20 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -13.26 | -14.93 | 19 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 808.3 | 20.4 | 3.31 | - | 82992 | 0 | 82992
P00143 | 56 | -15 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -10.79 | -13.79 | 15.2 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 525.1 | 8.7 | 3.7 | - | 54785 | 0 | 54785
P00144 | 56 | -16 | -6 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -6 | -9.6 | 10 | -11.24 | -14.24 | 15.8 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 575.9 | 10.6 | 3.52 | - | 59899 | 0 | 59899
P00154 | 47.5 | -20 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.86 | -14.54 | 18.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 821.1 | 20.1 | 3.75 | - | 89038 | 0 | 89038
P00155 | 47.5 | -15 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.48 | -13.48 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 527.2 | 8.6 | 4.31 | - | 58043 | 0 | 58043
P00156 | 47.5 | -16 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -11.02 | -14.02 | 15.5 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 592.9 | 10.6 | 4.19 | - | 65081 | 0 | 65081
P00157 | 55 | -20 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.78 | -14.46 | 18.2 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 851 | 22.2 | 3.32 | - | 87959 | 0 | 87959
P00158 | 55 | -15 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.45 | -13.45 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 549.7 | 9.5 | 3.64 | - | 57729 | 0 | 57729
P00159 | 55 | -16 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.98 | -13.98 | 15.5 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 617.3 | 11.8 | 3.58 | - | 64623 | 0 | 64623
P00160 | 62.5 | -20 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.64 | -14.31 | 18 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 876.9 | 24.6 | 3.02 | - | 86105 | 0 | 86105
P00161 | 62.5 | -15 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.42 | -13.42 | 14.7 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 574.3 | 10.6 | 3.28 | - | 57339 | 0 | 57339
P00162 | 62.5 | -16 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.95 | -13.95 | 15.4 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 644.6 | 13.1 | 3.24 | - | 64146 | 0 | 64146
P00163 | 70 | -20 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.55 | -14.23 | 17.8 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 914.1 | 27.3 | 2.81 | - | 84936 | 0 | 84936
P00164 | 70 | -15 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.39 | -13.39 | 14.7 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 601.9 | 11.9 | 3.02 | - | 56923 | 0 | 56923
P00165 | 70 | -16 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.9 | -13.9 | 15.4 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 674.7 | 14.7 | 2.99 | - | 63588 | 0 | 63588
P00166 | 56 | -20 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -12.77 | -14.45 | 18.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 855.4 | 22.5 | 3.28 | - | 87833 | 0 | 87833
P00167 | 56 | -15 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.45 | -13.45 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 552.9 | 9.7 | 3.58 | - | 57684 | 0 | 57684
P00168 | 56 | -16 | -6 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -6 | -9.6 | 10 | -10.98 | -13.98 | 15.5 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 620.8 | 11.9 | 3.53 | - | 64563 | 0 | 64563
P00178 | 47.5 | -20 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.13 | -15.82 | 20.6 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 684.7 | 14.6 | 3.86 | - | 74247 | 0 | 74247
P00179 | 47.5 | -15 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.3 | -14.41 | 15.9 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 439.3 | 5.7 | 4.62 | - | 48367 | 0 | 48367
P00180 | 47.5 | -16 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.89 | -15.24 | 16.8 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 489.4 | 7.5 | 4.42 | - | 53718 | 0 | 53718
P00181 | 55 | -20 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.07 | -15.76 | 20.5 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 713.1 | 16.3 | 3.43 | - | 73706 | 0 | 73706
P00182 | 55 | -15 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.27 | -14.38 | 15.9 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 458.2 | 6.6 | 3.91 | - | 48116 | 0 | 48116
P00183 | 55 | -16 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.86 | -15.21 | 16.8 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 511 | 8.4 | 3.76 | - | 53495 | 0 | 53495
P00184 | 62.5 | -20 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.93 | -15.61 | 20.2 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 737 | 18.2 | 3.1 | - | 72368 | 0 | 72368
P00185 | 62.5 | -15 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.25 | -14.25 | 15.9 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 480.3 | 7.7 | 3.51 | - | 47957 | 0 | 47957
P00186 | 62.5 | -16 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.83 | -15.16 | 16.7 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 534.7 | 9.5 | 3.39 | - | 53207 | 0 | 53207
P00187 | 70 | -20 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -13.85 | -15.52 | 20.1 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 770.8 | 20.3 | 2.88 | - | 71624 | 0 | 71624
P00188 | 70 | -15 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.16 | -14.16 | 15.7 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 498.2 | 8.6 | 3.16 | - | 47115 | 0 | 47115
P00189 | 70 | -16 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.74 | -15.02 | 16.6 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 555.5 | 10.6 | 3.07 | - | 52355 | 0 | 52355
P00190 | 56 | -20 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -14.05 | -15.73 | 20.4 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 716.1 | 16.5 | 3.38 | - | 73521 | 0 | 73521
P00191 | 56 | -15 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.27 | -14.37 | 15.9 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 460.9 | 6.8 | 3.85 | - | 48091 | 0 | 48091
P00192 | 56 | -16 | -6 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -6 | -9.6 | 10 | -11.86 | -15.2 | 16.7 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 514 | 8.6 | 3.71 | - | 53461 | 0 | 53461
P00208 | 47.5 | -20 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.95 | -14.37 | 33 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 842.7 | 19.7 | 4.05 | - | 91378 | 0 | 91378
P00209 | 47.5 | -15 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.93 | -12.48 | 25.2 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 650.3 | 10.9 | 4.85 | - | 71589 | 0 | 71589
P00212 | 47.5 | -16 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.57 | -13.1 | 26.6 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 690.4 | 12.4 | 4.63 | - | 75775 | 0 | 75775
P00213 | 55 | -20 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.84 | -14.26 | 32.7 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 877.5 | 22 | 3.57 | - | 90692 | 0 | 90692
P00214 | 55 | -15 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.88 | -12.43 | 25 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 678.5 | 12.3 | 4.02 | - | 71248 | 0 | 71248
P00215 | 55 | -10 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.53 | -9.66 | 18.7 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 462.5 | 5.6 | 4.77 | - | 49325 | 0 | 49325
P00216 | 55 | -5 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.76 | -6.96 | 13.5 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 227.1 | 1.3 | 5.98 | - | 24591 | 0 | 24591
P00217 | 55 | -16 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.44 | -12.98 | 26.3 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 716.2 | 14.1 | 3.86 | - | 74971 | 0 | 74971
P00218 | 62.5 | -20 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.72 | -14.14 | 32.3 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 915.6 | 24.7 | 3.27 | - | 89906 | 0 | 89906
P00219 | 62.5 | -15 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.75 | -12.32 | 24.8 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 705.5 | 13.9 | 3.55 | - | 70444 | 0 | 70444
P00220 | 62.5 | -10 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.52 | -9.65 | 18.7 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 485.6 | 6.4 | 4.12 | - | 49284 | 0 | 49284
P00221 | 62.5 | -5 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.73 | -6.94 | 13.5 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 236.8 | 1.5 | 4.96 | - | 24418 | 0 | 24418
P00222 | 62.5 | -16 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.37 | -12.9 | 26.2 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 748.4 | 15.8 | 3.47 | - | 74480 | 0 | 74480
P00223 | 70 | -20 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.53 | -13.95 | 31.8 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 954.1 | 27.5 | 3.05 | - | 88654 | 0 | 88654
P00224 | 70 | -15 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.69 | -12.25 | 24.6 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 740.1 | 15.7 | 3.26 | - | 70000 | 0 | 70000
P00225 | 70 | -10 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.51 | -9.64 | 18.6 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 511.2 | 7.3 | 3.7 | - | 49186 | 0 | 49186
P00226 | 70 | -5 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.74 | -6.95 | 13.5 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 250.1 | 1.6 | 4.38 | - | 24471 | 0 | 24471
P00227 | 70 | -16 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.28 | -12.81 | 25.9 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 783.8 | 17.9 | 3.19 | - | 73874 | 0 | 73874
P00228 | 56 | -20 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -12.83 | -14.25 | 32.6 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 882.3 | 22.4 | 3.52 | - | 90593 | 0 | 90593
P00229 | 56 | -15 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -9.87 | -12.42 | 25 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 682.4 | 12.4 | 3.95 | - | 71199 | 0 | 71199
P00230 | 56 | -10 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -6.53 | -9.66 | 18.7 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 465.4 | 5.7 | 4.65 | - | 49322 | 0 | 49322
P00231 | 56 | -5 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -2.76 | -6.96 | 13.5 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 228.7 | 1.3 | 5.81 | - | 24607 | 0 | 24607
P00232 | 56 | -16 | 1 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 1 | -4.48 | 10 | -10.44 | -12.98 | 26.3 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 720.9 | 14.3 | 3.8 | - | 74971 | 0 | 74971
P00248 | 47.5 | -20 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.76 | -14.43 | 29.6 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 947.2 | 24.1 | 3.99 | - | 102702 | 0 | 102702
P00249 | 47.5 | -15 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.1 | -11.73 | 23.4 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 738.4 | 13.7 | 4.71 | - | 81291 | 0 | 81291
P00252 | 47.5 | -16 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.6 | -12.18 | 24.4 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 777.2 | 15.6 | 4.45 | - | 85309 | 0 | 85309
P00253 | 55 | -20 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.59 | -14.23 | 29.2 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 980.8 | 26.6 | 3.54 | - | 101373 | 0 | 101373
P00254 | 55 | -15 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.98 | -11.62 | 23.1 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 764.5 | 15.4 | 3.85 | - | 80288 | 0 | 80288
P00255 | 55 | -10 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.02 | -9.27 | 17.9 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 529.3 | 7.1 | 4.55 | - | 56457 | 0 | 56457
P00256 | 55 | -5 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.44 | -6.75 | 13.2 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 255.6 | 1.6 | 5.57 | - | 27679 | 0 | 27679
P00257 | 55 | -16 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.54 | -12.12 | 24.3 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 810 | 17.5 | 3.75 | - | 84790 | 0 | 84790
P00258 | 62.5 | -20 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.61 | -14.25 | 29.2 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1033.8 | 30.4 | 3.22 | - | 101503 | 0 | 101503
P00259 | 62.5 | -15 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.91 | -11.57 | 23 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 798.8 | 17.3 | 3.45 | - | 79755 | 0 | 79755
P00260 | 62.5 | -10 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.99 | -9.25 | 17.8 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 554.2 | 8.1 | 3.94 | - | 56246 | 0 | 56246
P00261 | 62.5 | -5 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.52 | -6.8 | 13.3 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 274.9 | 1.8 | 4.74 | - | 28343 | 0 | 28343
P00262 | 62.5 | -16 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.45 | -12.04 | 24.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 844.8 | 19.6 | 3.38 | - | 84074 | 0 | 84074
P00263 | 70 | -20 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.43 | -14.03 | 28.8 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1076.6 | 33.9 | 3 | - | 100040 | 0 | 100040
P00264 | 70 | -15 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.82 | -11.49 | 22.8 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 835.9 | 19.5 | 3.17 | - | 79057 | 0 | 79057
P00265 | 70 | -10 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -5.89 | -9.17 | 17.7 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 575.7 | 9.1 | 3.5 | - | 55398 | 0 | 55398
P00266 | 70 | -5 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.48 | -6.77 | 13.2 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 286.2 | 2 | 4.13 | - | 28000 | 0 | 28000
P00267 | 70 | -16 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.35 | -11.95 | 23.9 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 884.2 | 22.1 | 3.12 | - | 83334 | 0 | 83334
P00268 | 56 | -20 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -11.58 | -14.21 | 29.1 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 985.9 | 27 | 3.49 | - | 101225 | 0 | 101225
P00269 | 56 | -15 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -8.98 | -11.62 | 23.1 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 769.5 | 15.7 | 3.78 | - | 80288 | 0 | 80288
P00270 | 56 | -10 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -6.01 | -9.27 | 17.9 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 532.5 | 7.3 | 4.45 | - | 56432 | 0 | 56432
P00271 | 56 | -5 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -2.51 | -6.79 | 13.3 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 262.3 | 1.6 | 5.5 | - | 28225 | 0 | 28225
P00272 | 56 | -16 | 1 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 1 | -4.48 | 10 | -9.53 | -12.11 | 24.3 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 814.6 | 17.8 | 3.7 | - | 84719 | 0 | 84719
P00288 | 47.5 | -20 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.85 | -13.39 | 27.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1048 | 28.7 | 3.97 | - | 113639 | 0 | 113639
P00292 | 47.5 | -16 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.87 | -11.54 | 22.9 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 863 | 18.5 | 4.45 | - | 94720 | 0 | 94720
P00293 | 55 | -20 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.75 | -13.29 | 27.1 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1090.6 | 32.1 | 3.48 | - | 112720 | 0 | 112720
P00294 | 55 | -15 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.21 | -10.98 | 21.6 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 841.5 | 18.3 | 3.77 | - | 88367 | 0 | 88367
P00295 | 55 | -10 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.48 | -8.87 | 17.1 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 582.2 | 8.6 | 4.36 | - | 62096 | 0 | 62096
P00296 | 55 | -5 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.31 | -6.66 | 13 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 293.2 | 1.9 | 5.41 | - | 31752 | 0 | 31752
P00297 | 55 | -16 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.73 | -11.42 | 22.6 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 891.9 | 20.8 | 3.69 | - | 93373 | 0 | 93373
P00298 | 62.5 | -20 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.64 | -13.18 | 26.8 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1137.4 | 36 | 3.19 | - | 111680 | 0 | 111680
P00299 | 62.5 | -15 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.17 | -10.94 | 21.5 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 880.5 | 20.6 | 3.39 | - | 87911 | 0 | 87911
P00300 | 62.5 | -10 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.45 | -8.85 | 17 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 609.2 | 9.7 | 3.78 | - | 61827 | 0 | 61827
P00301 | 62.5 | -5 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.25 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 302.1 | 2.1 | 4.47 | - | 31149 | 0 | 31149
P00302 | 62.5 | -16 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.65 | -11.34 | 22.5 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 930.2 | 23.2 | 3.34 | - | 92568 | 0 | 92568
P00303 | 70 | -20 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.46 | -12.99 | 26.4 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1182.7 | 39.8 | 2.97 | - | 109899 | 0 | 109899
P00304 | 70 | -15 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.08 | -10.87 | 21.4 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 921.2 | 23.1 | 3.12 | - | 87126 | 0 | 87126
P00305 | 70 | -10 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.41 | -8.82 | 17 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 638.3 | 10.9 | 3.4 | - | 61421 | 0 | 61421
P00306 | 70 | -5 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.26 | -6.62 | 13 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 319.3 | 2.3 | 3.96 | - | 31238 | 0 | 31238
P00307 | 70 | -16 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.54 | -11.25 | 22.3 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 971 | 26 | 3.07 | - | 91512 | 0 | 91512
P00308 | 56 | -20 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -10.74 | -13.27 | 27 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1096.5 | 32.6 | 3.44 | - | 112581 | 0 | 112581
P00309 | 56 | -15 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.21 | -10.97 | 21.6 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 846.4 | 18.6 | 3.71 | - | 88308 | 0 | 88308
P00310 | 56 | -10 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -5.47 | -8.87 | 17.1 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 585.6 | 8.7 | 4.25 | - | 62062 | 0 | 62062
P00311 | 56 | -5 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -2.31 | -6.66 | 13 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 295.3 | 1.9 | 5.25 | - | 31771 | 0 | 31771
P00312 | 56 | -16 | 1 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 1 | -4.48 | 10 | -8.73 | -11.41 | 22.6 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 897.2 | 21.1 | 3.64 | - | 93309 | 0 | 93309
P00328 | 47.5 | -20 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.95 | -12.5 | 25.2 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1124.3 | 33 | 3.92 | - | 121914 | 0 | 121914
P00332 | 47.5 | -16 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.18 | -10.96 | 21.6 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 931.8 | 21.1 | 4.46 | - | 102275 | 0 | 102275
P00333 | 55 | -20 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.83 | -12.39 | 24.9 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1167.4 | 36.7 | 3.41 | - | 120662 | 0 | 120662
P00334 | 55 | -15 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.58 | -10.46 | 20.5 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 909.5 | 21 | 3.73 | - | 95516 | 0 | 95516
P00335 | 55 | -10 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.06 | -8.57 | 16.5 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 632.4 | 10 | 4.25 | - | 67456 | 0 | 67456
P00336 | 55 | -5 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -1.96 | -6.43 | 12.7 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 304.7 | 2 | 5.59 | - | 32993 | 0 | 32993
P00337 | 55 | -16 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8.01 | -10.81 | 21.2 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 958.4 | 23.5 | 3.66 | - | 100332 | 0 | 100332
P00338 | 62.5 | -20 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.71 | -12.28 | 24.7 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1214.9 | 40.8 | 3.13 | - | 119290 | 0 | 119290
P00339 | 62.5 | -15 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.49 | -10.4 | 20.3 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 947.2 | 23.4 | 3.35 | - | 94577 | 0 | 94577
P00340 | 62.5 | -10 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.03 | -8.55 | 16.4 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 661.3 | 11.2 | 3.69 | - | 67120 | 0 | 67120
P00341 | 62.5 | -5 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.08 | -6.5 | 12.8 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 332.7 | 2.5 | 4.28 | - | 34308 | 0 | 34308
P00342 | 62.5 | -16 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.91 | -10.73 | 21.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 996.8 | 26.2 | 3.31 | - | 99200 | 0 | 99200
P00343 | 70 | -20 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.51 | -12.1 | 24.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1260.2 | 44.9 | 2.93 | - | 117097 | 0 | 117097
P00344 | 70 | -15 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.41 | -10.33 | 20.1 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 989.6 | 26.1 | 3.09 | - | 93593 | 0 | 93593
P00345 | 70 | -10 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -4.99 | -8.52 | 16.4 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 693 | 12.6 | 3.34 | - | 66679 | 0 | 66679
P00346 | 70 | -5 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.09 | -6.51 | 12.8 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 351.5 | 3 | 3.8 | - | 34389 | 0 | 34389
P00347 | 70 | -16 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.91 | -10.73 | 21.1 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1052.5 | 29.8 | 3.05 | - | 99200 | 0 | 99200
P00348 | 56 | -20 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -9.82 | -12.38 | 24.9 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1173.5 | 37.2 | 3.37 | - | 120492 | 0 | 120492
P00349 | 56 | -15 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -7.57 | -10.46 | 20.4 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 914.4 | 21.3 | 3.67 | - | 95407 | 0 | 95407
P00350 | 56 | -10 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -5.06 | -8.57 | 16.5 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 636.1 | 10.1 | 4.15 | - | 67415 | 0 | 67415
P00351 | 56 | -5 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -2.07 | -6.49 | 12.8 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 317.1 | 2.2 | 4.99 | - | 34116 | 0 | 34116
P00352 | 56 | -16 | 1 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 1 | -4.48 | 10 | -8 | -10.8 | 21.2 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 963.5 | 23.9 | 3.6 | - | 100211 | 0 | 100211
P00368 | 47.5 | -20 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.36 | -11.96 | 23.9 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1206.9 | 36.8 | 3.96 | - | 130868 | 0 | 130868
P00372 | 47.5 | -16 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.49 | -10.4 | 20.3 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 977.3 | 23.2 | 4.42 | - | 107270 | 0 | 107270
P00373 | 55 | -20 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.23 | -11.84 | 23.6 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1250.4 | 40.7 | 3.44 | - | 129235 | 0 | 129235
P00374 | 55 | -15 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.03 | -10.03 | 19.5 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 966.1 | 23.2 | 3.72 | - | 101455 | 0 | 101455
P00375 | 55 | -10 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.75 | -8.35 | 16 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 680.5 | 11.4 | 4.16 | - | 72584 | 0 | 72584
P00376 | 55 | -5 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.83 | -6.34 | 12.5 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 330.4 | 2.3 | 5.48 | - | 35776 | 0 | 35776
P00377 | 55 | -16 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.56 | -10.45 | 20.4 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1033.1 | 26.9 | 3.62 | - | 108156 | 0 | 108156
P00378 | 62.5 | -20 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.1 | -11.73 | 23.4 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1299.6 | 45.2 | 3.16 | - | 127607 | 0 | 127607
P00379 | 62.5 | -15 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.95 | -9.95 | 19.4 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1005.2 | 25.8 | 3.35 | - | 100368 | 0 | 100368
P00380 | 62.5 | -10 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.71 | -8.32 | 16 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 710.8 | 12.8 | 3.61 | - | 72135 | 0 | 72135
P00381 | 62.5 | -5 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.91 | -6.39 | 12.6 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 356.2 | 3 | 4.2 | - | 36728 | 0 | 36728
P00382 | 62.5 | -16 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.45 | -10.36 | 20.2 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1072.8 | 29.7 | 3.28 | - | 106759 | 0 | 106759
P00383 | 70 | -20 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -8.89 | -11.55 | 22.9 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1344.1 | 50.1 | 2.91 | - | 124896 | 0 | 124896
P00384 | 70 | -15 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -6.94 | -9.94 | 19.4 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1060.6 | 29.5 | 3.07 | - | 100307 | 0 | 100307
P00385 | 70 | -10 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.67 | -8.29 | 15.9 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 743.7 | 14.3 | 3.27 | - | 71561 | 0 | 71561
P00386 | 70 | -5 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.92 | -6.39 | 12.6 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 376.2 | 3.6 | 3.72 | - | 36809 | 0 | 36809
P00387 | 70 | -16 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.38 | -10.31 | 20.1 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1123.1 | 33.4 | 3.02 | - | 105847 | 0 | 105847
P00388 | 56 | -20 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -9.21 | -11.83 | 23.6 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1256.8 | 41.3 | 3.4 | - | 129040 | 0 | 129040
P00389 | 56 | -15 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.02 | -10.02 | 19.5 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 971.1 | 23.6 | 3.66 | - | 101319 | 0 | 101319
P00390 | 56 | -10 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -4.74 | -8.35 | 16 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 684.6 | 11.6 | 4.06 | - | 72554 | 0 | 72554
P00391 | 56 | -5 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -1.9 | -6.38 | 12.6 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 339.8 | 2.6 | 4.88 | - | 36563 | 0 | 36563
P00392 | 56 | -16 | 1 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 1 | -4.48 | 10 | -7.51 | -10.41 | 20.3 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1033.8 | 27 | 3.58 | - | 107518 | 0 | 107518
P00408 | 47.5 | -20 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.09 | -13.65 | 27.9 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 991.4 | 26 | 4.01 | - | 107504 | 0 | 107504
P00409 | 47.5 | -15 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.59 | -11.29 | 22.4 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 774.4 | 15.1 | 4.62 | - | 85251 | 0 | 85251
P00412 | 47.5 | -16 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.14 | -11.77 | 23.5 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 821.4 | 17.2 | 4.42 | - | 90161 | 0 | 90161
P00413 | 55 | -20 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.05 | -13.6 | 27.8 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1036.5 | 29.8 | 3.46 | - | 107127 | 0 | 107127
P00414 | 55 | -15 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.54 | -11.26 | 22.3 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 808 | 17 | 3.8 | - | 84852 | 0 | 84852
P00415 | 55 | -10 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.7 | -9.04 | 17.4 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 558.4 | 8 | 4.39 | - | 59558 | 0 | 59558
P00416 | 55 | -5 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.32 | -6.66 | 13.1 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 272.5 | 1.7 | 5.45 | - | 29509 | 0 | 29509
P00417 | 55 | -16 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.05 | -11.69 | 23.3 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 853.7 | 19.2 | 3.71 | - | 89366 | 0 | 89366
P00418 | 62.5 | -20 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.95 | -13.5 | 27.5 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1082 | 33.3 | 3.17 | - | 106243 | 0 | 106243
P00419 | 62.5 | -15 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.46 | -11.18 | 22.1 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 842.2 | 19 | 3.41 | - | 84094 | 0 | 84094
P00420 | 62.5 | -10 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.67 | -9.02 | 17.3 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 584.5 | 9 | 3.81 | - | 59317 | 0 | 59317
P00421 | 62.5 | -5 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.35 | -6.69 | 13.1 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 289.1 | 1.9 | 4.54 | - | 29805 | 0 | 29805
P00422 | 62.5 | -16 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.97 | -11.62 | 23.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 890.5 | 21.5 | 3.36 | - | 88623 | 0 | 88623
P00423 | 70 | -20 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -10.8 | -13.34 | 27.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1128.9 | 37.3 | 2.94 | - | 104901 | 0 | 104901
P00424 | 70 | -15 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.38 | -11.12 | 21.9 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 881.6 | 21.4 | 3.14 | - | 83378 | 0 | 83378
P00425 | 70 | -10 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.64 | -9 | 17.3 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 613.5 | 10.2 | 3.44 | - | 59036 | 0 | 59036
P00426 | 70 | -5 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.37 | -6.7 | 13.1 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 305.9 | 2.2 | 4.01 | - | 29934 | 0 | 29934
P00427 | 70 | -16 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.86 | -11.53 | 22.9 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 930.3 | 24.1 | 3.09 | - | 87680 | 0 | 87680
P00428 | 56 | -20 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -11.05 | -13.6 | 27.8 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1043.4 | 30.3 | 3.42 | - | 107127 | 0 | 107127
P00429 | 56 | -15 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -8.54 | -11.25 | 22.2 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 812.5 | 17.3 | 3.74 | - | 84772 | 0 | 84772
P00430 | 56 | -10 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -5.7 | -9.04 | 17.4 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 561.7 | 8.1 | 4.29 | - | 59528 | 0 | 59528
P00431 | 56 | -5 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -2.32 | -6.67 | 13.1 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 274.4 | 1.8 | 5.29 | - | 29526 | 0 | 29526
P00432 | 56 | -16 | 1 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 1 | -4.48 | 10 | -9.04 | -11.68 | 23.3 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 858.4 | 19.5 | 3.66 | - | 89279 | 0 | 89279
P00451 | 47.5 | -20 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.61 | -12.5 | 43.6 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1096.4 | 29.9 | 4.14 | - | 118879 | 0 | 118879
P00456 | 47.5 | -16 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.21 | -10.46 | 35.3 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 943.4 | 20.6 | 4.71 | - | 103543 | 0 | 103543
P00457 | 55 | -20 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.48 | -12.38 | 43.2 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1142.5 | 33.6 | 3.61 | - | 118087 | 0 | 118087
P00458 | 55 | -15 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.54 | -9.93 | 33.3 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 945.1 | 21.1 | 3.98 | - | 99255 | 0 | 99255
P00459 | 55 | -10 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.59 | -7.78 | 25.8 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 753.9 | 12.4 | 4.6 | - | 80408 | 0 | 80408
P00460 | 55 | -5 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.03 | -5.38 | 19.1 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 532.5 | 5.9 | 6.02 | - | 57661 | 0 | 57661
P00462 | 55 | -16 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.12 | -10.39 | 35 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 983.8 | 23.1 | 3.91 | - | 102987 | 0 | 102987
P00463 | 62.5 | -20 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.33 | -12.24 | 42.6 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1192.3 | 37.7 | 3.29 | - | 117074 | 0 | 117074
P00464 | 62.5 | -15 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.45 | -9.87 | 33 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 988.5 | 23.7 | 3.57 | - | 98696 | 0 | 98696
P00465 | 62.5 | -10 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.49 | -7.71 | 25.6 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 785.9 | 13.9 | 3.97 | - | 79764 | 0 | 79764
P00466 | 62.5 | -5 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.1 | -5.42 | 19.2 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 563.1 | 6.9 | 4.62 | - | 58067 | 0 | 58067
P00467 | 62.5 | 0 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.47 | -3.15 | 14.7 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 337.3 | 2.1 | 5.75 | - | 35313 | 0 | 35313
P00468 | 62.5 | -16 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.12 | -10.39 | 35 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1034.8 | 26.5 | 3.5 | - | 102985 | 0 | 102985
P00469 | 70 | -20 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.08 | -12.01 | 41.6 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1242.8 | 42.1 | 3.07 | - | 115483 | 0 | 115483
P00470 | 70 | -15 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.44 | -9.86 | 33 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1043 | 27.2 | 3.27 | - | 98645 | 0 | 98645
P00471 | 70 | -10 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.42 | -7.66 | 25.5 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 824.3 | 15.8 | 3.58 | - | 79320 | 0 | 79320
P00472 | 70 | -5 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.11 | -5.43 | 19.3 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 594.4 | 7.9 | 4.03 | - | 58157 | 0 | 58157
P00473 | 70 | 0 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | 2.46 | -3.15 | 14.7 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 355.8 | 2.5 | 4.91 | - | 35371 | 0 | 35371
P00474 | 70 | -16 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.02 | -10.3 | 34.7 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1085.4 | 30 | 3.22 | - | 102300 | 0 | 102300
P00475 | 56 | -20 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 8 | 0.19 | 10 | -10.47 | -12.37 | 43.1 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1148.9 | 34.1 | 3.56 | - | 117967 | 0 | 117967
P00476 | 56 | -15 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -7.53 | -9.93 | 33.3 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 950.7 | 21.4 | 3.91 | - | 99185 | 0 | 99185
P00477 | 56 | -10 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -4.54 | -7.75 | 25.7 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 755.8 | 12.5 | 4.5 | - | 80095 | 0 | 80095
P00478 | 56 | -5 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -1.16 | -5.46 | 19.3 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 543.3 | 6.2 | 5.51 | - | 58455 | 0 | 58455
P00480 | 56 | -16 | 8 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 8 | 0.19 | 10 | -8.11 | -10.38 | 35 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 989.5 | 23.5 | 3.85 | - | 102913 | 0 | 102913
P00499 | 47.5 | -20 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -9.13 | -11.2 | 38.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1239.7 | 37.1 | 4.12 | - | 134426 | 0 | 134426
P00505 | 55 | -20 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -9 | -11.09 | 37.8 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1290.7 | 41.6 | 3.57 | - | 133399 | 0 | 133399
P00506 | 55 | -15 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.42 | -9.1 | 30.2 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1077.8 | 26.6 | 3.91 | - | 113181 | 0 | 113181
P00507 | 55 | -10 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.61 | -7.1 | 23.8 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 853.8 | 15.5 | 4.48 | - | 91063 | 0 | 91063
P00508 | 55 | -5 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.4 | -4.97 | 18.2 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 608.2 | 7.5 | 5.8 | - | 65864 | 0 | 65864
P00510 | 55 | -16 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.96 | -9.5 | 31.7 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1121.5 | 29.2 | 3.83 | - | 117409 | 0 | 117409
P00511 | 62.5 | -20 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.77 | -10.9 | 37.1 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1340 | 46.1 | 3.27 | - | 131572 | 0 | 131572
P00512 | 62.5 | -15 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.34 | -9.03 | 30 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1126.9 | 30 | 3.49 | - | 112514 | 0 | 112514
P00513 | 62.5 | -10 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.54 | -7.06 | 23.6 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 891.9 | 17.5 | 3.86 | - | 90517 | 0 | 90517
P00514 | 62.5 | -5 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.49 | -5.03 | 18.3 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 646.1 | 8.8 | 4.4 | - | 66623 | 0 | 66623
P00515 | 62.5 | 0 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.83 | -2.92 | 14.3 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 387.5 | 3.1 | 5.45 | - | 40567 | 0 | 40567
P00516 | 62.5 | -16 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.88 | -9.43 | 31.4 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1173.2 | 33.1 | 3.44 | - | 116758 | 0 | 116758
P00517 | 70 | -20 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.54 | -10.72 | 36.3 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1396.8 | 51.5 | 3.03 | - | 129789 | 0 | 129789
P00518 | 70 | -15 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.23 | -8.95 | 29.7 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1180.5 | 33.9 | 3.21 | - | 111653 | 0 | 111653
P00519 | 70 | -10 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.44 | -6.99 | 23.4 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 932.8 | 19.7 | 3.48 | - | 89753 | 0 | 89753
P00520 | 70 | -5 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.46 | -5.01 | 18.3 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 678.5 | 10.1 | 3.87 | - | 66387 | 0 | 66387
P00521 | 70 | 0 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | 2.82 | -2.93 | 14.3 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 408.5 | 3.8 | 4.65 | - | 40617 | 0 | 40617
P00522 | 70 | -16 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.73 | -9.32 | 31 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1226.5 | 37.2 | 3.16 | - | 115594 | 0 | 115594
P00523 | 56 | -20 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 8 | 0.19 | 10 | -8.98 | -11.07 | 37.8 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1297.7 | 42.2 | 3.52 | - | 133237 | 0 | 133237
P00524 | 56 | -15 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.4 | -9.08 | 30.1 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1082.7 | 27 | 3.84 | - | 112957 | 0 | 112957
P00525 | 56 | -10 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -3.6 | -7.1 | 23.7 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 858.7 | 15.7 | 4.37 | - | 90997 | 0 | 90997
P00526 | 56 | -5 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -0.52 | -5.05 | 18.3 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 620.9 | 7.9 | 5.28 | - | 66810 | 0 | 66810
P00528 | 56 | -16 | 8 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 8 | 0.19 | 10 | -6.96 | -9.5 | 31.7 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1128.9 | 29.7 | 3.77 | - | 117409 | 0 | 117409
P00547 | 47.5 | -20 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.85 | -10.17 | 34.2 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1366.8 | 44 | 4.12 | - | 148207 | 0 | 148207
P00553 | 55 | -20 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.62 | -9.99 | 33.5 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1413 | 48.5 | 3.57 | - | 146040 | 0 | 146040
P00554 | 55 | -15 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.4 | -8.4 | 27.7 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1193.5 | 31.9 | 3.86 | - | 125334 | 0 | 125334
P00555 | 55 | -10 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.75 | -6.52 | 22.1 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 942.1 | 18.4 | 4.42 | - | 100481 | 0 | 100481
P00556 | 55 | -5 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.13 | -4.63 | 17.4 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 679.8 | 9.1 | 5.6 | - | 73606 | 0 | 73606
P00558 | 55 | -16 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.88 | -8.7 | 28.8 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1240.2 | 35.1 | 3.78 | - | 129832 | 0 | 129832
P00559 | 62.5 | -20 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.52 | -9.92 | 33.2 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1478.7 | 54.6 | 3.24 | - | 145195 | 0 | 145195
P00560 | 62.5 | -15 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.2 | -8.2 | 27.2 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1235.9 | 35.8 | 3.41 | - | 123397 | 0 | 123397
P00561 | 62.5 | -10 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.58 | -6.41 | 21.8 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 974.8 | 20.7 | 3.76 | - | 98937 | 0 | 98937
P00562 | 62.5 | -5 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.08 | -4.66 | 17.4 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 718.3 | 10.7 | 4.26 | - | 74070 | 0 | 74070
P00563 | 62.5 | 0 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.19 | -2.7 | 14 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 429.2 | 4 | 5.18 | - | 44927 | 0 | 44927
P00564 | 62.5 | -16 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.77 | -8.62 | 28.6 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1293.9 | 39.3 | 3.4 | - | 128763 | 0 | 128763
P00565 | 70 | -20 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.25 | -9.71 | 32.4 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1534.6 | 60.3 | 3.03 | - | 142598 | 0 | 142598
P00566 | 70 | -15 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.09 | -8.09 | 26.9 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1294.3 | 40.3 | 3.14 | - | 122415 | 0 | 122415
P00567 | 70 | -10 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.62 | -6.43 | 21.8 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1031.5 | 23.9 | 3.39 | - | 99249 | 0 | 99249
P00568 | 70 | -5 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.11 | -4.64 | 17.4 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 753.6 | 12.1 | 3.76 | - | 73734 | 0 | 73734
P00569 | 70 | 0 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 3.19 | -2.7 | 14 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 452.6 | 4.6 | 4.41 | - | 45000 | 0 | 45000
P00570 | 70 | -16 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.64 | -8.53 | 28.3 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1353.7 | 44.2 | 3.14 | - | 127584 | 0 | 127584
P00571 | 56 | -20 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 8 | 0.19 | 10 | -7.68 | -10.05 | 33.7 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1428.6 | 49.8 | 3.5 | - | 146678 | 0 | 146678
P00572 | 56 | -15 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.39 | -8.39 | 27.6 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1200.1 | 32.4 | 3.79 | - | 125214 | 0 | 125214
P00573 | 56 | -10 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -2.74 | -6.51 | 22.1 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 947.2 | 18.7 | 4.31 | - | 100385 | 0 | 100385
P00574 | 56 | -5 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | 0.05 | -4.68 | 17.5 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 690.7 | 9.6 | 5.12 | - | 74319 | 0 | 74319
P00576 | 56 | -16 | 8 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 8 | 0.19 | 10 | -5.87 | -8.69 | 28.8 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1247.2 | 35.6 | 3.72 | - | 129708 | 0 | 129708
P00595 | 47.5 | -20 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.74 | -9.33 | 31.1 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1476.2 | 50.2 | 4.16 | - | 160066 | 0 | 160066
P00601 | 55 | -20 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.61 | -9.23 | 30.7 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1534.8 | 55.9 | 3.56 | - | 158635 | 0 | 158635
P00602 | 55 | -15 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.53 | -7.74 | 25.7 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1295.7 | 36.9 | 3.84 | - | 136065 | 0 | 136065
P00603 | 55 | -10 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.09 | -6.09 | 20.9 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1026.9 | 21.9 | 4.28 | - | 109524 | 0 | 109524
P00606 | 55 | -16 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.98 | -8.05 | 26.7 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1345.9 | 40.4 | 3.77 | - | 140894 | 0 | 140894
P00607 | 62.5 | -20 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.4 | -9.08 | 30.1 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1592.1 | 61.8 | 3.24 | - | 156328 | 0 | 156328
P00608 | 62.5 | -15 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.42 | -7.66 | 25.4 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1350.1 | 41.3 | 3.42 | - | 134800 | 0 | 134800
P00609 | 62.5 | -10 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.98 | -5.98 | 20.7 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1067.8 | 24.4 | 3.7 | - | 108376 | 0 | 108376
P00610 | 62.5 | -5 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.56 | -4.35 | 16.8 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 782.7 | 12.5 | 4.18 | - | 80706 | 0 | 80706
P00611 | 62.5 | 0 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.43 | -2.57 | 13.7 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 474 | 4.8 | 4.97 | - | 49625 | 0 | 49625
P00612 | 62.5 | -16 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.83 | -7.95 | 26.3 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1399.2 | 45.1 | 3.37 | - | 139240 | 0 | 139240
P00613 | 70 | -20 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.2 | -8.93 | 29.6 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1658.9 | 68.8 | 3.01 | - | 154150 | 0 | 154150
P00614 | 70 | -15 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.26 | -7.55 | 25.1 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1407 | 46.1 | 3.14 | - | 133073 | 0 | 133073
P00615 | 70 | -10 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -1.92 | -5.92 | 20.6 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1118.6 | 27.6 | 3.34 | - | 107637 | 0 | 107637
P00616 | 70 | -5 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.68 | -4.32 | 16.7 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 811.7 | 14.1 | 3.64 | - | 79424 | 0 | 79424
P00617 | 70 | 0 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 3.42 | -2.58 | 13.7 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 499.7 | 5.4 | 4.25 | - | 49684 | 0 | 49684
P00618 | 70 | -16 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.58 | -7.77 | 25.8 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1448.4 | 50.2 | 3.08 | - | 136515 | 0 | 136515
P00619 | 56 | -20 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 8 | 0.19 | 10 | -6.56 | -9.2 | 30.6 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1540 | 56.6 | 3.5 | - | 158120 | 0 | 158120
P00620 | 56 | -15 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.52 | -7.73 | 25.7 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1302.7 | 37.4 | 3.77 | - | 135911 | 0 | 135911
P00621 | 56 | -10 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -2.1 | -6.1 | 20.9 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1034.2 | 22.2 | 4.19 | - | 109605 | 0 | 109605
P00622 | 56 | -5 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | 0.54 | -4.37 | 16.9 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 752.4 | 11.2 | 5.04 | - | 80960 | 0 | 80960
P00624 | 56 | -16 | 8 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 8 | 0.19 | 10 | -4.96 | -8.04 | 26.6 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1353 | 41 | 3.7 | - | 140717 | 0 | 140717
P00643 | 47.5 | -20 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.82 | -8.65 | 28.7 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1569.3 | 55.8 | 4.21 | - | 170157 | 0 | 170157
P00649 | 55 | -20 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.65 | -8.53 | 28.3 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1626.9 | 61.8 | 3.55 | - | 168149 | 0 | 168149
P00650 | 55 | -15 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.82 | -7.25 | 24.2 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1385.9 | 41.5 | 3.81 | - | 145543 | 0 | 145543
P00651 | 55 | -10 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.59 | -5.75 | 20 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1107.2 | 24.5 | 4.35 | - | 118088 | 0 | 118088
P00654 | 55 | -16 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.23 | -7.53 | 25 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1438.6 | 45.4 | 3.75 | - | 150605 | 0 | 150605
P00655 | 62.5 | -20 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.45 | -8.39 | 27.8 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1687.7 | 68.2 | 3.24 | - | 165712 | 0 | 165712
P00656 | 62.5 | -15 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.7 | -7.17 | 23.9 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1442.9 | 46.4 | 3.4 | - | 144069 | 0 | 144069
P00657 | 62.5 | -10 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.43 | -5.64 | 19.8 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1144.4 | 27.7 | 3.65 | - | 116148 | 0 | 116148
P00658 | 62.5 | -5 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.01 | -4.06 | 16.3 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 834.4 | 14 | 4.11 | - | 86040 | 0 | 86040
P00659 | 62.5 | 0 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.67 | -2.4 | 13.5 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 509.4 | 5.4 | 4.89 | - | 53326 | 0 | 53326
P00660 | 62.5 | -16 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.03 | -7.39 | 24.6 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1488.4 | 50 | 3.38 | - | 148124 | 0 | 148124
P00661 | 70 | -20 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.27 | -8.27 | 27.3 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1758.2 | 75.5 | 3.02 | - | 163374 | 0 | 163374
P00662 | 70 | -15 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.57 | -7.08 | 23.7 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1506.4 | 51.9 | 3.13 | - | 142478 | 0 | 142478
P00663 | 70 | -10 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.39 | -5.62 | 19.7 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1201.5 | 31.4 | 3.3 | - | 115607 | 0 | 115607
P00664 | 70 | -5 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 1.05 | -4.04 | 16.3 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 874.1 | 15.8 | 3.64 | - | 85532 | 0 | 85532
P00665 | 70 | 0 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | 3.68 | -2.39 | 13.5 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 534.3 | 6.1 | 4.15 | - | 53118 | 0 | 53118
P00666 | 70 | -16 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.9 | -7.3 | 24.3 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1554.9 | 56.1 | 3.11 | - | 146545 | 0 | 146545
P00667 | 56 | -20 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 8 | 0.19 | 10 | -5.63 | -8.52 | 28.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1634.9 | 62.6 | 3.5 | - | 167858 | 0 | 167858
P00668 | 56 | -15 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -3.8 | -7.24 | 24.1 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1393.3 | 42.2 | 3.74 | - | 145363 | 0 | 145363
P00669 | 56 | -10 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -1.58 | -5.74 | 20 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1113.5 | 24.9 | 4.23 | - | 118007 | 0 | 118007
P00672 | 56 | -16 | 8 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 8 | 0.19 | 10 | -4.21 | -7.52 | 25 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1446.1 | 46.1 | 3.68 | - | 150403 | 0 | 150403
P00691 | 47.5 | -20 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.35 | -10.57 | 35.7 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1307.1 | 40.7 | 4.12 | - | 141726 | 0 | 141726
P00697 | 55 | -20 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.2 | -10.45 | 35.3 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1358.7 | 45.5 | 3.55 | - | 140427 | 0 | 140427
P00698 | 55 | -15 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.82 | -8.65 | 28.7 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1140.2 | 29.3 | 3.9 | - | 119739 | 0 | 119739
P00699 | 55 | -10 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.07 | -6.73 | 22.7 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 899 | 17.2 | 4.37 | - | 95887 | 0 | 95887
P00700 | 55 | -5 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.11 | -4.78 | 17.7 | R290 (Propane) | Countercurrent | -5 | 5 | 55 | 60 | 648.6 | 8.4 | 5.68 | - | 70231 | 0 | 70231
P00702 | 55 | -16 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.41 | -9.09 | 30.2 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1193.2 | 32.7 | 3.79 | - | 124907 | 0 | 124907
P00703 | 62.5 | -20 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.06 | -10.34 | 34.8 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1417.8 | 50.8 | 3.26 | - | 139216 | 0 | 139216
P00704 | 62.5 | -15 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.79 | -8.63 | 28.6 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1197.2 | 33.5 | 3.46 | - | 119539 | 0 | 119539
P00705 | 62.5 | -10 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.99 | -6.68 | 22.5 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 938.5 | 19.4 | 3.77 | - | 95247 | 0 | 95247
P00706 | 62.5 | -5 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.14 | -4.8 | 17.8 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 683.9 | 9.8 | 4.32 | - | 70523 | 0 | 70523
P00707 | 62.5 | 0 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3.05 | -2.79 | 14.1 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 410 | 3.7 | 5.25 | - | 42917 | 0 | 42917
P00708 | 62.5 | -16 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.24 | -8.96 | 29.7 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1240.1 | 36.5 | 3.41 | - | 123415 | 0 | 123415
P00709 | 70 | -20 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -7.85 | -10.17 | 34.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1478.2 | 56.7 | 3.02 | - | 137356 | 0 | 137356
P00710 | 70 | -15 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.61 | -8.5 | 28.2 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1247.4 | 37.4 | 3.19 | - | 117978 | 0 | 117978
P00711 | 70 | -10 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -2.91 | -6.63 | 22.4 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 982.7 | 21.9 | 3.41 | - | 94561 | 0 | 94561
P00712 | 70 | -5 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.11 | -4.78 | 17.7 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 717.8 | 11.2 | 3.77 | - | 70231 | 0 | 70231
P00713 | 70 | 0 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | 3.04 | -2.79 | 14.1 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 432.4 | 4.2 | 4.47 | - | 42990 | 0 | 42990
P00714 | 70 | -16 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.07 | -8.84 | 29.3 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1294 | 40.9 | 3.14 | - | 121960 | 0 | 121960
P00715 | 56 | -20 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 8 | 0.19 | 10 | -8.19 | -10.44 | 35.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1366.5 | 46.2 | 3.51 | - | 140300 | 0 | 140300
P00716 | 56 | -15 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -5.88 | -8.7 | 28.8 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1153.1 | 30.2 | 3.8 | - | 120310 | 0 | 120310
P00717 | 56 | -10 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -3.06 | -6.73 | 22.7 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 904 | 17.5 | 4.26 | - | 95807 | 0 | 95807
P00718 | 56 | -5 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -0.17 | -4.82 | 17.8 | R290 (Propane) | Countercurrent | -5 | 5 | 56 | 60 | 658.2 | 8.8 | 5.19 | - | 70826 | 0 | 70826
P00720 | 56 | -16 | 8 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 8 | 0.19 | 10 | -6.4 | -9.08 | 30.1 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1199.9 | 33.2 | 3.73 | - | 124788 | 0 | 124788
P00742 | 47.5 | -20 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -8.34 | -9.79 | 56.8 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1341.9 | 41.1 | 4.29 | - | 145503 | 0 | 145503
P00749 | 55 | -20 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -8.12 | -9.63 | 55.7 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1394.8 | 46.1 | 3.67 | - | 144158 | 0 | 144158
P00750 | 55 | -15 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.46 | -7.7 | 44.2 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1214.2 | 31.6 | 4.02 | - | 127514 | 0 | 127514
P00751 | 55 | -10 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.49 | -5.69 | 34.4 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1021.9 | 20.3 | 4.62 | - | 108999 | 0 | 108999
P00755 | 55 | -16 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.09 | -8.09 | 46.7 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1255.6 | 34.4 | 3.94 | - | 131445 | 0 | 131445
P00756 | 62.5 | -20 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.9 | -9.46 | 54.6 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1454.3 | 51.6 | 3.34 | - | 142795 | 0 | 142795
P00757 | 62.5 | -15 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.3 | -7.59 | 43.6 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1267.4 | 35.7 | 3.57 | - | 126544 | 0 | 126544
P00758 | 62.5 | -10 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.39 | -5.63 | 34.1 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1067.9 | 23 | 3.94 | - | 108380 | 0 | 108380
P00759 | 62.5 | -5 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.81 | -3.58 | 26.3 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 857.2 | 13.7 | 4.48 | - | 88391 | 0 | 88391
P00760 | 62.5 | 0 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.18 | -1.5 | 20.7 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 644.2 | 7.3 | 5.36 | - | 67438 | 0 | 67438
P00762 | 62.5 | -16 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.94 | -8.04 | 46.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1311.5 | 38.9 | 3.52 | - | 130516 | 0 | 130516
P00763 | 70 | -20 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -7.64 | -9.26 | 53.4 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1518.7 | 57.9 | 3.1 | - | 141117 | 0 | 141117
P00764 | 70 | -15 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.19 | -7.52 | 43.2 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1330.7 | 40.5 | 3.28 | - | 125862 | 0 | 125862
P00765 | 70 | -10 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.28 | -5.56 | 33.8 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1119 | 26.2 | 3.54 | - | 107676 | 0 | 107676
P00766 | 70 | -5 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 0.88 | -3.53 | 26.2 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 899.2 | 15.6 | 3.93 | - | 87989 | 0 | 87989
P00767 | 70 | 0 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 4.2 | -1.49 | 20.7 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 676.8 | 8.4 | 4.48 | - | 67285 | 0 | 67285
P00768 | 70 | 5 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | 7.93 | 0.71 | 16 | R290 (Propane) | Countercurrent | 5 | 5 | 70 | 60 | 436.1 | 3.5 | 5.48 | - | 44063 | 0 | 44063
P00769 | 70 | -16 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.73 | -7.89 | 45.3 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1371.3 | 43.9 | 3.23 | - | 129244 | 0 | 129244
P00770 | 56 | -20 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -8.1 | -9.61 | 55.6 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1402.4 | 46.8 | 3.62 | - | 143990 | 0 | 143990
P00771 | 56 | -15 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -5.44 | -7.69 | 44.1 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1221.3 | 32.2 | 3.94 | - | 127423 | 0 | 127423
P00772 | 56 | -10 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | 15 | 4.6 | 10 | -2.5 | -5.7 | 34.4 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1029.4 | 20.7 | 4.49 | - | 109087 | 0 | 109087
P00776 | 56 | -16 | 15 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 24 | 15 | 4.6 | 10 | -6.08 | -8.13 | 46.6 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1263.2 | 35 | 3.87 | - | 131375 | 0 | 131375
P00798 | 47.5 | -20 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.48 | -8.42 | 48.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1517.4 | 50.9 | 4.33 | - | 164535 | 0 | 164535
P00805 | 55 | -20 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.25 | -8.25 | 47.3 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1574.5 | 56.8 | 3.66 | - | 162734 | 0 | 162734
P00806 | 55 | -15 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.91 | -6.64 | 38.7 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1379.1 | 39.7 | 3.97 | - | 144831 | 0 | 144831
P00807 | 55 | -10 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.27 | -4.9 | 31 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1168 | 25.9 | 4.52 | - | 124575 | 0 | 124575
P00811 | 55 | -16 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.46 | -7.02 | 40.6 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1423.5 | 43.1 | 3.9 | - | 149021 | 0 | 149021
P00812 | 62.5 | -20 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.01 | -8.09 | 46.4 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1638.9 | 63.3 | 3.33 | - | 160920 | 0 | 160920
P00813 | 62.5 | -15 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.8 | -6.57 | 38.4 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1442 | 44.8 | 3.53 | - | 143980 | 0 | 143980
P00814 | 62.5 | -10 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.14 | -4.81 | 30.7 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1217.3 | 29.2 | 3.85 | - | 123547 | 0 | 123547
P00815 | 62.5 | -5 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.9 | -2.89 | 24.3 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 972.3 | 17.1 | 4.37 | - | 100263 | 0 | 100263
P00816 | 62.5 | 0 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.92 | -1.08 | 19.7 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 737.1 | 9.3 | 5.13 | - | 77165 | 0 | 77165
P00818 | 62.5 | -16 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.28 | -6.89 | 40 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1483.2 | 48.4 | 3.47 | - | 147606 | 0 | 147606
P00819 | 70 | -20 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -5.72 | -7.88 | 45.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1707.5 | 70.4 | 3.1 | - | 158667 | 0 | 158667
P00820 | 70 | -15 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.59 | -6.42 | 37.7 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1505 | 50.4 | 3.23 | - | 142340 | 0 | 142340
P00821 | 70 | -10 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.01 | -4.73 | 30.4 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1273.8 | 33.1 | 3.46 | - | 122570 | 0 | 122570
P00822 | 70 | -5 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 1.83 | -2.94 | 24.5 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 1030.6 | 19.9 | 3.83 | - | 100839 | 0 | 100839
P00823 | 70 | 0 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 4.95 | -1.05 | 19.6 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 773.9 | 10.7 | 4.3 | - | 76941 | 0 | 76941
P00824 | 70 | 5 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | 8.35 | 0.95 | 15.5 | R290 (Propane) | Countercurrent | 5 | 5 | 70 | 60 | 503.7 | 4.5 | 5.2 | - | 50892 | 0 | 50892
P00825 | 70 | -16 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.09 | -6.76 | 39.3 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1550.6 | 54.4 | 3.19 | - | 146147 | 0 | 146147
P00826 | 56 | -20 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -6.22 | -8.22 | 47.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1582.8 | 57.6 | 3.6 | - | 162508 | 0 | 162508
P00827 | 56 | -15 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -3.87 | -6.62 | 38.6 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1385.2 | 40.4 | 3.89 | - | 144521 | 0 | 144521
P00828 | 56 | -10 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | 15 | 4.6 | 10 | -1.26 | -4.9 | 31 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1174.9 | 26.3 | 4.39 | - | 124507 | 0 | 124507
P00832 | 56 | -16 | 15 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 33 | 15 | 4.6 | 10 | -4.44 | -7 | 40.5 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1431.5 | 43.7 | 3.83 | - | 148883 | 0 | 148883
P00854 | 47.5 | -20 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.95 | -7.35 | 42.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1678.9 | 60.7 | 4.4 | - | 182046 | 0 | 182046
P00861 | 55 | -20 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.65 | -7.15 | 41.3 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1735.5 | 66.9 | 3.68 | - | 179376 | 0 | 179376
P00862 | 55 | -15 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.54 | -5.73 | 34.5 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1524.3 | 47.5 | 3.95 | - | 160075 | 0 | 160075
P00863 | 55 | -10 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | -0.09 | -4.15 | 28.2 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1291.2 | 31 | 4.5 | - | 137722 | 0 | 137722
P00867 | 55 | -16 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.01 | -6.01 | 35.9 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1569.7 | 51.1 | 3.89 | - | 164320 | 0 | 164320
P00868 | 62.5 | -20 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.37 | -6.96 | 40.3 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1800.9 | 74.2 | 3.33 | - | 176828 | 0 | 176828
P00869 | 62.5 | -15 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.37 | -5.62 | 34 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1587.6 | 53.2 | 3.5 | - | 158519 | 0 | 158519
P00870 | 62.5 | -10 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0 | -4.09 | 27.9 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1348.7 | 35.1 | 3.8 | - | 136878 | 0 | 136878
P00871 | 62.5 | -5 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.63 | -2.44 | 23.1 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 1094.2 | 21.2 | 4.27 | - | 112828 | 0 | 112828
P00872 | 62.5 | 0 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.59 | -0.66 | 18.8 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 820.2 | 11.3 | 4.99 | - | 85862 | 0 | 85862
P00874 | 62.5 | -16 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.87 | -5.95 | 35.5 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1638.8 | 57.4 | 3.47 | - | 163085 | 0 | 163085
P00875 | 70 | -20 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.08 | -6.76 | 39.3 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1873.9 | 82.3 | 3.09 | - | 174123 | 0 | 174123
P00876 | 70 | -15 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.22 | -5.52 | 33.6 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1661.2 | 59.7 | 3.22 | - | 157118 | 0 | 157118
P00877 | 70 | -10 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 0.03 | -4.07 | 27.8 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1419.5 | 40.2 | 3.41 | - | 136591 | 0 | 136591
P00878 | 70 | -5 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 2.78 | -2.35 | 22.8 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 1139.4 | 24.2 | 3.7 | - | 111486 | 0 | 111486
P00879 | 70 | 0 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 5.62 | -0.64 | 18.7 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 860.9 | 13 | 4.19 | - | 85589 | 0 | 85589
P00880 | 70 | 5 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | 8.77 | 1.19 | 15.1 | R290 (Propane) | Countercurrent | 5 | 5 | 70 | 60 | 562.6 | 5.5 | 4.99 | - | 56844 | 0 | 56844
P00881 | 70 | -16 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.63 | -5.79 | 34.8 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1707.4 | 64.1 | 3.18 | - | 160917 | 0 | 160917
P00882 | 56 | -20 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -4.62 | -7.13 | 41.1 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1744.2 | 67.8 | 3.62 | - | 179085 | 0 | 179085
P00883 | 56 | -15 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -2.52 | -5.72 | 34.5 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1532.7 | 48.2 | 3.87 | - | 159907 | 0 | 159907
P00884 | 56 | -10 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | 15 | 4.6 | 10 | -0.08 | -4.14 | 28.1 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1298.8 | 31.5 | 4.36 | - | 137639 | 0 | 137639
P00888 | 56 | -16 | 15 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 44 | 15 | 4.6 | 10 | -3.01 | -6.01 | 35.9 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1580 | 52 | 3.82 | - | 164320 | 0 | 164320
P00917 | 55 | -20 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3.34 | -6.26 | 36.9 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1880 | 76.6 | 3.69 | - | 194310 | 0 | 194310
P00918 | 55 | -15 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.42 | -5 | 31.4 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1656.3 | 54.8 | 3.97 | - | 173943 | 0 | 173943
P00919 | 55 | -10 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.77 | -3.6 | 26.4 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1413.4 | 36.6 | 4.46 | - | 150752 | 0 | 150752
P00923 | 55 | -16 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.81 | -5.25 | 32.5 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1701.2 | 58.9 | 3.89 | - | 178093 | 0 | 178093
P00924 | 62.5 | -20 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3.09 | -6.09 | 36.1 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1951.9 | 84.7 | 3.34 | - | 191656 | 0 | 191656
P00925 | 62.5 | -15 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.22 | -4.87 | 30.9 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1720.9 | 61 | 3.49 | - | 171823 | 0 | 171823
P00926 | 62.5 | -10 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.89 | -3.53 | 26.2 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1473.2 | 41.2 | 3.75 | - | 149511 | 0 | 149511
P00927 | 62.5 | -5 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.39 | -1.98 | 21.9 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 1192.1 | 24.8 | 4.21 | - | 122926 | 0 | 122926
P00928 | 62.5 | 0 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.19 | -0.3 | 18 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 891.1 | 13.2 | 4.9 | - | 93286 | 0 | 93286
P00930 | 62.5 | -16 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.6 | -5.12 | 31.9 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1767.7 | 65.5 | 3.45 | - | 175914 | 0 | 175914
P00931 | 70 | -20 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -2.75 | -5.87 | 35.1 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 2024 | 93 | 3.11 | - | 188073 | 0 | 188073
P00932 | 70 | -15 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -0.99 | -4.72 | 30.3 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1791.5 | 68 | 3.21 | - | 169444 | 0 | 169444
P00933 | 70 | -10 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 1.01 | -3.45 | 25.9 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1539.7 | 46.4 | 3.39 | - | 148154 | 0 | 148154
P00934 | 70 | -5 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 3.53 | -1.9 | 21.7 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 1241.8 | 28.3 | 3.65 | - | 121507 | 0 | 121507
P00935 | 70 | 0 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 6.24 | -0.27 | 17.9 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 932.6 | 15 | 4.11 | - | 92717 | 0 | 92717
P00936 | 70 | 5 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 9.14 | 1.4 | 14.7 | R290 (Propane) | Countercurrent | 5 | 5 | 70 | 60 | 613.7 | 6.4 | 4.86 | - | 62007 | 0 | 62007
P00937 | 70 | -16 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.42 | -5 | 31.4 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1845.8 | 73 | 3.19 | - | 173967 | 0 | 173967
P00938 | 56 | -20 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -3.31 | -6.24 | 36.8 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1889.3 | 77.7 | 3.63 | - | 193979 | 0 | 193979
P00939 | 56 | -15 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.37 | -4.97 | 31.3 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1662.1 | 55.5 | 3.87 | - | 173415 | 0 | 173415
P00940 | 56 | -10 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | 15 | 4.6 | 10 | 0.78 | -3.6 | 26.4 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1421.5 | 37.1 | 4.32 | - | 150640 | 0 | 150640
P00944 | 56 | -16 | 15 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 56 | 15 | 4.6 | 10 | -1.79 | -5.24 | 32.4 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1710 | 59.7 | 3.81 | - | 177844 | 0 | 177844
P00973 | 55 | -20 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -2.12 | -5.46 | 33.3 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1991.3 | 84.2 | 3.72 | - | 205818 | 0 | 205818
P00974 | 55 | -15 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.47 | -4.39 | 29 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1770.4 | 61.5 | 3.97 | - | 185922 | 0 | 185922
P00975 | 55 | -10 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.6 | -3.09 | 24.9 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1510 | 41.1 | 4.47 | - | 161052 | 0 | 161052
P00979 | 55 | -16 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.87 | -4.64 | 30 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1822 | 66.2 | 3.9 | - | 190739 | 0 | 190739
P00980 | 62.5 | -20 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -1.88 | -5.3 | 32.6 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 2065.9 | 92.7 | 3.37 | - | 202844 | 0 | 202844
P00981 | 62.5 | -15 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.21 | -4.21 | 28.4 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1830.5 | 67.6 | 3.51 | - | 182766 | 0 | 182766
P00982 | 62.5 | -10 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.71 | -3.02 | 24.7 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1574 | 46.2 | 3.74 | - | 159742 | 0 | 159742
P00983 | 62.5 | -5 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.03 | -1.59 | 20.9 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 1278 | 28.1 | 4.18 | - | 131776 | 0 | 131776
P00984 | 62.5 | 0 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.67 | -0.02 | 17.4 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 955.5 | 14.9 | 4.86 | - | 100026 | 0 | 100026
P00986 | 62.5 | -16 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.61 | -4.48 | 29.4 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1885.3 | 72.9 | 3.47 | - | 187623 | 0 | 187623
P00987 | 70 | -20 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -1.58 | -5.1 | 31.8 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 2144.6 | 102.1 | 3.13 | - | 199281 | 0 | 199281
P00988 | 70 | -15 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.1 | -4.15 | 28.2 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1918.4 | 76.3 | 3.21 | - | 181443 | 0 | 181443
P00989 | 70 | -10 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.9 | -2.89 | 24.3 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1635.3 | 52 | 3.35 | - | 157356 | 0 | 157356
P00990 | 70 | -5 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 4.18 | -1.5 | 20.7 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 1329.2 | 31.9 | 3.63 | - | 130056 | 0 | 130056
P00991 | 70 | 0 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 6.75 | 0.02 | 17.3 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 997.5 | 16.8 | 4.1 | - | 99167 | 0 | 99167
P00992 | 70 | 5 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 9.43 | 1.57 | 14.4 | R290 (Propane) | Countercurrent | 5 | 5 | 70 | 60 | 662.2 | 7.4 | 4.73 | - | 66902 | 0 | 66902
P00993 | 70 | -16 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.36 | -4.36 | 28.8 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1958.7 | 80.8 | 3.18 | - | 184603 | 0 | 184603
P00994 | 56 | -20 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -2.12 | -5.46 | 33.3 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 2004.6 | 85.5 | 3.66 | - | 205818 | 0 | 205818
P00995 | 56 | -15 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.45 | -4.37 | 29 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1779.4 | 62.4 | 3.88 | - | 185654 | 0 | 185654
P00996 | 56 | -10 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | 15 | 4.6 | 10 | 1.61 | -3.08 | 24.8 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1518.2 | 41.8 | 4.32 | - | 160895 | 0 | 160895
P01000 | 56 | -16 | 15 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 68 | 15 | 4.6 | 10 | -0.85 | -4.63 | 30 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1831.3 | 67.1 | 3.82 | - | 190455 | 0 | 190455
P01022 | 47.5 | -20 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.61 | -7.81 | 44.8 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 1607.9 | 56.3 | 4.38 | - | 174351 | 0 | 174351
P01029 | 55 | -20 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.38 | -7.65 | 43.9 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 1668.2 | 62.7 | 3.66 | - | 172420 | 0 | 172420
P01030 | 55 | -15 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.21 | -6.21 | 36.5 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 1467 | 44.4 | 3.95 | - | 154058 | 0 | 154058
P01031 | 55 | -10 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.58 | -4.46 | 29.3 | R290 (Propane) | Countercurrent | -10 | 5 | 55 | 60 | 1235.5 | 28.7 | 4.5 | - | 131780 | 0 | 131780
P01035 | 55 | -16 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.61 | -6.44 | 37.8 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 1503.4 | 47.5 | 3.88 | - | 157386 | 0 | 157386
P01036 | 62.5 | -20 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.15 | -7.49 | 43.1 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 1736.1 | 69.8 | 3.32 | - | 170466 | 0 | 170466
P01037 | 62.5 | -15 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.99 | -5.99 | 35.8 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 1524 | 49.4 | 3.51 | - | 152171 | 0 | 152171
P01038 | 62.5 | -10 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.55 | -4.44 | 29.2 | R290 (Propane) | Countercurrent | -10 | 5 | 62.5 | 60 | 1295.8 | 32.7 | 3.81 | - | 131513 | 0 | 131513
P01039 | 62.5 | -5 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.31 | -2.64 | 23.6 | R290 (Propane) | Countercurrent | -5 | 5 | 62.5 | 60 | 1041 | 19.4 | 4.32 | - | 107342 | 0 | 107342
P01040 | 62.5 | 0 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.32 | -0.82 | 19.1 | R290 (Propane) | Countercurrent | 0 | 5 | 62.5 | 60 | 781.5 | 10.4 | 5.04 | - | 81811 | 0 | 81811
P01042 | 62.5 | -16 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.43 | -6.32 | 37.2 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 1566.5 | 53.2 | 3.46 | - | 155889 | 0 | 155889
P01043 | 70 | -20 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -4.8 | -7.25 | 41.8 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 1802.5 | 77 | 3.1 | - | 167489 | 0 | 167489
P01044 | 70 | -15 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -2.77 | -5.88 | 35.2 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 1589.1 | 55.4 | 3.22 | - | 150296 | 0 | 150296
P01045 | 70 | -10 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.44 | -4.36 | 29 | R290 (Propane) | Countercurrent | -10 | 5 | 70 | 60 | 1356.6 | 37 | 3.44 | - | 130540 | 0 | 130540
P01046 | 70 | -5 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 2.35 | -2.65 | 23.5 | R290 (Propane) | Countercurrent | -5 | 5 | 70 | 60 | 1092.8 | 22.1 | 3.78 | - | 106924 | 0 | 106924
P01047 | 70 | 0 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 5.36 | -0.79 | 19.1 | R290 (Propane) | Countercurrent | 0 | 5 | 70 | 60 | 819.9 | 11.9 | 4.23 | - | 81511 | 0 | 81511
P01048 | 70 | 5 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | 8.61 | 1.1 | 15.2 | R290 (Propane) | Countercurrent | 5 | 5 | 70 | 60 | 534.9 | 5 | 5.1 | - | 54037 | 0 | 54037
P01049 | 70 | -16 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.2 | -6.2 | 36.5 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 1633.6 | 59.5 | 3.19 | - | 153964 | 0 | 153964
P01050 | 56 | -20 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -5.36 | -7.63 | 43.8 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 1677.6 | 63.7 | 3.6 | - | 172244 | 0 | 172244
P01051 | 56 | -15 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.19 | -6.19 | 36.5 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 1475.1 | 45 | 3.87 | - | 153896 | 0 | 153896
P01052 | 56 | -10 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | 15 | 4.6 | 10 | -0.58 | -4.46 | 29.3 | R290 (Propane) | Countercurrent | -10 | 5 | 56 | 60 | 1243.5 | 29.2 | 4.37 | - | 131780 | 0 | 131780
P01056 | 56 | -16 | 15 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 39 | 15 | 4.6 | 10 | -3.59 | -6.42 | 37.7 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 1511.6 | 48.2 | 3.81 | - | 157206 | 0 | 157206
P01066 | 47.5 | -20 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.59 | -17.33 | 21.6 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 535.1 | 9.5 | 4.06 | - | 58019 | 0 | 58019
P01067 | 47.5 | -15 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.14 | -13.85 | 15.8 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 315.4 | 2.7 | 4.94 | - | 34724 | 0 | 34724
P01068 | 47.5 | -16 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.94 | -14.64 | 16.9 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 365.1 | 3.4 | 4.71 | - | 40077 | 0 | 40077
P01069 | 55 | -20 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.54 | -17.28 | 21.5 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 558.2 | 10.7 | 3.59 | - | 57698 | 0 | 57698
P01070 | 55 | -15 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.15 | -13.86 | 15.8 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 331.2 | 3 | 4.19 | - | 34777 | 0 | 34777
P01071 | 55 | -16 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.93 | -14.63 | 16.9 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 382.4 | 4 | 4.03 | - | 40037 | 0 | 40037
P01072 | 62.5 | -20 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.49 | -17.23 | 21.4 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 584.1 | 12 | 3.28 | - | 57349 | 0 | 57349
P01073 | 62.5 | -15 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.18 | -13.89 | 15.8 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 350.5 | 3.4 | 3.72 | - | 34992 | 0 | 34992
P01074 | 62.5 | -16 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.83 | -14.53 | 16.8 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 395.2 | 4.6 | 3.59 | - | 39328 | 0 | 39328
P01075 | 70 | -20 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.4 | -17.13 | 21.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 610.4 | 13.4 | 3.04 | - | 56721 | 0 | 56721
P01076 | 70 | -15 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.18 | -13.89 | 15.8 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 369.9 | 3.9 | 3.39 | - | 34988 | 0 | 34988
P01077 | 70 | -16 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.81 | -14.51 | 16.7 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 416 | 5.6 | 3.28 | - | 39206 | 0 | 39206
P01078 | 56 | -20 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -15.54 | -17.27 | 21.5 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 561.5 | 10.9 | 3.54 | - | 57652 | 0 | 57652
P01079 | 56 | -15 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.15 | -13.86 | 15.8 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 333.4 | 3.1 | 4.12 | - | 34784 | 0 | 34784
P01080 | 56 | -16 | -7 | 18194.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 18194.4 | 1.4 | 19 | -7 | -10.41 | 10 | -12.93 | -14.63 | 16.9 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 384.9 | 4.1 | 3.97 | - | 40029 | 0 | 40029
P01090 | 47.5 | -20 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.92 | -16.64 | 20.3 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 605.7 | 11.9 | 3.92 | - | 65674 | 0 | 65674
P01091 | 47.5 | -15 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.79 | -15.17 | 15.3 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 360.9 | 3.3 | 4.69 | - | 39728 | 0 | 39728
P01092 | 47.5 | -16 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.5 | -14.21 | 16.3 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 416 | 4.9 | 4.51 | - | 45659 | 0 | 45659
P01093 | 55 | -20 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.86 | -16.58 | 20.2 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 631.1 | 13.3 | 3.48 | - | 65233 | 0 | 65233
P01094 | 55 | -15 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.78 | -15.16 | 15.3 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 377.7 | 3.9 | 3.99 | - | 39669 | 0 | 39669
P01095 | 55 | -16 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.4 | -14.1 | 16.1 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 427.6 | 5.7 | 3.82 | - | 44760 | 0 | 44760
P01096 | 62.5 | -20 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.81 | -16.53 | 20.1 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 659.6 | 14.9 | 3.18 | - | 64764 | 0 | 64764
P01097 | 62.5 | -15 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.77 | -15.15 | 15.2 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 396.6 | 4.7 | 3.58 | - | 39602 | 0 | 39602
P01098 | 62.5 | -16 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.38 | -14.08 | 16.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 448.1 | 6.7 | 3.45 | - | 44592 | 0 | 44592
P01099 | 70 | -20 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.7 | -16.42 | 19.9 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 687.9 | 16.6 | 2.96 | - | 63917 | 0 | 63917
P01100 | 70 | -15 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.76 | -15.13 | 15.2 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 417.5 | 5.6 | 3.27 | - | 39483 | 0 | 39483
P01101 | 70 | -16 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.35 | -14.05 | 16.1 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 470.8 | 8 | 3.17 | - | 44370 | 0 | 44370
P01102 | 56 | -20 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -14.86 | -16.58 | 20.2 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 634.7 | 13.5 | 3.43 | - | 65169 | 0 | 65169
P01103 | 56 | -15 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -11.78 | -15.16 | 15.3 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 380.2 | 4 | 3.92 | - | 39663 | 0 | 39663
P01104 | 56 | -16 | -7 | 22353.12 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 22353.12 | 1.72 | 27 | -7 | -10.41 | 10 | -12.39 | -14.1 | 16.1 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 430.2 | 5.8 | 3.76 | - | 44741 | 0 | 44741
P01114 | 47.5 | -20 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.32 | -16.03 | 19.2 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 667.8 | 14.2 | 3.83 | - | 72412 | 0 | 72412
P01115 | 47.5 | -15 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.49 | -14.73 | 14.9 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 402.7 | 4.6 | 4.51 | - | 44336 | 0 | 44336
P01116 | 47.5 | -16 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.05 | -13.76 | 15.6 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 455.1 | 6.6 | 4.3 | - | 49950 | 0 | 49950
P01117 | 55 | -20 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.27 | -15.98 | 19.1 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 695.1 | 15.8 | 3.4 | - | 71846 | 0 | 71846
P01118 | 55 | -15 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.48 | -14.71 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 421.3 | 5.4 | 3.84 | - | 44244 | 0 | 44244
P01119 | 55 | -16 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.01 | -13.72 | 15.6 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 472.9 | 7.6 | 3.71 | - | 49502 | 0 | 49502
P01120 | 62.5 | -20 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.2 | -15.91 | 19 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 724.9 | 17.6 | 3.12 | - | 71175 | 0 | 71175
P01121 | 62.5 | -15 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.46 | -14.69 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 441.6 | 6.4 | 3.45 | - | 44096 | 0 | 44096
P01122 | 62.5 | -16 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.02 | -13.73 | 15.6 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 498.6 | 8.6 | 3.33 | - | 49622 | 0 | 49622
P01123 | 70 | -20 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.02 | -15.72 | 18.7 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 746.5 | 19.4 | 2.86 | - | 69364 | 0 | 69364
P01124 | 70 | -15 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.41 | -14.63 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 461.3 | 7.4 | 3.18 | - | 43629 | 0 | 43629
P01125 | 70 | -16 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.99 | -15.5 | 15.5 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 523.6 | 9.7 | 3.06 | - | 49351 | 0 | 49351
P01126 | 56 | -20 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -14.26 | -15.97 | 19.1 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 699 | 16 | 3.36 | - | 71765 | 0 | 71765
P01127 | 56 | -15 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -11.47 | -14.71 | 14.8 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 423.9 | 5.5 | 3.77 | - | 44228 | 0 | 44228
P01128 | 56 | -16 | -7 | 26641.8 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 26641.8 | 2.05 | 35 | -7 | -10.41 | 10 | -12.01 | -13.71 | 15.6 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 475.8 | 7.7 | 3.65 | - | 49482 | 0 | 49482
P01138 | 47.5 | -20 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.75 | -15.45 | 18.2 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 714.3 | 16.2 | 3.72 | - | 77455 | 0 | 77455
P01139 | 47.5 | -15 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.19 | -14.34 | 14.5 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 436.9 | 5.8 | 4.41 | - | 48098 | 0 | 48098
P01140 | 47.5 | -16 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.8 | -15.19 | 15.3 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 502.3 | 8 | 4.29 | - | 55137 | 0 | 55137
P01141 | 55 | -20 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.68 | -15.38 | 18.1 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 741.6 | 17.9 | 3.3 | - | 76646 | 0 | 76646
P01142 | 55 | -15 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.18 | -14.32 | 14.4 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 456.3 | 6.8 | 3.74 | - | 47914 | 0 | 47914
P01143 | 55 | -16 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.72 | -15.06 | 15.2 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 516.9 | 8.9 | 3.61 | - | 54113 | 0 | 54113
P01144 | 62.5 | -20 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.61 | -15.31 | 18 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 772.7 | 19.9 | 3.03 | - | 75874 | 0 | 75874
P01145 | 62.5 | -15 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.1 | -14.23 | 14.4 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 471.7 | 7.7 | 3.32 | - | 47099 | 0 | 47099
P01146 | 62.5 | -16 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.69 | -15.02 | 15.1 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 540.7 | 9.9 | 3.25 | - | 53805 | 0 | 53805
P01147 | 70 | -20 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.5 | -15.2 | 17.8 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 802.8 | 21.9 | 2.84 | - | 74594 | 0 | 74594
P01148 | 70 | -15 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.09 | -14.22 | 14.3 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 496.5 | 8.7 | 3.04 | - | 46957 | 0 | 46957
P01149 | 70 | -16 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.65 | -14.96 | 15.1 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 566.4 | 11.1 | 3 | - | 53383 | 0 | 53383
P01150 | 56 | -20 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -13.67 | -15.37 | 18.1 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 745.5 | 18.2 | 3.26 | - | 76548 | 0 | 76548
P01151 | 56 | -15 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.12 | -14.25 | 14.4 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 453 | 6.8 | 3.62 | - | 47265 | 0 | 47265
P01152 | 56 | -16 | -7 | 30930.48 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 30930.48 | 2.38 | 45 | -7 | -10.41 | 10 | -11.72 | -15.06 | 15.2 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 520.3 | 9 | 3.55 | - | 54113 | 0 | 54113
P01162 | 47.5 | -20 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.39 | -15.09 | 17.6 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 767.5 | 18 | 3.74 | - | 83216 | 0 | 83216
P01163 | 47.5 | -15 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.96 | -13.96 | 14.2 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 467.8 | 7 | 4.35 | - | 51501 | 0 | 51501
P01164 | 47.5 | -16 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.45 | -14.68 | 14.8 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 528.3 | 8.9 | 4.14 | - | 57981 | 0 | 57981
P01165 | 55 | -20 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.33 | -15.03 | 17.5 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 797.1 | 20 | 3.33 | - | 82391 | 0 | 82391
P01166 | 55 | -15 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.95 | -13.95 | 14.1 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 489.1 | 7.9 | 3.69 | - | 51360 | 0 | 51360
P01167 | 55 | -16 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.43 | -14.65 | 14.8 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 550.7 | 9.9 | 3.55 | - | 57654 | 0 | 57654
P01168 | 62.5 | -20 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.16 | -14.87 | 17.3 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 817.4 | 22 | 3.01 | - | 80259 | 0 | 80259
P01169 | 62.5 | -15 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.92 | -13.92 | 14.1 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 511.7 | 8.8 | 3.32 | - | 51090 | 0 | 51090
P01170 | 62.5 | -16 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.4 | -14.61 | 14.7 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 575.3 | 11 | 3.22 | - | 57251 | 0 | 57251
P01171 | 70 | -20 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.11 | -14.81 | 17.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 856.1 | 24.5 | 2.8 | - | 79548 | 0 | 79548
P01172 | 70 | -15 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.9 | -13.9 | 14.1 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 536.6 | 9.8 | 3.05 | - | 50753 | 0 | 50753
P01173 | 70 | -16 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.36 | -14.56 | 14.7 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 602.8 | 12.3 | 2.96 | - | 56809 | 0 | 56809
P01174 | 56 | -20 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -13.32 | -15.02 | 17.5 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 801.3 | 20.3 | 3.29 | - | 82274 | 0 | 82274
P01175 | 56 | -15 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -10.94 | -13.94 | 14.1 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 492.1 | 8 | 3.63 | - | 51343 | 0 | 51343
P01176 | 56 | -16 | -7 | 35089.2 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 35089.2 | 2.7 | 55 | -7 | -10.41 | 10 | -11.42 | -14.64 | 14.8 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 553.7 | 10 | 3.5 | - | 57581 | 0 | 57581
P01186 | 47.5 | -20 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.56 | -16.27 | 19.6 | R290 (Propane) | Countercurrent | -20 | 5 | 47.5 | 60 | 638.9 | 13.1 | 3.87 | - | 69273 | 0 | 69273
P01187 | 47.5 | -15 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.61 | -14.9 | 15 | R290 (Propane) | Countercurrent | -15 | 5 | 47.5 | 60 | 383.6 | 4 | 4.58 | - | 42226 | 0 | 42226
P01188 | 47.5 | -16 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.27 | -13.98 | 15.9 | R290 (Propane) | Countercurrent | -16 | 5 | 47.5 | 60 | 440 | 5.8 | 4.44 | - | 48299 | 0 | 48299
P01189 | 55 | -20 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.44 | -16.16 | 19.4 | R290 (Propane) | Countercurrent | -20 | 5 | 55 | 60 | 659.8 | 14.6 | 3.39 | - | 68199 | 0 | 68199
P01190 | 55 | -15 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.6 | -14.89 | 15 | R290 (Propane) | Countercurrent | -15 | 5 | 55 | 60 | 401.6 | 4.7 | 3.89 | - | 42171 | 0 | 42171
P01191 | 55 | -16 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.25 | -13.96 | 15.9 | R290 (Propane) | Countercurrent | -16 | 5 | 55 | 60 | 459.7 | 6.9 | 3.81 | - | 48127 | 0 | 48127
P01192 | 62.5 | -20 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.37 | -16.08 | 19.3 | R290 (Propane) | Countercurrent | -20 | 5 | 62.5 | 60 | 687.6 | 16.3 | 3.1 | - | 67517 | 0 | 67517
P01193 | 62.5 | -15 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.54 | -14.81 | 14.9 | R290 (Propane) | Countercurrent | -15 | 5 | 62.5 | 60 | 416.8 | 5.5 | 3.44 | - | 41615 | 0 | 41615
P01194 | 62.5 | -16 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.16 | -13.87 | 15.8 | R290 (Propane) | Countercurrent | -16 | 5 | 62.5 | 60 | 475.3 | 7.9 | 3.38 | - | 47296 | 0 | 47296
P01195 | 70 | -20 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.29 | -16.01 | 19.2 | R290 (Propane) | Countercurrent | -20 | 5 | 70 | 60 | 719.4 | 18.2 | 2.88 | - | 66850 | 0 | 66850
P01196 | 70 | -15 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.52 | -14.77 | 14.9 | R290 (Propane) | Countercurrent | -15 | 5 | 70 | 60 | 437.7 | 6.5 | 3.15 | - | 41394 | 0 | 41394
P01197 | 70 | -16 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.16 | -13.87 | 15.8 | R290 (Propane) | Countercurrent | -16 | 5 | 70 | 60 | 501.8 | 8.9 | 3.1 | - | 47296 | 0 | 47296
P01198 | 56 | -20 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -14.44 | -16.15 | 19.4 | R290 (Propane) | Countercurrent | -20 | 5 | 56 | 60 | 663.8 | 14.8 | 3.35 | - | 68154 | 0 | 68154
P01199 | 56 | -15 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -11.6 | -14.89 | 15 | R290 (Propane) | Countercurrent | -15 | 5 | 56 | 60 | 404.1 | 4.8 | 3.83 | - | 42163 | 0 | 42163
P01200 | 56 | -16 | -7 | 24692.4 | 60 | 5 | 25 | 19 | 76 | 1900 | 4 | 76 | 3.4 | 0.15 | J - Corrugated Hydrophilic aluminum | 1900 | 40 | 9.52 | 0.43 | R | 41.236 | 24692.4 | 1.9 | 31 | -7 | -10.41 | 10 | -12.25 | -13.96 | 15.9 | R290 (Propane) | Countercurrent | -16 | 5 | 56 | 60 | 462.5 | 7 | 3.75 | - | 48101 | 0 | 48101